## TL02
Clarification No- III dated 27/11/2024 to the Bidding Documents for Transmission Line Tower Package- TL02 for 220 kV S/C (on D/C Tower) Pang-Upshi (Part-2) 220kV AC Transmission line between Pang and Phyang associated with Transmission system for evacuation of RE power from renewable energy parks in Leh (5 GW Leh-Kaithal transmission corridor); Spec. No: CC/NT/W-TW/DOM/A06/24/12013
Sl no. | Re. Clause no. | Existing provision | Bidder's Query/Comment | POWERGRID Reply
1 | Technical specification Volume II Clause no. 1.4.1 of Sec-1A TL02 | It is mentioned that few stretches of the transmission line are passing through very narrow corridor and may require narrow base towers. These narrow base towers shall be designed as one circuit terminated on one cross arm whereas other circuit shall be terminated at body itself. It is further mentioned that the base width & other dimension of tower shall be finalized by contractor as per the site requirement meeting all required design parameters as stipulated in this technical specification. | We have noted that while we have the design scope for narrow base towers, there is no specified limit for base width. Our analysis indicates that towers with a base width of 5 to 6 meters necessitate raft foundations, which in turn require a wider corridor and pose challenges for execution in the current terrain. Based on the KMZ file shared by PGCIL and the site investigation conducted by our team, we understand that a corridor width is available that would accommodate a base width of approximately 8 meters. This would allow us to implement isolated foundations, which is more feasible for the terrain. Kindly confirm whether our understanding is correct so that we may finalize our designs. | Bidder may refer clause no. 1.4.1 of Sec-1A
2 | Insulators | Disc insulators | Porcelein Long Road insulators may be included in the BOQ | TS(Vol-II)- Sec-VIIIB revised to incorporate Porcelain long rod insulators. Refer Amendment -V.
3 | General Query | Extension of Completion period | Due to the extreme weather and difficult terrain, we believe the current 24-month completion period is not enough. We request an extension to 36 months to ensure safe project execution. | Completion period shall be as indicated in bid document and Bidder to quote accordingly .