| Sl. No. | Clause ref | Existing clause | Queries asked by the bidder | POWERGRID’s clarification |
| --- | --- | --- | --- | --- |
| 1. | Volume II, Section VII, Clause 2. | Test and Standards | Add following Design Validation test for Composite core; In case of composite core type conductors, composite Core manufacturer must have successfully performed design validation tests prior to bid submission as per ASTM B987 on the class of core being offered and it must be witnessed by the representative (s) of Utility or witnessed by representative of a Laboratory which is accredited to ISO/IEC 17025 (different than that of laboratory where tests were performed). | No change in Technical Specification. |
| 2. | Volume II, Section VII, Clause 2.1.1, (i), point (n | Salt Spray Test (applicable for stranded composite core conductors having galvanic protection layer not conforming to ASTM B987) | Please remove this requirement | No change in Technical Specification. |
| 3. | Volume II, Section VII, Clause 2.1.1, (ii), point (a) | Heat resistance test on Aluminium/ Aluminium Alloy strands or core. | Please amend as follows: Heat resistance test on Aluminum Alloy strands or core (Not applicable to Composite Core Conductor) | Pl refers annexure -A clause 1.13 regarding procedure of Heat resistance test which is to be carried out on Aluminium Alloy strands. It is further clarified that Heat resistance test is applicable on Aluminium Alloy strands only. |
| 4. | Volume II, Section VII, Clause 2.2, point (t) | Galvanic Protection Barrier Layer Thickness test on composite core (applicable for composite core conductors having galvanic barrier layer conforming to ASTM B987) | Please amend as follows; Galvanic Protection Barrier Layer Thickness test on composite core (applicable for composite core conductors having galvanic barrier layer conforming to ASTM B987) | No change in specification requirement. |
| 5. | Volume II, Section VIII, Clause 2.13.2 | Table Sr. No. 18 – Ampacity | Title of IEEE 738 is as follows. Please amend. IEEE Standard for Calculating the Current-Temperature Relationship of Bare Overhead Conductors. | It is clarified that for ampacity calculations, IEEE 738 “Calculating the Current-Temperature Relationship of Bare Overhead Conductors “ is to be referred. |
| 6 | Volume II, Section VIII, Annexure A, Clause 1.13 | Heat Resistance test on Aluminium Alloy wire | Please amend as follows; Heat Resistance test on Aluminum Alloy wire (only for Aluminum Zirconium alloy) | No change in specification requirement. |
| 7 | Volume II, Section VIII, Annexure A, Clause 1.25 | Breaking load test on Aluminium/ Aluminium Alloy & Core wires/composite core and D.C Resistance test on Aluminium/ Aluminium Alloy wire. The above tests shall be carried out as per IEC: 888/889 and the results shall meet the requirements of the specification. | Please add as follow for composite core; For composite cores, the breaking load shall be performed as described in Section 9 of ASTM B987. | No change in specification requirement. |
| 8. | Volume II, Section VIII Annexure A, Clause 1.33 | Bending Test on Polymer Composite Core (Type Test) : Bending test on polymer composite core (CFC) before stranding shall be performed as per ASTM B987/B987M-17 on polymer composite core samples taken from composite core at conductor manufacturing unit before stranding of conductor. Alternatively, supplier may carry out bending test on polymer composite core (CFC) before stranding on the samples taken at the core manufacturing unit, from the same reel being supplied to conductor manufacturer subject to proper traceability of the same at the conductor manufacturers works. Bending test on polymer composite core (CFC) shall also be performed as per ASTM B987/B987M-17 on polymer composite core samples taken from stranded conductor. For test after stranding the diameter of cylindrical mandrel shall be as following: For high strength grade CFC – 60 times the diameter of CFC For Extra high strength grade CFC – 70 times the diameter of CFC. | Please amend requirement as follows; Bending test on polymer composite core (CFC) shall be performed as per ASTM B987/B987M-17 on polymer composite core samples taken from composite core manufacturing facility from the same reel being supplied to conductor manufacturer subject to proper traceability of the same at the conductor manufacturers works. Alternatively, supplier may carry out bending test on polymer composite core (CFC) samples taken at the conductor manufacturing facility before or after stranding. Bending test on polymer composite core (CFC) of these samples shall also be performed as per ASTM B987/B987M-17, and the diameter of cylindrical mandrel shall be as following: For high strength grade CFC – 60 times the diameter of CFC For Extra high strength grade CFC – 70 times the diameter of CFC | No change in specification requirement. |
| 9. | …… | …… | Requirement of Narrow Base Towers: During our site visit, we understood that to minimize the right of way issues during execution of the project, PGCIL may propose narrow base towers for the critical tower locations. We understand that PGCIL shall provide Structural drawings, BOM, Shop Sketches and foundation drawings required for these Type-tested Narrow-based towers. Kindly confirm our understanding. | POWERGRID shall provide relevant documents of tower and foundation drawings for the required Narrow-based towers to successful bidder. |
| 10. | Volume – III, Price Bid, Schedule -1: Supply price schedule | …….. | In this supply price schedule, the bidder has been asked to quote their unit prices for additional quantity of Towers, HTLS Conductor, Composite Long rod Insulators, Conductor – Hardware & Accessories. We understand that these additional quantities are spares requirement. Kindly confirm our understanding. | Yes ,provision of Spare items is stipulated in BPS. |
| 11. | Specification: Volume-II, Part 4, Section VII, Cl. No. 1.4.1: | ………. | Sag – Tension at 32°C and full wind & tension at designed maximum temperature and full wind - ≤ 6596 kg corresponding to 136.72 kg/m2 wind pressure & not exceeding 70% of UTS of proposed conductor. As per Initial 22% UTS of ACSR zebra with sag of 10.18 and maximum tension limitation of 6596 kg, the wind pressure should be 156 kg/m2 instead of 136.72 kg/ m2. Kindly review and change wind pressure accordingly. | No change in specification requirement. |
| 12. | Specification: Volume-II, Part 4, Section VII, Cl. No. 2.1.1 (ii): | On Conductor Strand/core: Heat resistance test on Aluminium/ Aluminium Alloy strands or core. | On Conductor Strand/core: Heat resistance test on Aluminium/ Aluminium Alloy strands or core. We understand that the Heat resistance test is not applicable for annealed aluminum. Kindly confirm our understanding. | Refer Sl.No. 3 above. |
| 13. | Specification: Volume-II, Part 4, Section VII, Annexure – A, Cl. No. 1.1: | UTS Test on Stranded Conductor at a) room temperature and b) elevated temperature | UTS test on stranded conductor at elevated temperature: UTS Test on Stranded Conductor shall be conducted as per clause no. 1.1(a) specified keeping conductor temperature at the designed maximum temperature. We wish to suggest addition of following line in this clause: “RTS for this test shall be 70% of the UTS guaranteed in the GTP.” | Please refer clause no.1.2.2 of section VII of Technical specification regarding UTS requirement at elevated temperature. |
| 14. | Specification: Volume-II, Part 4, Section VII, Annexure – A, Cl. No. 1.6 | High Temperature endurance & creep test | The conductor temperature shall be increased to designed maximum temperature in steps of 20 deg. C and thermal elongation of the conductor sample shall be measured & recorded at each step. The temperature shall be held at each step for sufficient duration for stabilisation of temperature. Further, the temperature of the conductor shall be maintained at designed maximum temperature (+10 Deg. C) for 1000 hours. The elongation /creep strain of the conductor during this period shall be measured and recorded at end of 1 hour, 10-hour, 100 hour and subsequently every 100-hour up to 1000 hours’ time period. After completion of the above, the conductor sample shall be subjected to UTS test as mentioned above at clause 1.1 of Annexure-A. Since the conductor offered at maximum operating temperature, the test temperature shall not exceed the same and the designed maximum temperature should be in the range of +0/-10 Deg. C. | No change in specification requirement. |
| 15. | PGCIL Specification: Volume-II, Part 4, Section VII, Cl. No. 2.1.1 (i): | Salt Spray Test (applicable for stranded composite core conductors having galvanic protection layer not conforming to ASTM B987) | Salt Spray Test (applicable for stranded composite core conductors having galvanic protection layer not conforming to ASTM B987). Salt spray provides a single point evaluation of the galvanic resistance of the conductor while it is in pristine condition. It does not address the possible breakdown of the galvanic barrier due to wearing down of the protective layer over time. We request PGCIL to remove this test requirement. | Refer Sl.No. 2 above. |
| 16. | Specification: Volume-II, Part 4, Section VII, Cl. No. 2.2, point (t): | Galvanic Protection Barrier Layer Thickness test on composite core (applicable for composite core conductors having galvanic barrier layer conforming to ASTM B987. | We wish to suggest following amendment in the clause: “All composite core should meet minimum Galvanic Protection Barrier Layer Thickness requirement specified in only available international standard ASTM B987 for composite core.” | Refer Sl.No. 4 above. |
| 17. | Specification: Volume-II, Part 4, Section VII, Annexure A, Cl. No. 1.25: | Breaking load test on Aluminium/ Aluminium Alloy & Core wires/composite core and D.C Resistance test on Aluminium/ Aluminium Alloy wire | Breaking load test on Aluminum/Aluminum Alloy & Composite core/ Core wires and D.C Resistance test on Aluminum/ Aluminum Alloy wire. The tests shall be carried out as per IEC: 888/889 or relevant international standards and the results shall meet the requirements of the specification. IEC 888/889 is not applicable to composite core. For composite cores, the breaking load test should be performed as described in Section 9 of ASTM B987. Kindly amend the clause accordingly | Refer Sl.No. 7 above. |
| 18. | Specification: Volume-II, Part 4, Section VII, Annexure A, Cl. No. 1.33: | Bending Test on Polymer Composite Core (Type Test): Bending Test on Polymer Composite Core (Type Test). Bending test on polymer composite core (CFC) before stranding shall be performed as per ASTM B987/B987M-17 on polymer composite core samples taken from composite core at conductor manufacturing unit before stranding of conductor. Alternatively, supplier may carry out bending test on polymer composite core (CFC) before stranding on the samples taken at the core manufacturing unit, from the same reel being supplied to conductor manufacturer subject to proper traceability of the same at the conductor manufacturers works. Bending test on polymer composite core (CFC) shall also be performed as per ASTM B987/B987M-17 on polymer composite core samples taken from stranded conductor. For test after stranding the diameter of cylindrical mandrel shall be as following: - For high strength grade CFC – 60 times the diameter of CFC. - For Extra high strength grade CFC – 70 times the diameter of CFC | We wish to suggest following amendment to this clause: “Bending test on polymer composite core (CFC) shall be performed as per ASTM B987/B987M-17 on polymer composite core samples taken from composite core manufacturing facility from the same reel being supplied to conductor manufacturer subject to proper traceability of the same at the conductor manufacturers works. Alternatively, supplier may carry out bending test on polymer composite core (CFC) samples taken at the conductor manufacturing facility before or after stranding. Bending test on polymer composite core (CFC) of these samples shall also be performed as per ASTM B987/B987M-17, and the diameter of cylindrical mandrel shall be as following: - For high strength grade CFC – 60 times the diameter of CFC - For Extra high strength grade CFC – 70 times the diameter of CFC” | Refer Sl.No. 8 above. |
| 19. | Specification: Volume-II, Part 4, Section VII, Cl. No. 2.13.2 | Table Sr. No. 18 - Ampacity. | Please state for the actual title of IEEE 738 as per following: “IEEE 738 Standard for calculating the Current – Temperature Relationship of Bare overhead conductors.” | Refer Sl.No. 5 above. |