| Sl. No. | Clause ref | Existing clause | Queries asked by the bidder | POWERGRID’s clarification |
| --- | --- | --- | --- | --- |
| 1. | Specification: Volume-II, Part 4, Section VII, Cl. No. 1.3 | The HTLS conductor shall meet the following minimum requirements: Overall diameter of complete conductor Not exceeding 28.62mm and Not less than 21 mm | Kindly confirm the lower limit of diameter for complete conductor - Not exceeding 28.62mm and Not less than 25 mm | It is clarified that Overall diameter of complete conductor shall not exceed 28.62mm and shall not be less than 25 mm. Necessary correction due to the above typographical error is incorporated in the Errata-I |
| 2. | Section VII, Cl. No. 1.4.1 | Sag – Tension requirements Tension at 32°C and full wind & Tension at designed maximum temperature and full wind - ≤ 6596 kg corresponding to 136.72 kg/m2 wind pressure & not exceeding 70% of UTS of proposed conductor | Kindly confirm the mentioned wind pressure & max. tension limitation. As per Initial 22% UTS of ACSR zebra & with sag of 10.18 and max. tension limitation of 6596 kgf, the wind pressure shall be 156 kg/sq.m. instead of 136.72 as per previous | Refer our earlier Clarification-I (Part 2 of 3) |
| 3. | Section VII, Cl. No. 2.1.1 (ii) | (ii) On Conductor Strand/core Heat resistance test on Aluminium/ Aluminium Alloy strands or core | Kindly add as mentioned below, Heat resistance test on Aluminium/ Aluminium Alloy strands or core (If applicable) |  |
| 4. | Volume II, Section VIII, Annexure A, Clause 1.13 | Heat Resistance test on Aluminum Alloy wire | Please amend as follows; Heat Resistance test on Aluminum Alloy wire (only for Aluminum Zirconium alloy) |  |
| 5. | Section VII, Annexure – A Cl. No. 1.1 | b) UTS test on stranded conductor at elevated temperature UTS Test on Stranded Conductor shall be conducted as per clause no. 1.1(a) specified above keeping conductor temperature at the designed maximum temperature. | Kindly modify as mentioned below, UTS Test on Stranded Conductor shall be conducted as per clause no. 1.1(a) specified above keeping conductor temperature at the designed maximum temperature. RTS for this test shall be 70% of the UTS guaranteed in the GTP. |  |
| 6. | Section VII, Annexure – A Cl. No. 1.6 | High Temperature endurance & creep test (ii) On other conductor sample, the conductor temperature shall be increased to designed maximum temperature in steps of 20 deg. C and thermal elongation of the conductor sample shall be easured & recorded at each step. The temperature shall be held at each step for sufficient duration for stablisation of temperature. Further, the temperature of the onductor shall be maintained at designed maximum temperature (+10 Deg. C) for 1000 hours. The elongation/creep strain of the conductor during this period shall be measured and recorded at end of 1 hour, 10 hour, 100 hour andsubsequently every 100 hour upto 1000 hours time period. After completion of the above, the conductor sample shall be subjected to UTS test as mentioned above at clause 1.1 of Annexure-A. | Kindly modify as mentioned below, On other conductor sample, the conductor temperature shall be increased to designed maximum temperature in steps of 20 deg. C and thermal elongation of the conductor sample shall be easured & recorded at each step. The temperature shall be held at each step for sufficient duration for stablisation of temperature. Further, the temperature of the onductor shall be maintained at designed maximum temperature (+0/-10 Deg. C) for 1000 hours. The elongation/creep strain of the conductor during this period shall be measured and recorded at end of 1 hour, 10 hour, 100 hour and subsequently every 100 hour upto 1000 hours time period. After completion of the above, the conductor sample shall be subjected to UTS test as mentioned above at clause 1.1 of Annexure-A. |  |
| 7 | Volume II, Section VIII, Clause 2.1.1, (i), point (n) | Salt Spray Test (applicable for stranded composite core conductors having galvanic protection layer not conforming to ASTM B987) | Please remove this requirement |  |
| 8 | Volume II, Section VIII, Clause 2.2, point (t) | Galvanic Protection Barrier Layer Thickness test on composite core (applicable for composite core conductors having galvanic barrier layer conforming to ASTM B987) | Please amend as follows; Galvanic Protection Barrier Layer Thickness test on composite core (applicable for composite core conductors having galvanic barrier layer conforming to ASTM B987). |  |
| 9 | Volume II, Section VIII, Clause 2.13.2 | Table Sr. No. 18 – Ampacity | Title of IEEE 738 is as follows. Please amend. IEEE Standard for Calculating the Current-Temperature Relationship of Bare Overhead Conductors |  |
| 10 | Volume II, Section VIII, Clause 2. | Test and Standards | Add following Design Validation test for Composite core; In case of composite core type conductors, composite Core manufacturer must have successfully performed design validation tests prior to bid submission as per ASTM B987 on the class of core being offered and it must be witnessed by the representative (s) of Utility or witnessed by representative of a Laboratory which is accredited to ISO/IEC 17025 (different than that of laboratory where tests were performed). |  |
| 11 | Volume II, Section VIII, Annexure A, Clause 1.25 | Breaking load test on Aluminium/Aluminium Alloy & Composite core/ Core wires and D.C Resistance test on Aluminium/ Aluminium Alloy wire The above tests shall be carried out as per IEC: 888/889 or relevant international standards and the results shall meet the requirements of the specification | Please add as follow for composite core; For composite cores, the breaking load shall be performed as described in Section 9 of ASTM B987.understanding. |  |
| 12 | Volume II, Section VIII, Annexure A, Clause 1.33 | Bending Test on Polymer Composite Core (Type Test) Bending test on polymer composite core (CFC) before stranding shall be performed as per ASTM B987/B987M-17 on polymer composite core samples taken from composite core at conductor manufacturing unit before stranding of conductor. Alternatively, supplier may carry out bending test on polymer composite core (CFC) before stranding on the samples taken at the core manufacturing unit, from the same reel being supplied to conductor manufacturer subject to proper traceability of the same at the conductor manufacturers works. Bending test on polymer composite core (CFC) shall also be performed as per ASTM B987/B987M-17 on polymer composite core samples taken from stranded conductor. For test after stranding the diameter of cylindrical mandrel shall be as following: For high strength grade CFC – 60 times the diameter of CFC For Extra high strength grade CFC – 70 times the diameter of CFC | Please amend requirement as follows; Bending test on polymer composite core (CFC) shall be performed as per ASTM B987/B987M-17 on polymer composite core samples taken from composite core manufacturing facility from the same reel being supplied to conductor manufacturer subject to proper traceability of the same at the conductor manufacturers works. Alternatively, supplier may carry out bending test on polymer composite core (CFC) samples taken at the conductor manufacturing facility before or after stranding. Bending test on polymer composite core (CFC) of these samples shall also be performed as per ASTM B987/B987M-17, and the diameter of cylindrical mandrel shall be as following: For high strength grade CFC – 60 times the diameter of CFC For Extra high strength grade CFC – 70 times the diameter of CFC |  |