| SN | Bidder’s query Sl. No. | Clause reference | Provision in Specification | Bidder’s Query | POWERGRID Reply |
| --- | --- | --- | --- | --- | --- |
|  | Volume-II of the Bidding Documents |  |  |  |  |
|  | 1. | Technical specification: Section-Project- Rev-00 | Clause 2: Scope of Work 2.1 The scope of this specification covers the following at 765/400/220kV Ramgarh PS S/s • STATCOM Station, having following rated capacity in 400kV Bus Section-1... • STATCOM Station, having following rated capacity in 400kV Bus Section-2... • Associated 400kV bays for above STATCOM Stations. And Clause 6 Basic Reference Drawings ... The Single line diagram and general layout drawings for Ramgarh substation will be finalized during execution stage and shall be provided subsequently during the detailed engineering of STATCOM station. | Bidder request to provide Single Line diagram and Layout to form the common basis of bid preparation for all bidders. Any change in estimated quantities due to changes in SLD/Layout during detailed engineering shall be charged on unit rate basis. Following information must be included in the provided SLD/Layout: 1. SLD with clearly identified 400kV Bays associated with STATCOM stations. 2. Layout showing allocated space for STATCOM station, distance of associated 400kV bays from STATCOM Yard and distance of Main Control Room from STATCOM yard. Above information is required to plan STATCOM Layout, Its interconnection and interfaces for proper costing. | Kindly refer clause no 6 of section project. “765/400/220kV RAMGARH PS is being executed under separate contract with one and half breaker scheme arrangement for 400kV voltage level. The Single line diagram and general layout drawings for Ramgarh substation will be finalized during execution stage and shall be provided subsequently during the detailed engineering of STATCOM station..” Bidder to quote as per provisions of bidding documents. |
|  | 2. | Technical specification: Section-Project- Rev-00 | Clause 2: Scope of Work 2.1 The scope of this specification covers the following at 765/400/220kV Ramgarh PS S/s • STATCOM Station, having following rated capacity in 400kV Bus Section-1... • STATCOM Station, having following rated capacity in 400kV Bus Section-2... • Associated 400kV bays for above STATCOM Stations. | For STATCOM associated bay in 400kV yard, Auxiliary Supply shall be made available from Main substation (nearby BMK and Lighting Panels) | Auxiliary supply for 400kV Bay for STATCOM shall be taken from ACDB Located in Control Room Building/Auxiliary Building. |
|  | 3. | Technical specification: Section-Project- Rev-00 | Clause 2.2.1 e) 33/0.415 kV XXX kVA Auxiliary LT transformer along with associated 72.5kV out door switchgear equipment’s to be installed on tertiary of existing 500 MVA, 400/220/33 kV Auto transformer including cable for interconnection. | This is to note that all 72.5kV/33kV outdoor equipment ( CB,CT, ISO etc)required for 33kV hookup from tertiary of ICT shall be located in main station transformer yard near respective ICT. Please confirm 1. Availability of space 2. Approximate distance 3. Elaborate metering arrangement requirement for 33kV Auxiliary power supply. | General arrangement & Sectional view of Ramgarh-II is under preparation, same shall be provided during detailed engineering. However, following may please be noted regarding tertiary loading of existing 500MVA, 400/220/33kV ICT: - Space shall be made available. - Approximate distance shall be provided after finalisation of GA. - Cut out & mounting arrangement shall be provided by Bidder for POWERGRID supplied energy meter shall be suitable for mounting of energy meter on CB relay panel. |
|  | 4. | Technical specification: Section-Project- Rev-00 | Clause 2.2.1 e) … The kVA rating of LT Transformer shall be adequate to feed the entire required load of STATCOM Station’s considering worst operating condition | Bidder understands that trafo size mentioned in C/ENGG/STD/STATCOM//LT/SLD/01 is only indicative and kVA rating of LT Transformer shall be selected based on the load of STATCOM station. | Bidder understanding is generally in order. |
|  | 5. | Technical specification: Section-Project- Rev-00 | Clause 2.2.2 Civil Works 8. The contractor shall acquaint themselves for the above details by visiting the site before bidding | Bidder request PGCIL to share the site location along with plot plan for site visit. | Coordinates of substation land shall be provided to the successful bidder during detailed engineering. |
|  | 6. | Technical specification: Section-Project- Rev-00 | Clause 4 II Meteorological Data | In order to perform Bid engineering and to arrive at appropriate technical solution the meteorological data is necessary. Bidder request PGCIL to confirm following environmental condition for Ramgarh STATCOM site: 1. Seismic Zone - III, Acceleration = 0.16, Importance factor 1.5 2. Wind Speed - 47m/s, Risk coefficient (K1) + 1, 3. Out Door Ambient Temperature: Max = 50 Deg C, Min = 0 Deg C . 4. Thunderstorm days per year - 10 5. Specific Creepage distance - 25mm/kV is considered for all outdoor equipment/ insulators other than Transformer Bushing and Long Rod Insulator. For all indoor insulators, creepage distance to be selected as per design requirements established by bidder. | Kindly refer clause no 4.II of section project wherein Snow fall, Seismic zone, wind zone, design ambient temperature and costal are consideration has already been provided. Other Required Information may be obtained by Bidder from the Meteorological department. |
|  | 7. | Technical specification: Section-Project- Rev-00 | Clause 13.9 Clause no 9.7 of section Technical Specification: Section-STATCOM Station, Rev02 (May, 2020) amended as below:- 9.7 Software simulation models a) Stability model ... Stability model should be non-proprietary and freely available for distribution. b) Transients model If any other proprietary softwares are used by the contractor for system control design, the contractor shall provide these softwares with perpetual license for use by the Employer. | Bidder understands that provisions in following clarifications publsihed by RECPDCL shall supersede the mentioned clause of Section project. "Additional clarifications dated 22.07.2023 on RFP Project Documents for selection of Bidder as Transmission Service Provider to establish Transmission System for “Transmission system for evacuation of power from REZ in Rajasthan (20GW) under Phase-III Part C1” through tariff based competitive bidding process. " Please confirm. | Bidder may Quote as per bidding document. Further in regard to confidentiality by CEA/CTUIL shall be maintained by them in line with RFP document issued by BPC. |
|  | 8. | Section-STATCOM Station, Rev02 | Clause 6.4.1 Radio Interference a) ...the radio interference level from electromagnetic or electrostatic inductions generated by the STATCOM station shall not exceed 100 micro-volts/m, under fair weather conditions, at any point outside the station fence. The Radio Interference Level (RIL) criteria shall be achieved at all frequencies within the range of 150 kHz to 300 MHz and with the STATCOM operation at any level up to and including rated value, the design shall provide correcting measures, should the specified design not being realized in the final installation. b) Measurements of actual RI at STATCOM Station shall be made by the TSP, at points along the above defined contour and at other critical point. c) RIV (Radio Interference voltage) measured at a phase to ground voltage (266 kVrms) in accordance to NEMA-107 shall not be more than 500 micro-volts for 400 kV system. For other system Voltages IEC/NEMA in the order of preference shall be applicable. | 1. The limit of 100 micro-volts/m specified in the RFP is based on some old references which cannot be achieved under fair weather conditions, at the STATCOM station fence. However, the limit based on IEC 62236-2 will be complied. We understand that this is acceptable. 2. We understand that the "Station Fence" refers to the external fence/boundary wall of the substation. Please confirm acceptance of our understanding. 3. We understand that the successful bidder has to conduct RI/EMC/PLC studies during execution. However, if required field measurement to be done by the TSP. | 1 & 2 Kindly refer amendment-I for the same. - Kindly refer clause no 6.4.1 b) again, as per that measurement of actual RI at STATOCM Station is in scope of contractor/bidder. |
|  | 9. | Section-STATCOM Station, Rev02 | 6.1.4 Over Voltage Strategy d) The contractor shall demonstrate to the satisfaction of the Employer that STATCOM Station will not excite ferro-resonance and sub-synchronous oscillation in the AC system. | Bidder confirms that their STATCOM solution does not excite Ferro-resonance and sub-synchronous oscillations in AC network. If required, an undertaking will be provided in this regard. No study or simulation is foreseen in this regard. | Bidder to quote as per provisions of bidding documents. |
|  | 10. | Section-STATCOM Station, Rev02 | 8.1.5 STATCOM Valve Cooling system ...The Valve cooling system shall have black start capability and necessary UPS/UMD shall be provided separately for each STATCOM Unit. | 1. We understand that bidder can decide between UMD and UPS based on his design. In case Employer have specific requirement please specify. 2. UPS will be provided for ride-through application (5 min back-up) for Valve Cooling Skid Motors. Other essential loads including outdoor fan operation, HVAC operation and motor starting will be through DG set during blackout. Starting of the Valve Cooling motor is not envisaged on UPS. 3. Inline with previously executed projects in India, Balck-start capability is provided with combination of Diesel Generator Set and UPS/UMD. 4. Non-redundant UPS may suffice the purpose by maintaining required spares. However, It is recommended to consider redundant UPS with common battery and bypass switch. | Bidder understanding is generally in order for 1,2 &3, however following may please be noted for sl no 4.. UPS/UMD shall be designed to cater continuous and starting load of valve cooling system without interruption during changeover of auxiliary power from normal to DG Set. The above duty of UPS/UMD shall also be required during changeover of the pumps of Valve Cooling System or Starting the valve cooling system, when the auxiliary supply System is running on DG set. At any given time, only one number main pump runs and UPS/UMD shall be designed to deliver power to the same as specified in the specification. UPS/UMD shall be provided in parallel redundant configuration to prevent valve cooling system outage due to failure of a single UMD. |
|  | 11. | Section-STATCOM Station, Rev02 | Clause No 8.1.7, Tests on STATCOM Unit Valve: All applicable tests i.e. Operational Type Tests (except Short- circuit test), Dielectric Type Tests & Test for valve insensitivity to electromagnetic disturbance shall be done as per latest edition of IEC62927. | Bidder offers type tested converters and have not considered repetition of converter type test. Existing type test reports will be provided for review. In case of change in any equipment / component, type test reports specific to the component / equipment can be provided separatly. | Kindyl refer amendment-I. |
|  | 12. | Section-STATCOM Station, Rev02 | Clause No. 8.7 Air Core Reactors : k) Tests on Reactors: The reactors shall be subjected to type and routine tests in accordance with the latest issue of IEC- 60076 as appropriate to the type of reactor provided. | Bidder understand that if offered Reactors or reactors with similar design are already Type Tested then repetition of Type Test is not required. Please confirm Also, Special Test are not in bidder scope. | Kindly refer clause no 8.7.k) of section STATCOM Station rev 02 in conjunction with Cl. 9.2 of Section-GTR Rev 15 regarding Type test, validity & acceptance of earlier conducted type test report. |
|  | 13. | Section-STATCOM Station, Rev02 | Clause 8.9.1, General Requirements l) The transformer should be designed to carry a certain level of direct current consistent with the STATCOM design. To ensure minimum harmonics generation, the saturation flux density of the transformer should be higher than the maximum flux density reached over the full steady state (continuous operating) range; this margin shall be at least 10%. This maximum flux density (over the full steady-state range) is obtained at the highest secondary voltage during any reactive power generation, highest reference voltage, minimum slope, and minimum continuous frequency. The flux density at the highest secondary voltage shall lie in the linear portion of the BH curve of the core. Any harmonic generated by the transformer should be considered for the design of the STATCOM. | The highest voltage on secondary side occurs when the band (0.95- 1.05) is set to zero, held at 1.05pu primary voltage, slope is 0% and the STATCOM STATION (including MSCs) operates with its maximum capacitive output. It is understood that this highest voltage plus the specified safety margin of 10% shall be used for the transformer knee point. Please confirm. | Noted, however, in case during details engineering if max flux density is achieved at any other point , it shall be used for design of transformer. |
|  | 14. | Section-STATCOM Station, Rev02 | Clause 6.1,4, Over Voltage Strategy c) The TSP shall evolve the insulation co-ordination of the components of the STATCOM Station after studies have been conducted to determine the over- voltage profile with the STATCOM connected to the system. Clause 9.5 Insulation coordination study Overall insulation coordination should be verified by considering the results of 8.4 (dynamic over voltages, and fault and switching transients), including the impacts of lightning surges on the STATCOM equipment. This study should determine and verify insulation levels, clearances, and arrester placement and ratings. | The insulation coordination is provided within the Basic Design Report. The insulation coordination of the Basic Desing considers the overvoltage profile and insulation levels according the specifications from CEA. The used station insulation coordination is based on recommended practice defined in IEC 60071 especially in IEC 60071 – 2 Annex E as well as IEC 60076 – 3 Annex B. No further studies for seen by bidder. | Insulation coordination study can be submitted along with Basic Design report is acceptable how ever any observation/comment by employer during detailed engineering stage shall be incorporated by Contractor. |
|  | 15. | Section-STATCOM Station, Rev02 | Clause 9.2.1, System Dynamic Performance Studies Clause 9.4 Electromagnetic transients, control performance, and overvoltage studies | If possible most of the system dynamic performance studies will be performed on the real time simulator during FAT. If needed, some studies (namely the POD, interaction study, control interaction study) in this section will be performed in the software PSSE. | The requirement of dynamic study as per clause 13.9 of Section Project is to be complied. |
|  | 16. | Section-STATCOM Station, Rev02 | Clause 10.1 Factory Tests of Controls b. The simulator should provide an accurate network representation including network harmonic behavior, as well as synchronous condensers, power stations, generators (with AVRs), and pump storage schemes, existing HVDC, SVCs and STATCOMs, future SVCs and STATCOMs, FSC(fixed series capacitors), and shunt reactors/ capacitors/ filters. | 1. To perform the subsequent contingency zero Sequence Impedance of power system models (Transformer, Transmission Line, Machines, etc..), needs to be furnished at the time of/before Award of Contract. In case zero sequence impedance is not available in PSSE file suitable value is assumed for modelling in RSCAD (i.e. 3 or 2 times of positive sequence impedance) 2. The PSSE (raw and dyr) files cannot be used to develop an RSCAD file/model. A network reduction in PSSE can be performed and the reduced network can be used as an input to develop the RSCAD file. In the RTDS simulator (used for factory testing of controls), the user-defined and standard library dynamic models of HVDC, SVC, STATCOM, solar, and other models that are utilized in PSSE are not available. In order to preserve the dynamics of the network In case these electrical elements are considered in the vicinity of STATCOM, they will be represented as synchronous machines and/or PQ loads in PSSE and RSCAD in order to provide an accurate network representation. The dynamics of the entire network shall be captured using elements that can be modelled in RSCAD with a pre-requisite that they are available in both PSSE and RSCAD (i.e IEEE standard dynamic models). Please confirm 3. In case there are user defined models, or HVDC/SOLAR/STATCOM/WIND etc. models in the vicinity of the STATCOM bus under consideration, they will be replaced by either synchronous machines or PQ loads, keeping the dynamics of the bus under study similar to that of the original network. No generic models from RSCAD in any form will be implemented or used. In case there are contingencies defined that involve tripping of the user defined models, or HVDC/SOLAR/STATCOM/WIND in the technical specification, the replaced synchronous machines or PQ loads shall be tripped instead. 4. In case generic models available in RSCAD have to be used, the parameters for these models shall be provided by the customer. The usage of these models are limited to the stability of the entire network. In case the network is unstable after introduction of these generic models, the original working models will be replaced back again. Since the dynamic models of RSCAD are not available in PSSE and vice-versa, the overall dynamics of the system (fault behaviour for the contingencies defined) will be different between the two software. In case there are contingencies that involve the tripping of such aforementioned models, this will be performed only if the system remains stable post fault, else neglected. | Please refer Amendment-I |
|  | 17. | Section-STATCOM Station, Rev02 | Clause 6.1.6 Dynamic Performance Controls of STATCOM Station The TSP must describe in detail, the dynamic reactive power controls for enhancing stability margin and also damp oscillations of any critical frequencies. The dead band for continuous damping control must be very small so that there are no discernible sustained oscillations. | Noted. Bidder understand that the requirement of enhancing stability margin and damp oscillations of any critical frequencies is generic in nature without any defined criteria. | Bidder may quote as per bidding document. |
|  | 18. | Section-STATCOM Station, Rev02 | Clause 8.1 STATCOM Unit/Branch ...In general the STATCOM units shall equally share the load however under contingency condition it should be possible to run the units with unequal load. | Unequal loading is not foreseen during operation. Load will be shared symmetrically between active STATCOM branches by the control system. However, uneven load sharing can be controlled manually through HMI, if required for testing purpose. Please confirm bidders understanding is correct. | Bidder understanding is generally in order. |
|  | 19. | Section-STATCOM Station, Rev02 | Clause 8.8 AC POWER CAPACITORS iv) Tests on Capacitors All the tests on capacitor units shall be generally in accordance with the latest issue of IEC publication 60871. | Bidders understand that there is no requirement of special test. Type tests are not required to be performed if type test report of similar design is available. Please confirm. | Kindly refer clause no 8.8.iv) of section STATCOM Station rev 02 in conjunction with Cl. 9.2 of Section-GTR Rev 15 regarding Type test, validity & acceptance of earlier conducted type test report. |
|  | 20. | Section-STATCOM Station, Rev02 | Clause 8.9 Coupling Transformer 15.1.4. SCADA Integration of online monitoring equipment - All the online monitoring equipment i.e. Online Dissolved Gas (Multi-gas) and Moisture Analyser, On-line insulating oil drying system (Cartridge type) etc. provided for individual transformer unit including Spare | Bidder clarifies that Coupling Transformer is to be supplied along with Online Drying System, DGA and fiber optic sensors and its measuring unit. Please confirm. | Confirmed. |
|  | 21. | 2-Volume II - STATCOM Specification Rev-2 May-2020 | The rated capability of STATCOM, MSC (as applicable) & MSR (as applicable) shall be at 400 kV (Referred to as “Point of Common Coupling” or PCC) and in the steady state frequency range of 48.5 Hz-50.5 Hz. | Bidder understand that STATCOM, MSC, MSR rating shall be designed at 400kV and 50Hz, and 48.5Hz~50.5Hz are the device steady stage operation range, which means MSC & MSR output not equal to the rating when the frequency is not 50Hz is accepted, please confirm. | Bidder’s understanding is correct; The referred para is for the harmonic performance capability of STATCOM Station |
|  | 22. | STATCOM Specification Rev 2 May 2020 clause 6.8.9: | Fulfillment of reliability guarantee: …........ The contractor* shall furnish at the start of the guarantee period a Bank Guarantee against reliability and availability requirement for an amount of 10% of the total contract value. | Bidder understood that the BG towards reliability & availability (R&A) shall be in addition to the CPG required at the Contract(s). However, the BG towards R&A shall be provided by the successful bidder at the start of guarantee period. | Confirmed |
|  | 23. | Technical Specification: Section-STATCOM Station, Rev02, Cl 3. Scope of work / Page 7 of 62 | The total cumulative Capacitive (+ve) and Inductive (-ve) MVAR rated Capacity of STATCOM Station as defined in Section project comprising of STATCOM, MSCs (as applicable), MSRs (as applicable), Coupling Transformer, Coupling Reactor or any filter (if applicable) shall be rated at 1 p.u. voltage, 1 p.u. frequency and 20 deg C ambient temperature at 400 kV Bus (Referred to as “Point of Common Coupling” or PCC). The rated capability of STATCOM, MSC (as applicable) & MSR (as applicable) shall be at 400 kV (Referred to as “Point of Common Coupling” or PCC) and in the steady state frequency range of 48.5 Hz-50.5 Hz. | Bidder understand that the nominal cumulative capacitive and inductive reactive power output of the STATCOM Station for any of the Options mentioned above shall be +550 MVAr (Point A of Figure-3 in Section-STATCOM Station) and -425 MVAr (Point B of Figure-3 in Section-STATCOM Station) at 1.0 p.u. ac bus voltage (at PCC) and nominal system frequency and 20°C ambient temperature. | The steady state frequency rate of 48.5Hz-50.5Hz shall be used for designing individual equipment rating in STATCOM, MSR & MSC branch. The points in figure-3 are for performance requirements, it is clarified that STATCOM rating shall be guaranteed at specified ambient temperature of 0-50deg C. |
|  | 24. | Technical specification: Section-Project (Clause 2.2.1. (b)) | The coupling transformer is required to be single phase units and the supply shall include supply of one number spare unit. The necessary provision of switching of spare unit of transformer to be achieved through the help of isolator and associated switching of control & protection shall be automatic through isolator contacts. Isolator based switching is envisaged for both HV and MV side of coupling transformer. Neutral formation of spare unit of transformer shall be done by manual connection. All associated materials like isolator string, hardware, structure required for above mentioned arrangement shall be provided by the contractor. | Bidder understands that provision of spare switching in HV side shall be done by disconnectors. However in MV side it can be done by jumpers. | Isolator based switching is envisaged for both HV and MV side of coupling transformer as per clause no 2.2.1(b) of section project. |
|  | 25. | Technical specification: Section-Project (Clause 2.8 (i)) | Height of Lightning masts shall be as per approved structure layout and designed for diagonal wind condition. Lightning masts shall be provided with platforms for mounting lighting fixtures and a structural steel ladder within its base up to the level of platform. The ladder shall be provided with protection rings. The platforms shall also have protection railing. The details of lighting fixtures would be as per the approved drawings | Bidder proposes that tubular type Lighting cum Lightning Masts (LCLM) can be used for lightning protection for STATCOM Yard. Please confirm. | Confirmed subject to without any additional financial implication to Employer. |
|  | 26. | 1.0 Sections_Project_Statcom Ramgarh | Clause No. 13.15.e Interface Points .........The contractor shall also provide duplicate control facility (HMI workstations and Disturbance recorder workstation) of STATCOM STATION to be located in main control room (control room of 400kV switchyard being provided by the Employer) with the necessary selector switch/ facility to operate and control STATCOM STATION from main control room. | As per the clause, HMI Work station (One remote HMI) in Substation control room shall be provided. Instead of providing Duplicated Disturbance recorder, as per the clause 8.2.2 Operator Interface (f), DFR Fault record files shall be transferred to Substation DR PC via SFTP communication link. Also, fault recorder software shall be installed in Substation DR PC for analysis purpose. In addition to this, DFR PC can be accessed through remote desktop connection. Kindly accept. | Kindly refer amendment-I, This HMI Workstation in Substation control room also be able to function as duplicate to DR PC provided in STATCOM Station is also acceptable. |
|  | 27. | 4.0 STATCOM Specification Rev-2 May-2020 | Clause No. 8.2.2.e Operator Interface e. A facility shall be provided whereby the local HMI features and functions shall be accessible from remote. A remote user shall be able to view screens and change STATCOM Station parameter settings. Access security shall be provided by password for each defined user level (viewer, operator, administrator etc.) to prevent unauthorized access | Please confirm that Remote location referred in this clause is Substation Control Room. | Confirmed |
|  | 28. | Technical Specification: Section-STATCOM Station, Rev02 (May, 2020) | Clause No. 8.10.1.ix Circuit Breaker MV Circuit Breaker The medium voltage circuit breakers in any of the branches shall be designed to switch off metallic three phase short circuits limited only by the transformer impedance of the STATCOM System (Coupling transformer) with the initial short circuit current and DC component according to IEC 60909-0... | Bidder understands that to meet this requirement, if required, breaker of higher voltage class shall be considered and protection settings shall be coordinated for safe operation. Please confirm. | Confirmed. |
|  | 29. | Technical Specification: Section-STATCOM Station, Rev02 (May, 2020) | 13.19 For the design purpose, following Power System parameters (at PCC) may be considered: Basic Insulation Level (BIL) -1550kVp | Based on the standard component design given in specifications, the BIL of 1425kVp will be selected as the BIL level for 400kV system. | The BIL of 400kV System shall be as per clause 13.19. However BIL of equipment shall be as specified in respective section of technical specification. |
|  | 30. | Volume-II Part 3 of 7 4.0 STATCOM Specification REV-2 | Clause No. 8.2.2 f) It is proposed to connect STATCOM Station SCADA with SAS through a Gateway and the database, configuration etc. of existing SAS shall be upgraded to incorporate STATCOM Station events, alarms, Controls (both switchgear and control functions of STATCOM Station like setting of parameters etc.) so that STATCOM Station can be effectively monitored and controlled from SAS. | We are providing Remote HMI at Substation control room as per requirement. Statcom station control and monitoring can be done via the same Remote HMI. Additionally the data (alarm & events) shall be made available in main substation SAS through Gateway. We understand this fulfils specification requirements. Please confirm. | Bidder to quote as per provisions of bidding documents. |
|  | 31. | Volume-II Part 3 of 7 4.0 STATCOM Specification REV-2 | Clause No. 8.2.2 f) all fault records (as per subsequent section) etc. is required to be uploaded to our National Transmission Asset Monitoring (NTAMC) Center located in Manesar, Gurugram, Haryana through a separate gateway either directly or through a server available in the sub-station for similar purpose for substation disturbance records | Bidder requests that details of Substation Disturbance Record Server will be provided during detailed engineering. Please confirm. | The required details shall be provided during detailed engineering stage. |
|  | 32. | Volume-II Part 3 of 7 4.0 STATCOM Specification REV-2 | Clause No. 8.2.1 The control system design shall be based on single fail criterion i.e. failure of any one component in the system should not result in to outage of the complete system | Please clarify if referred clause is also applicable to - BCU(bay control unit) for control of switchgears. - DC CT for measuring the valve current. | Confirmed. |
|  | 33. | Volume-II Part 3 of 7 4.0 STATCOM Specification REV-2 | Clause No. 8.3.2 r) List of Protection functions for STATCOM station STATCOM Branch Protection: i) Differential protection (87) | In place of differential protection, duplicate over current protection and converter blocking at high current in valve can be provided. | Offered protection is also Acceptable |
|  | 34. | Price_Schedule | Sch-1A, Clause 10.0 Mandatory Spares for STATCOM and 400kV Bay Equipment And Clause VI Coupling Transformer Nitrogen Sealing, Pressure Gauge and Pressure Switch - 1 set | Bidder clarifies that only those spares will be supplied that are required for operation and maintenance of the equipment. Please confirm. Therefore, Bidder understand that referred items may only be supplied if these items are required for operation and maintenance of coupling transformer being offered by bidders. Please confirm. | Confirmed. |
|  | 35 | Technical Specification, Section: Civil Works C/ENGG/SPEC/CIVIL/ Rev-11A/Jun’18 | Clause 20.22.2 In case pile foundation is not envisaged originally in the LOA then concrete and reinforcement steel shall be measured and paid as per items mentioned under relevant clauses as mentioned above. Boring installation including temporary casing, bentonite treatment, initial and routine tests etc. of pile will be paid as an extra item. In case extra quantity of cement is required to meet the provisions of IS: 2911, it will be paid as an extra item. | As soil investigation report as well as site address is not provided hence pile foundations cant be envisaged at this stage. Bidder understand that if pile foundations are envisaged during detail engineering, bidder shall be paid extra for 400 kV as well as STATCOM Station civil works as per refered clause. Please confirm. | Pile foundations are currently not envisaged. Bidder to qoute as per the provisions of the bidding document. |
|  | 36. | Technical Specification, Section: Civil Works C/ENGG/SPEC/CIVIL/ Rev-11A/Jun’18 | 20.27.1 Earth work in excavation and filling For hard rock excavation, the volume of hard rock shall be computed on the basis of stacks of excavated rubble after making 50% deduction for voids. The unit of measurement shall be in cubic meter. The unit rate shall include stacking, disposal of excavated material for leads up to 2000 meters beyond the levelling boundary. | As soil investigation report as well as site address is not provided. Hence, rock blasting & rock excavation cant be envisaged at this stage. Bidder understand that if rock blasting or rock excavation are envisaged during detail engineering as per actual site soil investigation report bidder shall be paid extra at actual for 400 kV as well as STATCOM Station civil works. Please confirm. | STATCOM Yard If excavation in hard rock (requried blasting) is encountered during site execution inside the STATCOM Yard, the same is deemed to be included in the BPS item for foundations and nothing extra shall be payable on this account. Area other than STATCOM Yard If excavation in hard rock (requried blasting) is encountered during site execution in the area other than STATCOM Yard, the same shall be paybale in the respective line item for excavation in hard rock (requried blasting). Bidder to qoute as per the provisions of the bidding document. |
|  | 37 | Vol II TECHNICAL SPECIFICATION: CIVIL WORKS C/ENGG/SPEC/CIVIL/REV -11A/JUN’18 | 1.7 General Unless levelling is in the scope of the bidder, fairly levelled site with single level/terraces with different levels/ gradual slope shall be handed over to the Contractor | We understand that levelled land will be handed over to contractor. We request you to provide the original contour of proposed switchyard area to assess the depth of filling done and the foundation depth accordingly. Also please confirm that FGL of STATCOM yard will be same as the Main switchyard and STATCOM yard will be in a single level. | 1. Contouring and site levelling is in the scope of the contractor. 2. FGL for STATCOM yard and other areas under the scope shall be decided during detailed engineering. Bidder to qoute as per the provisions of the bidding document. |
|  | 38. | Vol II TECHNICAL SPECIFICATION: CIVIL WORKS C/ENGG/SPEC/CIVIL/REV -11A/JUN’18 | 1.7 General Unless levelling is in the scope of the bidder, fairly levelled site with single level/terraces with different levels/ gradual slope shall be handed over to the Contractor | (i) In case original contour of switchyard area is not available, bidder request following data to perform bid engineering and cost estimates:- 1. Depth of filling 2. Levels in switchyard Above information is important to estimate civil cost. (ii) In case during execution if above data varies, contractor shall be allowed to claim commercial implications. Please confirm. | Contouring and site levelling is in the scope of the contractor. 3. FGL for STATCOM yard and other areas under the scope shall be decided during detailed engineering. Bidder to qoute as per the provisions of the bidding document. |
|  | 39. | VOL II TECHNICAL SPECIFICATION: CIVIL WORKS C/ENGG/SPEC/CIVIL/REV -11A/JUN’18 | 2.0 Geotechnical Investigation The Contractor shall perform a detailed soil investigation to arrive at sufficiently accurate conclusion regarding general as well as specific information about the soil profile and the necessary soil parameters of the site, in order to design and construct the foundation of the various structures safely and rationally | We request you to kindly furnish us the preliminary soil investigation report for estimating the bid stage civil quantities. In case during execution if above data varies, contractor shall be allowed to claim commercial implications. Please confirm. | Soil Investigation is in the scope of the contractor. Bidder to quote as per the provisions of the bidding document |
|  | 40. | TECHNICAL SPECIFICATION: CIVIL WORKS C/ENGG/SPEC/CIVIL/REV -11A/JUN’18 | 1.0 General All civil works shall be carried out as per design/drawings provided by the Employer/ Contractor and as per these specification provided by the Employer | Request you to furnish the employer supplied drawings (e.g. Foundation Drawings for Equipment & Tower etc.) for bid stage engineering & cost estimations. | Foundation drawings which are supposed to be issued by POWERGRID shall be shared to be successful bidder. Bidder to quote as per the provisions of the bidding document. |
|  | 41. | Technical specification: Section-Project- Rev-00 Annexure - VI | 1.0 General The building shall be of RCC framed structure, minimum grade of concrete shall be M25 design mix. | Considering short execution time we request employer to allow Steel Building (PEB) for STATCOM Converter Room & STATCOM Control Room Building as an alternative. | Bidder to quote as per the provisions of the bidding document. |
|  | 42. | Volume-II, Part-2 STATCOM Specification Rev-2 May-2020 | 8.1.5 Statcom Valve Cooling System h) Each cooling system shall be provided with independent/dedicated UMD supply however common battery for both UMD power supply may be accepted. A UMD system will provide an extended capability of the STATCOM Station to deliver reactive power without any interruption, adding a buffer against the system faults or during events such as delayed voltage recovery or TOV. | Please clarify if this clause shall be applicable for UPS also. Please confirm. | Acceptable subject to meeting the requirement of black start capability. |
|  | 43. | Volume-II, Part-2 STATCOM Specification Rev-2 May-2020 | 8.1.5 Statcom Valve Cooling System i) The secondary cooling system shall be redundant type such that it shall be possible to take out 10% (minimum one number) of the cooler module (fan unit) of secondary cooling system without affecting the rated performance of STATCOM). | We understand, in this clause, cooler module refers to single fan unit only. Please confirm. | Confirmed. |
|  | 44. | Technical specification: Section-Project- Rev-00 | Clause 2.2.1.l Fire protection system for STATCOM Station HVW System The contractor shall submit the pressure drop calculation and in case the necessary pressure is not available due to pipe size etc., the additional pipe or any other material to achieve the desired pressure is also in the scope of contractor. | (1). We understand that main station FFPH system shall already have necessary provision for STATCOM STATION and there shall not be any requirement of further augmentation under this contract. Bidder shall provide inputs related to STATCOM Station for sizing of main station firefighting system. Please confirm. (2). We understand that employer shall arrange 250 NB main header (with 6-7 kg/cm2 pressure) with end flange with isolation valve near STATCOM STATION for taking taping for HVWS / Hydrant systems. Please confirm. (3) Employer shall provide necessary (Maximum 16 Nos. at each location) annunciator windows in main station FFPH & Control room annunciator panel to Hookup STATCOM STATION fire fighting system. | 1). Confirmed 2) Please refer Clause 2.2.1 l) of Section project wherein it is mentioned The hydrant system shall be extended from existing firefighting system in the yard. The Details of existing hydrant system shall be provided to successful bidder during detailed engineering stage. 3) The fire detection & alarm system for STATCOM Building is in scope of bidder. These fire detection systems shall be connected to a separate Fire annunciation system clearly identifying the zone. |
|  | 45. | General | AIR CONDITIONING SYSTEM FOR CONTROL ROOM BUILDING | Please provide specification for Air Conditioning units for area other than converter hall (i.e. control room, battery room, Cooling system room etc) | 2TR & 3TR unit are to be considered for AC System(Except valve hall), in line with annexure-V, of section project,. The number of these units shall be decided based on heat load calculation to be submitted by contractor during detailed Engineering Further, BTU & Star requirement for these unit kindly refer modified clause in specific requirement rev 08 in Section-Air condition system Rev 04. |
|  | 46. | Price_Schedule | Sch-1b, 10.0 Mandatory Spares | There is no mention of mandatory spares of fire protection system in price schedule. Therefore, we understand that no spares are to be considered. Kindly confirm. | Confirmed. |
|  | 47. | Price_Schedule | Sch-1b, 10.0, XII b) Ventilation system motor of each type and rating-1set. | We understand that ventilation system to be read as AHU & DX unit for STATCOM. 1 set of each type and rating of motor used in AHU unit shall be provided as spare. | Confirmed. |
|  | 48. | Volume-II, Part 2 of 5_STATCOM SPECIFICATION_CL No. 8.7 | Air Core Reactors (for STATCOM, MSR, MSC branches etc.) k) Tests on Reactors: The reactors shall be subjected to type and routine tests in accordance with the latest issue of IEC-60076 as appropriate to the type of reactor provided. | For MSR reactors induced a.c. withstand voltage test is not feasible due to the high test power rating requirement and hence will not be conducted. According to IEC 60076-6 requirement of this test are fulfilled by lighting Impulse voltage test to be performed as routine test as per clause no 7.8.10.4 of IEC 60076-6. | Confirmed, however, BPI used to support the reactor shall be type tested as per IEC 60168. |
|  | 49. | Volume-II, Part 2 of 5_STATCOM SPECIFICATION_CL No. 8.7 | Air Core Reactors (for STATCOM, MSR, MSC branches etc.) k) Tests on Reactors: The reactors shall be subjected to type and routine tests in accordance with the latest issue of IEC-60076 as appropriate to the type of reactor provided. | For current limiting reactor due to small size temperature rise test are not practical and hence these test will not be performed. Kindly confirm. | Please refer amendment -I |
|  | 50. | Volume-II, Part 2 of 5_STATCOM SPECIFICATION_CL No. 8.7 | Air Core Reactors (for STATCOM, MSR, MSC branches etc.) a) Reactors shall be air core, dry type, be suitable for outdoor installation. No tapping on reactor shall be accepted. The insulation level shall be adequate. | (1) Please specify is bird cage protection arrangement is required. (2) As per IEC 60076-1, following service conditions have been considered for reactors considering specified maximum ambient temperature of 50 deg C: - Yearly average temperature = 30 deg C - Monthly average temperature of the hottest month = 40 deg C | (1) Required. (2) the design of reactor shall be as per meteorological data from authorized government department/website. |
|  | 51. | Volume-II, Part 2 of 5_STATCOM SPECIFICATION_CL No. 8.10 | STATCOM Station MV Switchgear The Circuit Breaker offered should be of SF6 type and of class C2, M2 as per IEC | Please confirm that MV disconnectors in STATCOM shall comply endurance class M1 and MV earth switches in STATCOM shall comply endurance class M0. | Confirmed. |
|  | 52. | Volume-II, Part 2 of 5_STATCOM SPECIFICATION_CL No. 8.10.4 | Surge Arrester The Contractor shall supply the surge arresters necessary for the protection of the equipment associated with STATCOM Station in accordance with the requirements specified. | Please confirm that surge counter will be required only for Surge Arrester at the HV side of coupling transformer. | Surge counter shall be required for all voltage class HV as well as MV. |
|  | 53. | Technical specification: Section-Project | Clause 2.2.1. (t) Visual Monitoring System for watch and ward of STATCOM Station Visual monitoring system (VMS) for effective watch and ward of STATCOM station premises covering the areas of entire switchyard, Statcom Building, Coupling Transformer, cooling Towers and Main Gate, shall be provided. | We understand switchyard in this clause refers to out door area of STATCOM Station fenced area only. | The VMS system for is to be provided as per clause 2.2.1 (t) of Section Project. |
|  | 54. | Technical specification: Section-Project | Clause 2.2.1. (t) Visual Monitoring System for watch and ward of STATCOM Station System with Colour IP Cameras for VMS surveillance would be located at various locations including indoor areas and outdoor switchyard and as per the direction of Engineer-In-Charge | We understand that the scope of VMS under the subject package is restricted only to Statcom Area and excludes the VMS for switchyard extension portion. Please confirm our understanding. | Bidder to comply the requirement mentioned in technical specification. |
|  | 55. | SPECIFIC REQUIREMENT’S (Section- Project) C/ENGG/SPEC/SEC-PROJECT/SPECIFIC REQUIREMENT REV NO 08 | Annexure S9 Visual Monitoring System for watch and ward of STATCOM Station Clause 1.1.3 The system shall use video signals from various types of indoor/outdoor CCD colour cameras installed at different locations, process them for viewing on work stations/monitors in the Control Room and simultaneously record all the cameras………………… | (1) We understand that Visual Monitoring System for watch and ward of STATCOM station is stand alone type. (2) Control room in this clause refers to STATCOM control room only. (3) Any kind of interfacing or integration with any other system of employer is not in bidders scope. We understand that the viewing point is Statcom Control Room Building. Any interface/integration of VMS System from existing Control Room Building/existing VMS system is not envisaged by the Bidder. Please confirm. | (1) VMS system for STATCOM Station area shall be separate from the existing VMS for substation. (2)Confirmed. (3) Confirmed. However, duplicate of VMS display in the Main Substation Control Room & further sending this VMS data to remote centres is also in the present scope. |
|  | 56. | SPECIFIC REQUIREMENT’S (Section- Project) C/ENGG/SPEC/SEC-PROJECT/SPECIFIC REQUIREMENT REV NO 08 | Annexure S9 Visual Monitoring System for watch and ward of STATCOM Station The System shall have provision of WAN connectivity for remote Monitoring | Offered VMS system will be provided with WAN port. Further connectivity (ie. For Remote monitoring e.t.c.) is not in bidders scope. | Provision for viewing the VMS data from Main Substation Control Room and further to remote centres is in the scope of bidder. |
|  | 57. | General | Earth Mat | Since soil investigation report is not provided, therefore, please provide earthmat spacing for bid engineering and preparation. In case of any variation in spacing of the earth mat during detailed engineering, contractor shall be entitled for variation order. Please Confirm. | Kindly refer new clause N.3 of Section Specific Requirement. |
|  | 58. | Volume-II, Section-Project | 13.15 Interface Points (f) ...Necessary cabling between STATCOM STATION and 400kV AC switchyard for this purpose shall be carried out by the contractor. | We understood that cabling between main switchyard /control room and STATCOM Yard shall be done through main switchyard cable trench being constructed in separate contract. No extension / construction / strengthening of the cable trench in existing station is considered in present scope. Please confirm. | The Cable trenches for laying of Cables between Equipment’s under Present scope and existing CRB/SPR is under present scope. However in case of space available in existing trenches the same can be utilized. |
|  | 59. | Volume-II, Clause 1.1.18 / Technical Specification : LT Switchgear Rev 05 | All Circuit breaker boards shall be of Single Front type, with fully draw out circuit breakers, which can be drawn out without having to unscrew any connections. | We understand that only ACB Compartments of corresponding LT Switchboards should be single front type. However other vertical can be single/double front depending on space availability and requirement. | Confirmed. |
|  | 60. | Price_Schedule | Sch-1b, 15.6 Main Lighting Distribution Board 15.7 Emergency Lighting Distribution Board | As per STATCOM LT SLD (C/ENGG/STD/STATCOM//LT/SLD/01); we understand that supply to Lighting panels shall be directly fed from ACDB. Therefore, the mentioned items of the price schedule are not required. Kindly update the price schedule accordingly. | Kindly refer amendment I |
|  | 61. | Volume-II, Section-Project | Clause 13.20 Average Lux Level i) 50 Lux- 400kV Switchyard equipments | Bidder understand this requirement is applicable for Coupling Transformer and associated 400 kV Equipment’s. Please confirm. | Confirmed, however, Additional 2nos of firewall mounted Flood Lights have to be provided for each 1- ph coupling Transformer for maintenance purpose. |
|  | 62. | Volume-II, Section-Project | Clause 2.2.1 s) Direct Stroke Lightning protection of STATCOM station area and 400 kV Switchyard is in the scope of Contractor. | It is understood that 400kV switchyard is being constructed in separate contract. The scope of DSLP protection is limited within new STATCOM STATION yard, Coupling Transformer and 400kV interconnection area only. | The DSLP Protection for STATCOM Yard, Coupling Transformer & Interconnection between 400kV Switchyard & MV Switchyard is under present scope. |
|  | 63. | Volume-II, Section-Project | Clause 2.2.1 r) Illumination Lighting and illumination of the switchyard extension area & STATCOM Station area are covered under present scope. | It is understood that 400kV switchyard is being constructed in separate contract. The scope of illumination is limited within new STATCOM STATION yard, Coupling Transformer and 400kV interconnection area only. | The Illumination for STATCOM Yard, Coupling Transformer area & Interconnection between 400kV Switchyard & MV Switchyard, 400kV Bays for STATCOM is under present scope. |
|  | 64. | Volume-II, 3.STATCOM Specification Rev-2 | 8.2.1 Control Equipment e). The Controller shall have at least 10% excess I/O capacity to allow future program upgrades to satisfy the changing requirements of the power systems or future extensions to the STATCOM Stations. As a minimum a control of up to 4 future HV shunt devices (reactors or capacitors) shall be included in the offer. | (1) We understand requirement of control of up to 4 HV External devices for future specified in referred specification / clause is general requirement and is superseded by requirement specified in Section Project. Following requirement specified in In Section- Project (2.3.4) shall be considered : Provision in the control system for integrating additional 02 Nos. of 240MVAr, 765kV Bus Reactors and 1 no. of 125 MVAR, 420kV Bus Reactor in future. Please confirm. (ii) Also, please specify the switching requirement of LV MSR/MSC in case VSC is OFF. | The requirement of 4 future HV shunt devices (reactors or capacitors) mentioned in Section-STATCOM Station include the requirement of future 420kV Reactors specified in Section-Project. ii) MSCs/MSR alone may be permitted to Switch IN/OUT, when all the STATCOM Branches of a STATCOM Station are out of Service. |
|  | 65. | Volume-II, 20.Section-Sub-station Automation_Rev04 | 2.3 FUNCTIONAL REQUIREMENTS The high-voltage apparatus within the station shall be operated from different places: Remote control centres Station HMI Local Bay controller IED (in the bays) | We understand high-voltage apparatus, specified here refers to 400 kV switchgears only. Please Confirm. | Confirmed. |
|  | 66. | Vol - II STATCOM Specification Rev. 2; clause 8.2.2.f | Operator Interface As the sub-stations, where STATCOM Station shall be installed, are equipped with Sub- station Automation System (SAS) conforming to IEC 61850, it is required that STATCOM Station control and monitoring shall be integrated with SAS already provided at Sub-stations by the Contractor. | Employer to confirm that the gateway of the main substation SAS will receive data from STATCOM gateway on IEC61850 protocol. | Requirement of Technical Specification shall prevail. |
|  | 67. | Price_Schedule; Sch-1b;10.0, I & STATCOM Specification Rev. 2 & Section-Project & Elsewhere | Power Module | Please note that with reference to the above clause we understand that the Power Module as mentioned in the clause is same as the term Sub-Module defined in Section-STATCOM Rev.02 as "Basic single power module of a Modular Multi-Level STATCOM unit Valve. It is Part of a STATCOM unit valve comprising, controllable switches and diodes connected in full bridge arrangement, together with their immediate auxiliaries, and storage capacitor, where each controllable switch consists of one or more switched valve device(s) connected in series." | Confirmed |
|  | 68. | Vol II: - Section Project | The bidder is also required to provide complete Substation Automation System of STATCOM Station. The SAS for STATCOM station shall be a separate;… | Please clarify that SAS for STATCOM is the same as the control system for STATCOM and not a separate SAS as used for sub-station. | Bidder may Quote as per Provision of Bidding Document |
|  | 69. | Vol II: - Section Project 2.2.2.2.a(iv) | Permanent water supply for STATCOM building. | We Understand PGCIL will provide the permanent water supply at the edge of the STATCOM building from where the STATCOM contractor has to connect to the plumbing inside the STATCOM building. Please confirm. | Kindly refer cl 14 of the Technical Specification, Section: Civil Works, Rev 11A wherein it is specified that POWERGRID will provide a water supply point at any one location within the substation. Contractor shall carry out plumbing/ erection works from that supply point to the STATCOM building etc. Bidder to qoute as per the provisions of the bidding document. |
|  | 70. | Vol II: - Section Project 2.2.2.2.a(v) | Laying of plumbing and external sewerage system for STATCOM building | The laying of external sewerage system is between the STATCOM building and the external septic tank & soak pit as defined in the clause 2.2.2.2.(vi) to be constructed with in STATCOM STATION. | Bidder's understanding is correct. |
|  | 71 | Vol II: - Section Project 2.2.2.2(l ) | New fencing including gate in the STATCOM Station area including dismantling, re erection, rerouting of the existing fence if required. The serviceable material during dismantling may be used for re erection. | The layout of the sub-station showing the STATCOM area may please be provided to estimate the quantities for dismantling, re-erection and re-routing of fence and gates. | Bidder to quote as per provision of bidding documents. |
|  | 72 | Vol II: - Section Project 2.2.2.7 | Glass Fibre Reinforced Polymer (as per manufacturer’s specification) shall be used instead of steel reinforcement in reinforced cement concrete (RCC) if required. | Please confirm that only Glass Fibre Reinforced Polymer reinforcement shall be used for foundations of reactors if the magnetic circle extends below the footing of the reactors. | Confirmed |
|  | 73 | Vol II: - Section Project 2.2.1.j | Control of following bus reactors shall be provided in STATCOM station controller for coordinated reactive power control & supplementary VCS current control of external devices at RAMGARH PS substation: • 02 Nos. of existing 125MVAr, 400kV Bus Reactor connected to 400kV substation bus. • Provision in the control system of integrating additional 01 Nos. of 125MVAr, 400kV Bus Reactor connected to 400kV substation bus envisaged in the future. | Please confirm that no switchable line reactors have to be considered for control by the STATCOM | Confirmed. |
|  | 74. | Vol II: - Section Project 2.2.1.k | Interface panel (if required) shall be provided for exchange of signals from the existing 400KV substation equipment (available in the form of potential free contacts) with control and protection system of STATCOM STATION, services and facilities. | Please clarify the location of this interface panel - STATCOM building or main substation building or any Switchyard Panel Room | Location of interface panels shall be decided by Bidder based on availability of space. |
|  | 75. | General | Auxiliary Supply | 1) Employer is requested to confirm the voltage level of the auxiliary power source e.g. 33kV / 11kV or 415V, 3-phase, 50 Hz along with the maximum variation in voltage and frequency. 2) In order to ensure fair and equitable costing consideration between all Bidders, it is requested that Employer confirms the energy rates at which the auxiliary power will be charged (in case Bidder opts to take Employer's auxiliary power connection). 3) Employer is requested to confirm the location of the auxiliary power source so that the further distribution can be planned accordingly. Alternatively, the Employer is requested to confirm maximum cable routing distance between STATCOM STATION entrance gate and the single point auxiliary power connection. 4) Employer is requested to confirm that the charges for auxiliary power will apply only when used by Contractor for construction purpose. Hence, the auxiliary power consumed by the STATCOM STATION Facilities (e.g. HVAC system, valve cooling system, C&P system, etc.) after installation for powering up of individual equipment / system and its subsequent testing and commissioning shall not be payable by Contractor. Please confirm. 5) Employer is requested to confirm that the energy consumption at 400kV level (i.e. from point of coupling onwards up to STATCOM station) for energization of STATCOM station and subsequent testing, commissioning, trial operation, etc. will not be chargeable to the Contractor. 6)We understand that the Employer shall make available the auxiliary power supplies on chargeable basis at a single point in the Sub-station with in one month of Notice of award (NOA). Employer will charge only as per the energy charge on unit rates of the states. The fixed costs will not be charged. | 1), 2), 3) & 6) For auxiliary supply refer Cl. 14.3.1 in Section-GTR of Technical Specification. 4). Acceptable 5) Acceptable |
|  | 76. | General | Auxiliary Supply | The temporary power supply used for construction purposes is not foreseen (due to quality or power and low capacity) to be used as a source to run/ test the STATCOM / charge the battery bank. Any power used to test/run the STATCOM and its auxiliaries (battery chargers, UPS, ventilation, air-conditioning, etc) shall be provided by the Employer free of cost. | Acceptable. |
|  | 77. | General | Potable Water | Potable water to be used in the STATCOM building shall be supplied by the Employer from his treatment plant free of charge. | For water supply refer Cl. 14.3.1 in Section-GTR of Technical Specification. |
|  | 78. | Vol II: - Section Project 13.15.(g) | Employer has provided 400kV CVTs at the bus. Contractor may take signals from these CVTs as required for synchronizing and bus voltage monitoring purpose for which necessary cabling arrangements from respective junction boxes of these equipment to STATCOM STATION shall be in the present scope. | The location of the Bus CVTs may please be marked on the station layout together with the cable trenches for estimation of cabling requirements. Else, provide the cable route distance of these CVTs from STATCOM Yard. | Layout of Ramgarh-II Substation is under finalization, same shall be provide to successful bidder during detailed engineering of STATCOM. |
|  | 79. | Vol II: - Section Project 12.1 | Employers personnel stationed at the .....Contractor's office/works, the association / training of these engineers shall constitute 1 man months and at Employers office/site shall constitute 2 man months for which price shall be quoted in the BPS. The broad break up of man months for Training shall be as follows: a) System engineering design and equipment Specification: 2 man months b) Operation and maintenance: 2 man months c) Operation and maintenance hands on Training at site:2 man months (1 man month = 20 man days) ...... | (1) We understand that the man-months indicated are for the Employer's personnel. We request employer to specify minimum number trainees per training batch (e.g.. 5 personnel per batch). (2) It is understood that 1 man month = 4 man weeks, 1 man week = 5 man days. Hence 1 man month = 20 man days. Please confirm. | Requirement of technical specification shall prevail. |
|  | 80. | Vol II: - Section Project 12.1 | The training shall be carried out at the place of manufacture, design and engineering offices or as agreed by the Employer so as to ensure the complete adequacy of the program and the imparting of detailed knowledge of all aspects of the STATCOM STATION system. | The Bidder understands that trainings to be carried out in hybrid mode (remote/classroom/on-job). | Confirmed. |
|  | 81. | Volume-II, Technical specification: Section-Project- Rev-00 Annexure-III S. No. 7 | Transformer Winding Resistance Testing Kit …..... The equipment shall have eight Independent measuring channels…...... SPECIFICATIONS Input Voltage: 240V, 50Hz, 1-Phase AC supply Output : Current Ranges : Variable 5 mA - 10A (dc) Open-Circuit Test Voltage: 50 Vdc | In the specified make/model (MTO 330), the open circuit test voltage available is 40 V dc. Alternatively, Scope make TRM 25 has open circuit test voltage of 50Vdc but has 5 measuring channels instead of specified 8. Please confirm acceptance of Scope make of testing kit. | The make of testing kit shall be finalized during detailed engineering stage. However technical details mentioned in bidders query are acceptable. |
|  | 82. | Volume-II, Technical Specification: Section-STATCOM Station, Rev02 (April, 2020) 8.9 | Coupling Transformer General | As there is no specific requirement / restriction on CRGO grade for Transformer in technical specifications, the CRGO grade as per manufacturer's design and shall meet the requirements of the technical specifications. Kindly confirm our understanding. | Bidder may Quote as per provision of Bidding document |
|  | 83. | Volume-II, Technical Specification: Section-STATCOM Station, Rev02 (April, 2020) 11 | Commissioning Responsibilities The Contractor shall supply the testing equipment for the dielectric tests and all measuring devices, including instrument transformers, oscillograph, etc., for tests performed at the Site. These instruments and instrument transformers shall be previously calibrated against accepted standards. | We understand that the "Annexure-III (Rev-0) -STATION OPERATION AND MAINTENANCE & TEST EQUIPMENT" includes all types and required quantity of testing equipments; and that these can be used at site by the Contractor during on-site testing and commissioning. Further, in case any additional testing equipment’s (...i.e. which do not classify as special testing equipment) are brought by the Contractor to site, these will be supplied on returnable basis. Please confirm this understanding. | Bidder understanding is generally in order. Further, in case bidder utilize the supplied operation, maintenance & test equipment’s, the same including its consumables shall be refurbished before handing over to site. |
|  | 84. | Volume-II, Technical Specification: Section-STATCOM Station, Rev02 (April, 2020) 8.9 | Coupling Transformer General | PGCIL may confirm the type of bushings for HV/ MV/ Neutral (Oil filled condenser type/ RIP bushing with porcelain or composite insulator/ solid porcelain or oil communicating type). Alternatively please clarify, if bidder can select suitable type of bushing as per design requirements. | Kindly refer Section-Transformer (upto 400kV class) rev 13 attached with the bidding document. |
|  | 85. | I 04_Section-III- Bid Data Sheets (BDS) | Sr. No. 66, Time for Completion 21 (Twenty One Months) | Considering experience from previously executed STATCOM stations in India with similar scope, requirements of localisation etc., where site was already in possession of employer and all soil data was available to start engineering immediately after award of contract, these STATCOMs were completed in 24 months. Further, supply chain conditions for STATCOM components have worsened in last 2 years. Therefore in line with past projects execution experience a project completion schedule for this size of STATCOM Stations shall be allowed as 24 Months without any delay penalty. However bidder shall make efforts to achieve early completion with in 21 Months duration. if required employer can consider incentive for early completion. Please confirm. | Bidder to quote as per provision of bidding documents. |
|  | 86. | Vol - II Section: STATCOM Stations Chapter 6.2.4, page 18 | Chapter 7.3 of CIGRE Publication 139 together with information in PSSE network files given in Tender Stage shall be used for the Network harmonic impedance. | No harmonic network impedances are available, therefore to provide reasonable harmonic performance and rating calculations the CIGRE (WG 14.30) [4] sector approach was used to calculate the harmonic network impedances based on the specified short circuit power of the network. Please confirm your acceptance. | Noted. |
|  | 87. | Vol - II Section: STATCOM Stations General | Number of switching for MSC & MSR are not defined. | Number of switching events of the MSC/MSR is not defined within any document. Hence, Switching stresses may be calculated as per IEC 60871-Part1. | Noted. |
|  | 88. | Vol - II Section: STATCOM Stations Page 47, 8.9.1 | To ensure minimum harmonic generation, the saturation flux density of the transformer should be higher than the maximum flux density reached over the full steady state (continuous operating) range, and the bidder should state the margin by which it is exceeded. This margin shall be at least 10%. This maximum flux density (over the full steady state range) is obtained at the highest secondary voltage during any reactive power generation, highest reference voltage, minimum slope, and minimum continuous frequency. The Contractor shall submit B-H curve to substantiate this requirement. The flux density at the highest secondary voltage shall lie in the linear portion of the B-H curve. Any harmonic generated by the transformer should be considered by the design of the STATCOM . | The highest voltage on secondary side occurs when the band (0.95-1.05) is set to zero, held at 1.05pu primary voltage, slope is 0% and the STATCOM STATION (including MSCs) operates with its nominal capacitive output. It is understood that this highest voltage plus the specified safety margin of 10% shall be used for the transformer knee point. Please confirm. | Noted, however, in case during details engineering if max flux density is achieved at any other point , it shall be used for design of transformer. |
|  | 89. | Vol - II Section: STATCOM Stations Chapter 6.1.8, page 16 | STATCOM station response shall be such that the change in measured system voltage to small disturbance should reach 90% of the desired total change within 30ms of the initiating a 5% step change of voltage reference. | Bidder clarifies that these response times are achievable/applicable only to the STATCOM branches. Please confirm this understanding. | Noted. |
|  | 90. | Section: STATCOM Stations Rev 02 Chapter 8.6, page 41 and Chapter 8.5, page 41 | The MSC Components shall be designed with the aim to achieve operation according to the overall performance requirements of the STATCOM Station. And The MSR Components shall be designed with the aim to achieve operation according to the overall performance requirements of the STATCOM Station. | The bidder clarifies that the dynamic performance requirements of the STATCOM station shall be met using STATCOM Branches only whereas steady state performances shall be met using MSCs & MSRs. In this way the overall performance requirements of the STATCOM STATION are met. Kindly confirm this understanding. Alternatively please elaborate "Overall performance Requirements" with respect to individual elements (e.g. MSCs. MSRs & STATCOM). | Bidder understating is generally in order. |
|  | 91. | Vol ll Section Project Cl. 12 | Association and Training of Employer personals Cl. 13.1 Scope The Contractor shall submit …................................ Wherever the Employer intends to have Employers personnel stationed at the Contractor's office/works, the association / training of these engineers shall constitute 1 man months and at Employers office/site shall constitute 2 man months for which price shall be quoted in the BPS. The broad break up of man months for Training shall be as follows: a) System engineering design and equipment Specification: 2 man months b) Operation and maintenance: 2 man months c) Operation and maintenance hands on Training at site:2 man months (1 man month = 20 man days) | As per 3rd paragraph of referred CL. number, training is required for 3 man months (1 man month in Contractor’s office/works + 2 man months in Employer’s office/site), however as per next para where breakup is specified, training is required for 6 man months as mentioned in the next clause (4 man months in Contractor’s office/works + 2 man months in Employer’s site). Please clarify duration of trainings to be considered by bidder under subject project. | Training is required for 6 man months (4 man months in Contractor’s office/works + 2 man months in Employer’s site) in line with breakup of the mentioned clause . |
|  | 92. | Vol ll Section Project Cl. 12 | Association and Training of Employer personals General | Bidder understand that that the training requirements mentioned at various sections / clauses in tender documents e.g. Section-Project, Section-SAS Rev04 (Cl. 12.0), etc. are deemed to be included in the total number of man months mentioned under Cl. 12.1 of Section-Project. | Bidder understanding is generally in order. |
|  | 93. | Vol ll Section Project Annexure - IV | Details of System Studies to be performed 1. GENERAL ….......................... The Contractor may note that the following list is only indicative and if any other studies, calculations etc. are required the same shall have to be done by contractor without any extra charges to the employer. | Predefined studies in tender documents cover a large spectrum of cases according to the needs of the customer. In case other extra studies are needed by the customer they should be discussed separately. If additional studies other that what is envisaged in the Technical Specification are required at project stage the same shall be discussed with the successful bidder. The time schedule and commercial terms shall be mutually agreed. Please Confirm. | The provisions of the Technical Specification are amply clear and bidder shall follow the same. |
|  | 94. | Vol II Section STATCOM Cl. 8.1.5. r | STATCOM Valve Cooling system The power losses are transferred to the external ambient by means of a deionized water /air heat exchanger. All the piping and other components Complete instrumentation set has been mounted on board in order to check the status of the cooling system: • Conductivity gauge system. • Flow meter equipped with two set points (alarm and trip). • Pressure meter • Two thermometers for inlet and two thermometers for outlet (two set points for alarm and trip) • Thermostat | As per bidder's standard design, Two Nos. Inlet Temperature Sensor is provided with Alarm and Trip, But Two Nos. Outlet Temperature can be provided with Alarm. As per Bidder Design the Outlet Temperature sensor will not act as Trip Sensor. Please confirm if this is acceptable. Bidders proposal is inline with previously executed STATCOM projects. | Bidder’s understanding is generally in order. However, all signals associated with Valve Cooling System (including for indicators like pressure meter) shall be displayed in local HMI and recorded in STATCOM Station SAS. |
|  | 95. | Vol II Section STATCOM Cl. 8.1.5. t | STATCOM Valve Cooling system Replacement of certain cooling equipment (e.g., pumps, fans, cooler unit etc.), if defective, should be possible while the cooling system still operates. | Bidder clarifies that replacement of cooler unit (Cooler Bank / cooler module) shall not be possible while STATCOM is in service at full load, as only 10% redundancy in cooler modules (Fan units) has been specified. However replacement of cooler units shall be possible at reduced load. Please clarify requirement. | Bidder to follow the requirements of technical specification. It basically envisages that it should be possible to replace certain cooling equipment without the outage of complete cooling system. |
|  | 96. | Vol II Section STATCOM Cl. 9.7 | Software Simulation Models If any other proprietary software's are used by the contractor for system control design, the contractor shall provide these software's with perpetual license for use by the Employer. | We will be using RSCAD software for network simulation in our RTDS; but the software license and simulation model are not foreseen to be handed over to PGCIL. The software of the STATCOM control (SVC PLUSCONTROL) is proprietary and hence no logic diagram / documentation / user manuals shall be provided. Please confirm. | No Licence of STATCOM Software is envisage. Block diagram level details for all functionality to be provided for STATOCM STATION Control. |
|  | 97. | Vol II Section Project Section 13.13 | For integration of STATCOM control and protection system, the configuration of hardware, software, its integrated testing (both dynamic and steady state) is to be carried out at the works. Simulation testing is required to be carried out on RTDS. During RTDS testing and configuration, POWERGRID representative is required to be closely associated. | Bidder understand that Protection relays testing to be done by Via Omicron and an integrated testing of Protection & Control System however RTDS modelling of Protection relays is not foreseen , But control system testing as well as protection functions which are part of control system will be performed through RTDS. Please Confirm. | Confirmed. |
|  | 98. | Vol II Section STATCOM Cl. 8.1.3 | Sub module for Modular Multi-Level Topology Sub module shall be designed to guarantee high maintainability with self-sealing type hydraulic valves and electrical plugs for ease of installation or un-installation. | It is understood that instead of electrical plugs, the power connections between the submodules can be alternatively made using removable bus bars. | Confirmed. |
|  | 99. | Vol II Section STATCOM Cl. 8.1.2 | Semiconductor Switches Basic semiconductor devices shall be of the Press Pack type, or packaged to provide short circuit means in case of device failure such that the STATCOM can continue to operate without interruption. | It is understood that bidders who do not use "press pack" or "packaged to provide short circuit" design can propose alternative design where in the functional requirement is met by incorporating the bypass switch as an external device to the AC connections of the sub module. | Acceptable if meeting the functional requirement mentioned in the specifications. |
|  | 100. | Vol II Section STATCOM CL. 6.1 (m) | Section-STATCOM Station, Rev02; 6.1. m The term "firing" or "valve firing" has been used at various places in the specification in connection with the STATCOM technology. | Since we are using IGBTs in the STATCOM technology, hence there will be IGBT switching only and no valve firing. Hence, the term "firing" or "valve firing" may be read as "switching" or "IGBT switching". Kindly confirm this understanding. | Confirmed |
|  | 101. | Vol II Section STATCOM | A.2 Relevant Standards: STATCOM station shall comply with following standards (latest version) 1. Voltage source converter (VSC) valves for STATCOM : IEC 60747 6. 400 kV Power transformer (Coupling Transformer) : IEC-60354. 14. Cyber Security : IEC-62243 | 1. IEC 60747 is generally not applicable for the proposed multi- level configuration. However, some definitions used by the OEMs of the semiconductor switch are based on IEC 60747. Kindly confirm this understanding. 6. Please note that the standard IEC 60354 has been withdrawn by IEC and has been replaced by IEC 60076.We understand that the same shall be considered. Please clarify our understanding. 14. We understand that in place of IEC 62243 which relates to "Artificial Intelligence Exchange and Service Tie to All Test Environments." the international cyber security standards and recommendations like Govt of India guidelines and IEC 62443 can be considered. Please clarify our understanding. | 1., 6. 14 Bidder’s understanding is generally in order.. |
|  | 102. | Vol II Section STATCOM Cl. 6.1 (i) | STATCOM Station Ratings The bidder shall assume the negative sequence voltage of 1% at rated short circuit level and provide control to reduce this unbalance. | Bidder understands that the specified negative sequence is only valid for the STATCOM because a single phase operation of MSRs and MSCs is not possible (only three phase operation). Kindly confirm this understanding. | Bidder understanding is generally in order. |
|  | 103. | Vol II Section Project Cl. 8.0.(II) | Availability Spares The Contractor shall supply the spare parts required to meet the specified guaranteed availability and shall include such spare parts in the scope of supply. The detailed lists of spare parts to meet the guaranteed reliability & availability requirements shall be part of the contract documents. | The bidder doesn't envisage supply of any separate availability spares because the guaranteed availability is being met considering the mandatory spares specified in TS. As per specification, the availability period will start six months after trial operation. The mandatory spares will be delivered site before scheduled completion date (i.e. final commissioning). During the availability monitoring period, in the event of failure of any component leading to forced outage (complete or partial), the failed component will be replaced from the stock of mandatory spares available at site. At the same time, a new spare will be ordered and delivered to site by Contractor in order to replenish the stock of mandatory spares. Hence, there shall be no need to keep any additional availability spares at site. Kindly confirm your acceptance. | Noted. However, any outage during availability & reliability guarantee period due to unavailability of spares shall be attributable to the contractors account. |
|  | 104. | Vol II TECHNICAL SPECIFICATION: CIVIL WORKS C/ENGG/SPEC/CIVIL/REV -11A/JUN’18 | 1.7 General Unless levelling is in the scope of the bidder, fairly levelled site with single level/terraces with different levels/ gradual slope shall be handed over to the Contractor | Bidder further wants to clarify that : 1. Handing over of encumbrance free levelled land with in one month of Notice of award (NoA). 2. Approach road shall be provided with in one month of Notice of award (NoA). 3. Here approach road means road suitable for general transport of construction material and STATCOM STATION Equipment’s. Please confirm. | The timelines of activities described in Queries shall be as per Approved L2 Schedule. |
|  | 105. | Vol II Section Project Annexure-III, Sr. no. 9 | Capacitance, Inductance & Resistance Meter The equipment should be Table top and should be able to carry out measurement of R,L &C of valve components. | The specified meter is not part of the Bidder's standard tools for convertor because as the OEM we do not recommend/require measurement of R, L, C of our valve components for O&M as the same is not necessary. Nevertheless, the bidder will supply the Capacitance Inductance and resistance meter as per specification and it can be used by Employer for their own application other than the converter. | Bidder to Quote as per Bidding document. |
|  | 106. | Vol II Section STATCOM Cl. 6.8.11 | Guaranteed of Failure Rate - AC Power Capacitor Till the expiry of guarantee period, all replacement for failed units shall be supplied by the Contractor free of cost. | Bidder understand that till the expiry of Defect Liability Period, all replacement for failed units shall be supplied by the Contractor free of cost in accordance with the terms & conditions mentioned in General Conditions of Contract (GCC). Please confirm. | Confirmed. |
|  | 107. | Technical specification: Section-Project- Rev-00 | Clause 6 Basic Reference Drawings ... The Single line diagram and general layout drawings for Ramgarh substation will be finalized during execution stage and shall be provided subsequently during the detailed engineering of STATCOM station. | As the drawings ( SLD, GA drawing, cable trench layout) of the existing s/stn. are not available, and employer have denied to provide same during bidding stage, following considerations are made for BID submission, 1. The min. area required for new Statcom station shall be 175 x 175 m. 2. No additional tower/ gantry shall be envisaged between Statcom transformer 400kV I/C bay Gantry and Statcom transformer HV ( 400kV) bushing. Any variation to these quantities shall be paid at actual. Please confirm your acceptance to allow an uniform understanding across the bidders. Alternatively, bidder request employer to shift these items under unit rate quantities. | The detailed engineering for Layout is to be done by contractor during detailed engineering stage. In the land of RAMGARH appropriate spare for Installation of STATCOM shall be provided. At present no tower/gantry is envisaged between 400kV Switchyard and coupling transformer. However in case gantries/towers required for Isolator based Switching arrangement the same shall be included in scope of work. |
|  | 108. | Vol II Section Project Annexure-V | AIR-CONDITIONING AND VENTILATION SYSTEM Necessary copper piping (with necessary insulation) will be laid for interconnecting the outdoor and indoor units (Condensing unit & AHU).Condensing unit will be installed outside of the building at a suitable location as per site condition. | Bidder understand that in line with previously executed STATCOM projects, mechanical items meant for outdoor installation e.g. condensing units, outdoor units of split AC units, etc. shall be installed on the roof of the building. Kindly confirm. | Mechanical item meant for outdoor installation will be installed outside of the building at a suitable location as per site condition and shall be finalized during detailed engineering. |
|  |  | Vol II Section Project 2.5 | System Engineering and Studies The contractor ….................................................. The Employer shall have right to observe and participate in the studies performed as a part of the Contract and shall have access to all data necessary for complete understanding of the purpose of such studies as well as the validity of the results. The Contractor shall give the Employer at least thirty days prior notice before commencement of the above studies. | The participation is understood to mean review & verification of design results only; and will be done after the studies have been completed by the Contractor. There will be trainings about the Contractor STATCOM technology, the software packages and the models provided by Contractor for the customer to get a complete understanding. Moreover complete documentation will also be handed over to customer. Therefore, please note that the Employer's study team will only be involved in the discussion on the study and cannot participate in the studies during project execution as the design and engineering process remains the intellectual property of Contractor. Please confirm. | Noted. |
|  | 109. | Vol II Section Project General | General | Site tests shall not be performed for the spares. Handing over shall be done based on the physical inspection or factory inspection wherever applicable. However general check and physical verification shall be offered. Kindly confirm. | Confirmed. |
|  | 111. | TECHNICAL SPECIFICATION SECTION-GENERAL TECHNICAL REQUIREMENTS | Clause No. 3.2 10.15 The equipment offered by the contractor shall at least conform to the requirements specified under relevant IS standard. In case of discrepancy between IS and other international standard, provisions of IS shall prevail. The Contractor shall also note that the list of standards presented in this specification is not complete. Whenever necessary, the list of standards shall be considered in conjunction with specific IS. If the IS standard is not available for an equipment/material, then other applicable International standard (IEC / Equivalent), as per the specification, shall be accepted.” | Bidder request PGCIL to provide list of all applicable Indian standard for this contract, to avoid any ambiguity during execution of contract. | Please refer Annexure-C of Section GTR |
|  | 1. | Project, Clause no2, Scope of work | List of mandatory spares | Bidder is not able to trace list of "Mandatory Spares" to be supplied as a part of this project. Request you to please provide the same. | Please refer Bid Price Schedule. |
|  | 2. | Price Schedule 10(a) Power module (Sub-Module) spares | Semiconductor based Power module (sub-module) of multi modular valve of each rating and type - 1set | Bidder request PowerGrid to please provide the definition of "1set" | 1 set means quantities required for Complete replacement for 1- phase of STATCOM Unit/Branch. |
|  | 3. | Technical Specification: Section-STATCOM Station clause no 3. Scope of work | The total cumulative Capacitive (+ve) and Inductive (-ve) MVAR rated Capacity of STATCOM Station as defined in Section project comprising of STATCOM, MSCs (as applicable), MSRs (as applicable), Coupling Transformer, Coupling Reactor or any filter (if applicable) shall be rated at 1 p.u. voltage, 1 p.u. frequency and 20 deg C ambient temperature at 400 kV Bus (Referred to as “Point of Common Coupling” or PCC). The rated capability of STATCOM, MSC (as applicable) & MSR (as applicable) shall be at 400 kV (Referred to as “Point of Common Coupling” or PCC) and in the steady state frequency range of 48.5 Hz-50.5 Hz. | 1) Please confirm whether the cumulative MVAR of +550 / -425 MVAR to be fulfilled at PCC OR individual MSC and MSR rating of 125 MVAR at 1 pu voltage at 400kV when connected without any other branches also to be fulfilled? 2) Please confirm whether the MSC/MSR capacity of 125MVAR is at total cumulative capacitive output of 550/425MVAR or when one MSC/MSR or for two MSCs/MSRs alone connected. | Kindly refer clause no 2.1 of section project. |
|  | 4. | Technical Specification: Section-STATCOM Station clause no 3. Scope of work | The STATCOM Station including STATCOM Units, MSCs and MSRs shall be designed to operate continuously under the worst possible combination of steady state voltage and frequency range of 360- 440 kV and 48 Hz – 52 Hz respectively and transient and temporary over voltages defined in Clause 6.1-e). | As per clause 5.2 & 5.3 the ac system voltage range is 380kV to 420kV. Request you to please confirm whether bidder need to design STATCOM continuous operation rating based on clause 3 (Para 3) OR based on clause 5.2 & 5.3 . | Design of STATCOM Station shall be so as to operate continuously in the range of 360-440kV as given in the Specification. |
|  | 5. | Technical Specification: Section-STATCOM Station 6.1 j) STATCOM Station Ratings | The injected harmonics by STATCOM Station under the full operating range measured at 400 kV Bus (PCC) in accordance with IEEE-519-2014 and limiting values of individual harmonic distortions and total harmonic distortion shall be 0.5% and 1 % respectively. | Please note that, conventional CVT and IVT are not in position to measure the harmonic voltage at the secondary side of the VTs because the bandwidth of the VTs are not enough to measure the harmonic voltages up to 3kHz. Only RCVT or PQ Sensor installed in CVT can measure the power system harmonics exactly. It is recommended to specify RCT or PQ Sensor or other similar devices for the VTs used for STATCOM control. | The bidder may quote asper bidding document, Any additional requirement to met the specification shall be deemed included in scope of bidder. |
|  | 6. | Statcom Station 6.1.2.10 Coordinated reactive power control of external devices | To optimize the use of dynamic vars versus steady state vars, control of externally connected shunt capacitor or reactor banks as applicable shall be implemented. | 1) We recommend you to please specify maximum number of external devices to be controlled as part of standard specification. 2) Please suggest methodology of external device control i.e. the standard direct control with hard wiring between STATCOM controller and external devices OR communication via the existing SAS. | 1) Kindly refer amendment -I 2) Communication for control of external devices via existing SAS is to be adopted by the bidder. |
|  | 7. | Statcom Station 6.1.8 STATCOM Station Response | STATCOM station response shall be such that the change in measured system voltage to small disturbance should reach 90% of the desired total change within 30ms of the initiating a 5% step change of voltage reference | 1) Please request you to please clarify this clause based on Clause 8.2.2 of IEEE std. 1052-2018. - According to the clause (in the IEEE std.), the step response is defined as the response of PCC voltage to the step change of voltage reference. 2) Please define the phrase “small disturbance,” in % value of voltage step change. Please also specify the slope setting value for the response time test. 3) Please note that, Step response is applicable for STATCOM only, not for slow switching devices like MSCs and MSR. The specification says "STATCOM station" response to be fulfilled. MSCs and MSR switching is associated with time delays We recommend to amend the statement accordingly. | Bidding document are amply clear. |
|  | 8. | Technical Specification: Section-STATCOM Station 6.2.4 Harmonic calculation | Chapter 7.3 of CIGRE Publication 139together with information in PSSE network files given in Tender Stage shall be used for the Network harmonic impedance. | It is understood that Bidder can use the sector diagrams defined in Clause 7.3.2 of CIGRE Brochure 139, based on the specified short-circuit level at 400kV PCC. Please confirm. | Kindly refer reply against similar clarifications sl. No 86 above . |
|  | 9. | Technical Specification: Section-STATCOM Station 9.7b) transient model | The vendor should provide a detailed STATCOM Station transients model for use in [PSCAD and EMTP-RV] transients simulation software. | Please confirm whether Bidder can submit only PSCAD OR EMTDC model | Kindly read clause no 13.9, 9.7 b) of section project in conjunction with clarification provided at Sl no7. |
|  | 10. | Technical Specification: Section-STATCOM Station 10 tests | Field tests should be carried out in accordance with IEEE Std 1303™ | Please note that, The document, “IEEE std. 1303,” is only for SVC. Hence, some parts cannot be applied to STATCOM field test. Hence, It is recommended that the STATCOM field test should be based on the submitted and approved ITP (The ITP itself will be made referring to IEEE std. 1303 wherever possible) We request PGCIL to amend the clause accordingly. | Bidder understanding is generally in order, |
|  | 11. | Technical Specification: Section-STATCOM Station 6.1.1 Control objectives | The control system shall control the STATCOM, MSCs, MSRs required under this Technical Specification, as well as any existing switchable capacitor and reactor banks as stated in the Section project of Technical Specification. | Please confirm the quantity of switchable capacitor and reactor banks | Kindly refer amendment-I |
|  | 12. | Technical Specification: Section-STATCOM Station 6.1.2.6 | The STATCOM shall provide necessary damping to power oscillations by modulating its output in its entire range based on measured active power or rate of change of frequency at the 400kV bus. The damping controller would track local area oscillations as well as wide area oscillations and control would include several loops each focused on different frequency. | 1) Where does the power source come from? 2) How many lines should it be based on? | Bidder has to design controller based on Network file provided along with bidding document. |
|  | 13. | Technical Specification: Section-STATCOM Station 6.4.1 | a) With the STATCOM Station operating at any load upto rated value and within the design range of firing angle, the radio interference level from electromagnetic or electrostatic inductions generated by the STATCOM station shall not exceed 100 micro-volts/m, under fair weather conditions, at any point outside the station fence. c) RIV (Radio Interference voltage) measured at a phase to ground voltage (266 kV rms) in accordance to NEMA-107 shall not be more than 500 micro-volts for 400 kV system. For other system voltages IEC/NEMA in the order of preference shall be applicable. | a) there is no layout drawing in tender documents. Please provide a layout drawing specifying the Statcom area at the substation site. If the boundary of the fence is too close to STATCOM, the required value may not be satisfied. C) Does this mean the size generated by AC or DC devices? | Layout drawing shall be provide to successful bidder during detailed engineering stage. |
|  | 14. | Technical Specification: Section-STATCOM Station 6.6.7 | VSC Valves Converter losses are composed of losses in power electronic switches [insulated gate bipolar transistor (IGBT) or equivalent], made up of conduction and switching losses, and the losses in dc capacitors, resistors, and inductors used within the converter system. Refer IEEE-1052 for calculating VSC losses. | The loss is calculated based on simulation. | Bidder to quote as per provision of bidding documents. |
|  | 15. | Technical Specification: Section-STATCOM Station 8.1.1 | The Bidder must describe valve assembly and maintenance aspects of Sub-Modules including grounding provisions of each module for safe maintenance. | Could you explain what it mean? | Bidder has to submit detailed procedure for assembly of valves and maintenance aspect for utilization by employer during O&M stage. |
|  | 16. | Technical Specification: Section-STATCOM Station 8.1.5 | The Valve cooling system shall have black start capability and necessary UPS/UMD shall be provided separately for each STATCOM Unit. h) Each cooling system shall be provided with independent/dedicated UMD supply however common battery for both UMD power supply may be accepted. A UMD system will provide an extended capability of the STATCOM Station to deliver reactive power without any interruption, adding a buffer against the system faults or during events such as delayed voltage recovery or TOV. | Is it possible to use both UPS and UMD? Because the acceptance conditions for each equipment are different. | Bidder is free to decided UPS or UMD based on their design philosophy. However, system shall be designed to provide black start capability as per TS. |
|  | 17. | Technical Specification: Section-STATCOM Station 8.1.7 | Partial Discharge test shall be done during routine test of each sub module without DC Capacitor in addition to other routine/production tests specified in IEC 62927. | We conducts PD testing with the DC capacitor assembled. Is it possible to proceed based on our procedure? | Kindly refer amendment-I |
|  | 18. | Technical Specification: Section-STATCOM Station 8.2.3 | Control Equipment Test Requirement : offered Control equipment shall confirm to the following test. • Verification of control equipment performance for auxiliary power supply voltage (ac and dc) and frequency variations (ac). • Climatic test, i.e., verification of control equipment performance for a specified range of ambient temperatures and humidity. If climatic test certificates are available for the conditions specified, no further tests are needed. • Interference tests, i.e., the controls should be tested to operate in the environment of ac substations and suitable surge withstand capability (SWC). Tests should be carried out, or proof of previous testing provided, in accordance with IEEE Std C37.90.1™ (covering fast transient burst and a damping oscillatory wave) and IEEE/ANSI Std C63.16™ (electrostatic discharge tests). | Please confirm whether the test should be conducted during the FAT or whether a pre-test report should be submitted. | For Factory test on control system kindly refer clause no 10.1, of section- STATCOM STATION, however, test mentioned in clause no 8.2.3 section- STATCOM STATION are Type test, for which earlier conducted report in line with clause no 9.2 of GTR are also acceptable. |
|  | 19. | Technical Specification: Section-STATCOM Station 8.2.2 operator interface | f) As the sub-stations, where STATCOM Station shall be installed, are equipped with Sub- station Automation System (SAS) conforming to IEC 61850, it is required that STATCOM Station control and monitoring shall be integrated with SAS already provided at Sub-stations by the Contractor. It is proposed to connect STATCOM Station SCADA with SAS through a Gateway and the database, configuration etc. of existing SAS shall be upgraded to incorporate STATCOM Station events, alarms, Controls (both switchgear and control functions of STATCOM Station like setting of parameters etc.) | One HMI (identical to HMI in the STATCOM control room) is requested in control room of existing substation as per cl. 8.2.1-k. Integration of STATCOM Station SCADA with the existing SAS seems to require the same functionality with the HMI request in control room of existing substation. It may no need to integrate STATCOM Station SCADA with the existing substation SAS. If the integration with the existing substation SAS is required, the supply scope of the Contractor shall be limited to modification of the existing Gateway to connect STATCOM Station SCADA to the existing SAS. | Integration of STATCOM Station SCADA with existing Substation SAS shall be done through Gateway. |
|  | 20. | Technical Specification: Section-STATCOM Station 8.2.1 Control equipment | The control system design shall be based on single fail criterion i.e. failure of any one component in the system should not result in to outage of the complete system. | Kindly confirm that the below equipment shall be considered for single fail criterion. - BCU(bay control unit) for control of switchgears - DC CT for measuring the valve current | Kindly refer reply against similar query at Sl. No 32. |
|  | 21. | Section Project, 2 scope of work | Option 1: ±300MVAR STATCOM, 2x125MVAr Mechanically switched Shunt Capacitor (MSC), 1x125MVAr Mechanically switched Shunt Reactor (MSR). Option 2: +425/-300MVAR STATCOM, 1x125MVAr Mechanically switched Shunt Capacitor (MSC), 1x125MVAr Mechanically switched Shunt Reactor (MSR). Option 3: +300/-425MVAR STATCOM, 2x125MVAr Mechanically switched Shunt Capacitor (MSC). Option 4: ±425MVAR STATCOM, 1x125MVAr Mechanically switched Shunt Capacitor (MSC) Option 5: +550/-425MVAR STATCOM | Bidder understand that for all the options STATCOM shall consist of minimum 2 (Two) identical STATCOM branches/units at MV bus. | Single or multiple units are acceptable as per clause no 1.0 of section STATCOM rev02. |
|  | 22. | Section Project 2.5 System Engineering and Studies | The Studies to be conducted are detailed in Annexure-IV of this specification. | It is noted that PSCAD is platform suitable to study the overall performance of STATCOM w.r.t system as it can pre-validate the STATCOM performance which can be reviewed by customer well in advance before going for RTDS testing. In view of the above, bidder understand that: - Control performance of STATCOM like fault cases, energization, De-energization, and Contingency Cases for Ramgarh STATCOM will be performed in PSCAD, and submitted to customer for approval, using the reduced network equivalent model developed during benchmark studies in PSCAD. - The same reduced network model, developed during PSCAD studies, shall be modelled in RSCAD and used for control performance study during RTDS testing. | Bidder understanding is generally in order, subject to meeting the requirement mentioned in the Technical specifications. |
|  | 23. | Section Project 2.2.1 Controlled Switching Device | h) Controlled Switching device (CSD) for 400kV Main breakers under present scope and Tie Breakers for which make shall be provide during detailed engineering.. | Kindly provide the approved make & model of CSD. | Make and Model of Tie CB shall be provided to bidder during detailed engineering for which CSD is to be provided by them. |
|  | 24. | Section Project 2.2.1 SAS | h) Augmentation of above-mentioned existing Substation automation system, based on IEC 61850 for following bays is also under present scope (bay as defined in technical specification, Sec.-Substation Automation). | Existing Substation Automation system details to be provided for interfacing (including manufacturer, model, SAS architecture, spare etc) as mentioned. | Make and model of SAS shall be provided to successful bidder during detailed engineering |
|  | 25. | Section Project 2.2.1 Relay & protection | i) PU of 400kV distributed Bus bar protection scheme at RAMGARH PS shall be procured under separate contract for the bays under present scope. Make and model of the same shall be shared during detailed Engineering. However necessary wiring/cabling for extension of Bus Bar Protection for bays under present scope is covered under present contract. | a) We understand that distributed type bus bar protection is provided at Ramgarh station. Kindly confirm that the Bus bar protection panels envisaged for STATCOM bay will be placed in the existing control room, else the approximate distance between the existing control room & STATCOM STATION shall be provided. b) Please confirm there is spare space available in existing Substation control room for installing Substation CRP under the present scope. c) PGCIL is requested to advise whether spare cards are available in existing Bus Bar Differential Protection. | a) Bus Bar protection panel for STATCOM bay shall be installed in Switchyard panel room (SPR) inside the 400kV Switchyard. b ) Spare Space for installation of CB relay panel for 400kV Main STATCOM bay shall be made available in the existing Switchyard panel room. Other control & relay panel for STATCOM STATION shall be housed in new control room building meant for STACOM STATION. c) PU for present bays are already available in Tie bays, same shall be shifted in main bays under present scope or work. |
|  | 26. | Section Project 2.2.1 k) Relay and protection | Interface panel (if required) shall be provided for exchange of signals from the existing 400KV substation equipment (available in the form of potential free contacts) with control and protection system of STATCOM STATION, services and facilities | Please inform whether interface panel need to consider by bidder. If required, please add in the Price Schedule. | Interface panel if required shall be considered inclusive in the BPS line item of STATCOM station’s Control and relay panels. |
|  | 27. | Section Project 2.2.1 k) Relay and protection | Interface panel (if required) shall be provided for exchange of signals from the existing 400KV substation equipment (available in the form of potential free contacts) with control and protection system of STATCOM STATION, services and facilities | Kindly provide the approximate distance between existing 400kV Control Room & STATCOM STATION. | The Required details shall be shared with successful bidder during detailed engineering. |
|  | 28. | Section Project 2.2.1 control of bus reactor | j) Control of following bus reactors shall be provided in STATCOM station controller for coordinated reactive power control & supplementary VCS current control of external devices at RAMGARH PS substation: • 02 Nos. of existing 125MVAr, 400kV Bus Reactor connected to 400kV substation bus. • Provision in the control system of integrating additional 01 Nos. of 125MVAr, 400kV Bus Reactor connected to 400kV substation bus envisaged in the future. | a) PGCIL is requested to remove this feature from the current scope, if possible. b) Existing make & model of the Bus Reactor protection system & switching details requested to be provided. c) Kindly provide the clear scope of work/ scheme envisaged for the future. | a) Bidder to quote as per provision of bidding documents. b) The required details shall be shared with successful bidder during detailed engineering. c) kindly refer amendment - I |
|  | 29. | Section Project 2.2.1 Fire protection System | l) Suitable fire detection system using smoke detectors and/or heat detectors shall be provided in STATCOM Building for all room and areas. The requirement shall be as per Section Fire Fighting Protection for control Room Building. These fire detection systems shall be connected to a separate Fire annunciation system clearly identifying the zone | Kindly clarify if the fire detection devices under present scope will be connected with new Fire Alarm Pannel or with the existing substation Fire Alarm Pannel ? If connected with the existing fire system, please provide details of the existing system & distance. | New Fire alarm panel is envisaged for STATCOM building. |
|  | 30. | Section Project 2.2.1 Fire protection System | l) Hydrant & HVW System. The hydrant system shall be extended from existing firefighting system in the yard. The tapping for HVW system shall be done from nearby transformer/Reactor or any other suitable point in existing firefighting line. | Kindly provide the make, model & scheme (P&ID) of existing Hydrant & HVW System. | Make, model & Scheme of existing hydrant & HVS system shall be provided to successful bidder during detailed engineering. |
|  | 31. | Section Project 2.2.1 Earthmat | q) Earthmat for 400kV bays in switchyard under present scope is being laid in a separate package | We understand that Main Mat is not under present scope and the 40 dia MS Rod mentioned in the Bid Price Schedule is for underground risers only. Kindly confirm. | Main Earthmat for 400kV Switchyard under present scope is being laid under separate package, however, supplying & laying of main earth-mat in STATCOM STATION, 400kV interconnection area and interconnections required with main earth mat is in present scope of bidder in addition to risers/auxiliary earth mat required for equipment’s. |
|  | 32. | Section Project 13.5 Earthmat | c) The grounding grid of STATCOM Station shall be connected with the grounding grid of the 400kV switchyard of the Employer by the contractor. | Kindly confirm in whose scope is the main Earth Mat & necessary extension work. | Kindyl refer clarification at Sl no 142 |
|  | 33. | Section Project 2.2.1 VMS | t) Visual Monitoring System (VMS) for complete STATCOM Station: | Kindly clarify if the VMS will be connected with new separate systems or with the existing system? If connected with the existing system, please provide details of the same. | Kindly refer clarification sl no 55 above. |
|  | 34. | Section Project 2.2.1 Auxiliary LT Transformer | e) Auxiliary LT transformer along with associated 72.5kV outdoor switchgear equipment’s to be installed on tertiary of existing 500 MVA, | As per STATCOM Station LT SLD, another supply needs to be provided from 33kV Tertiary of existing 500 MVA, 400/220/33 kV Auto transformer. a) Kindly confirm the same & the location of existing 500 MVA, 400/220/33 kV Auto transformer. b) Also the spare KVA rating of the 500MVA Auto Transformer may please be provided. c) In case this spare capacity is not sufficient, kindly propose alternate option. | - Confirmed, location of 500MVA, 400/220/33kV Auto Transformer shall be provided to successful bidder during detailed engineering. - Sufficient spare KVA rating shall be made available to bidder for tertiary tapping. - Kindly refer clarification above. |
|  | 35 | Section Project 2.2.1 Auxiliary LT Transformer | e) Option 1: If XX/0.415 kV XXX KVA Auxiliary LT transformer along with associated switchgear equipment applicable for tapping auxiliary power(main incomer-II to supply for LT switchboard) from STATCOM station MV Bus including cable and automatic voltage stabilizer for interconnection. Primary rating of auxiliary transformer shall be based on STATCOM Station Bus voltage (XX) rating and the LT voltage variation in worst case shall not be more than specified voltage for 415V bus. The kVA rating shall be adequate to feed the entire required load of STATCOM Station considering worst operating condition. | Voltage Stabiliser is not shown in Bid Price Schedule, kindly include the same & type test validity of the required vendor. | Voltage Stabilizer is subsumed in item no 15.9 of BPS, no separate item is envisaged for the same. |
|  | 36. | Section Project 2.2.2 ) Civil Works |  | The section project specifies in clause 2.2.2: The scope of civil works (Design, Engineering & execution for STATCOM Buildings, Equipment foundations, Rods, Drains, Culverts, Other building structures, Transformer and Reactor foundations etc.) shall be based on the drawings developed by the contractor. However, the same is missing in price schedule. Needs clarification. | Bidding documents (Section Project & BPS under Volume II) are amply clear. Bidder to quote as per the provisions of bidding documents. |
|  | 37 | Section Project 2.2.1 Phase measurement unit | h) Scope of Work for Phasor Measurement Unit: | Please inform PMU panel supply and related wiring/ cabling is out of scope for this tender. | Bidder to comply as per Clause No. 1.5 of PMU Technical Specifications. |
|  | 38. | Section Project 13.12 Specific Requirement | The Bidder shall offer the STATCOM Valve along with all accessories and its control and Protection system from its own works or its own subsidiary company or Group Company or a Joint Venture Company (JVC) works in India. | Bidder understand that the clause is applicable only to STATCOM Valve. STATCOM control & protection system from outside India is acceptable. | Bidder to comply the requirement mentioned in the technical specification. |
|  | 39. | Section Project 13.13 Specific Requirement | For integration of STATCOM control and protection system, the configuration of hardware, software, its integrated testing (both dynamic and steady state) is to be carried out at the works. Simulation testing is required to be carried out on RTDS. During RTDS testing and configuration, POWERGRID representative is required to be closely associated. | Bidder understand that Protection Relays testing to be carried out using Omicron and an integrated testing of Protection & Control System however RTDS modelling of Protection relays is not foreseen. Control System testing as well as Protection functions which are part of control system will be performed using RTDS. Please Confirm acceptance. | Confirmed. |
|  | 40. | Section Project 13.15 Interface points | f) The contractor shall also provide duplicate control facility (HMI workstations and Disturbance recorder workstation) of STATCOM STATION to be located in main control room (control room of 400kV switchyard being provided by the Employer) with the necessary selector switch/ facility to operate and control STATCOM STATION from main control room. | Does the duplication control facility that the contractor has to supply to the main control room mean each HMI work station and Disturbance recorder work station? Do we have to supply duplicate Disturbance recorder workstations to the main control room? The operator can access the Disturbance recorder using remote access on duplicate HMI Workstations in main control room. Please check if the contractor must supply the duplicate Disturbance recorder workstation to the main control room. | Kindly refer amendment-I |
|  | 41. | Section Project 13.15 Interface points | h) The STATCOM Station System shall provide remote communication interface (RCI) in the form of gateways for simultaneous communications with multiple independent remote control centres as defined here. There shall be no restriction to the type or number of signals and controls, which are available in the STATCOM Station system to be configured for communication to remote control centers. The following signals and controls shall generally be required: a. Measurements (MVar, Current, Voltages, cooling system parameters, Temperatures) b. Control (Start, Stop, Operational parameter setting etc.) c. Alarms & warnings (STATCOM Station health monitoring) d. Disturbance records (in COMTRADE format) | Should Disturbance records be sent whenever a failure is triggered? Then, Remote Control Center PC conditions are required to send Disturbance records (in COMTRADE format) to the Remote-Control Center. Please check this (whether it is a Windows, whether it is accessible to share folders, etc.). | The bidder may quote as per bidding document |
|  | 42. | General | - | Please provide existing Substation Layout, SLD, Proposed Location for STATCOM station, existing control room, earthing layout, cable trench layout, DSLP layout, soil resistivity report etc. for calculating LOT item BOQ. | The Required details/document shall be provided to successful bidder during detailed engineering. |
|  | 43. | BPS - Schedule 1 (Part A) 9.0 Bus work (from 400kV take off Gantry to STATCOM Yard) | - | Could you please provide the Layout drawing to understand the existing Gantry location & required MV & HV Bus extension work. | The Required details/document shall be provided to successful bidder during detailed engineering. |
|  | 44. | BPS - Schedule 1 (Part B) 9.0 Special Tools and Tackles as per Technical Specification section project Annexure-II | - | In Price Schedule item No. 9, all items are given in LOT. Could you please provide the same in numbers. | Bidder to quote as per provision of bidding documents. |
|  | 45. | BPS - Schedule 1 (Part A) 15.8 UPS/UMD for STATCOM Station systems | - | Kindly confirm whether same UPS can be considered for Cooling System & other auxiliary systems or separately required. | Bidder to quote as per provision of bidding documents. |
|  | 46. | BPS 15.11 DG set. | - | a) Kindly confirm why 2 sets of DG is required. Also kindly confirm DG location whether it is outdoor / Indoor. b) In Standard SLD AC&DC System for STATCOM station Dwg No: C/ENGG/STD/ STATCOM/ LT/ SLD/01, only 1 No DG Set is shown. Kindly confirm which document to consider. | a) 2nos of DG required, one for each LT Switchboard DG incomer of STATCOM-I & II respectively. Further, DG sets shall be installed outdoor b) please refer reply above. |
|  | 47. | BPS - Schedule 1 (Part B) '8.0 & Cl 2.2.1 e) Electrical auxiliaries supply systems (from existing ICT Tertiary) | 33/0.415 kV XXX kVA Auxiliary LT transformer along with associated 72.5kV outdoor switchgear equipment’s to be installed on tertiary of existing 500 MVA, 400/220/33 kV Auto transformer including cable for interconnection. The kVA rating of LT Transformer shall be adequate to feed the entire required load of STATCOM Station’s considering worst operating condition | Kindly specify how many Auxiliary Transformers need to consider under present scope, for LT Incomer I & Incomer II. | Bidder to quote as per provision of bidding documents. |
|  | 48. | BPS - Schedule 3 'Part-A-Option 5 (Clause 20.0) '9.0 (Part B) Civil works as per technical specification and employer supplied drawings | - | Please inform the following a) Supply of materials in in who’s scope? b) Design, Engineering and Drawings submission is in who’s scope? c) Execution as per IFC drawings is in who’s scope? d) Soil investigation, site levelling etc. for STATCOM yard will be in who’s scope of work. | Bidding documents (Section Project & BPS under Volume II) are amply clear. Bidder to quote as per the provisions of bidding documents. |
|  | 49. | General | - | Please inform for equipment support structures & foundations PGCIL will issue their standard drawings or bidder needs to design. | Bidding documents (Section Project under Volume II) are amply clear. Bidder to quote as per the provisions of bidding documents. |
|  | 50. | Technical Specifications for Phasor Measurement Unit (PMU) .1.1.1 | The supplied PMUs shall be mounted in the C&R/SAS panels being supplied by the Contractor for respective substation package and interface cabling requirements shall be as applicable for relay. | According to the specifications, Bidder understood that the PMU should be located on the STATCOM C&P Panel by the Contractor. Please make sure that what Bidder understood is correct. | Bidder to supply panels for PMUs as per TS |
|  | 51. | Technical Specifications for Phasor Measurement Unit (PMU) 1.1.1 | PMUs shall be provided to measure Voltage and Current Phasors of feeders and transformers specified in the BoQ. PMU shall also measure status of master protection and circuit breakers for units, feeders and transformers as per SLD. The PMUs shall be able to measure/calculate following: | Please inform the bidder of the exact purpose of the PMU. If the voltage and current phasors of feeders and transformers specified in BoQ can be measured with a STATCOM controllers, is it okay to supply only the STATCOM controller without supplying PMU separately? | Bidder to supply panels for PMUs as per TS |
|  | 52. | SUBSTATION AUTOMATION SYSTEM 1.6 | The Sub-station Automation system being offered shall generally conform to provision of IEC 62351, IEEE1686 and NERC CIP (applicable part such as CIP 003, CIP-005, and CIP-007) for cyber security. | Does the scope of cyber security (IEC 62351, IEEE1686 and NERC CIP) include devices (STATCOM controllers, relays) in all Sub-station Automation system? Or Only network (HMI, Ethernet LAN communication, server, gateway)? | Requirement of technical specification shall prevail. |
|  | 53. | BDS Annexure-A Qualifying Requirements (QR) 1.2.2 & 1.2.5 Local supply of STATCOM & Indian Associate | 1.2.5: If bid is submitted as an Individual Firm or in a Joint Venture without any Indian Entity as a Partner, the Bidder should propose, in its Bid, an Indian Associate for executing the On-Shore Supply and On-Shore Services Contract.... | As per clause 1.2.5, Bidder (Foreign Entity) need to propose an Indian associate (who meets the required Qualifying Requirement as per clause 1.2.5) to perform on-shore supply and services scope. However, as per bidding document, it not defined whether the Indian associate only has to be an "Individual Firm" OR A "Joint Venture of two or more Indian Firm" can also be an Indian Associate. Bidder understand that: - Bidder may propose an Indian associate which is a "Joint Venture of two or more Indian Firm" which collectively meets Qualifying Requirement as specified in clause 1.2.5. Please confirm above understanding. | As only technical requirement is specified for Indian Associate hence JV in Indian Associate is not envisaged |
|  | 54. | GENERAL TECHNICAL REQUIREMENTS 22.1 BUSHINGS, HOLLOW COLUMN INSULATORS, SUPPORT INSULATORS | General | Please note that, composite insulators will be applied to the VSC valve structure. | Bidder to quote as per provision of bidding document. |
|  | 55. | Section Project Clause no 2 and STATCOM Station clause no 8.3.2.r | Option 5: +550/-425MVAR STATCOM and Any fault on MV bus will trip the 400kV breaker. However, any branch fault shall be cleared by respective MV branch Circuit Breaker | Bidder understand that for "Option 5 i.e. Full STATCOM option", circuit breaker at MV-level will not be applicable and hence for "Any fault (bus/branch) on MV side will trip the 400kV breaker." Please confirm. | Bidder to quote as per provision of bidding document. |
|  | 56. | Section Project Clause no 2 STATCOM Station Clause no 6.6.1 Bid Forms Att-10 | Option 5: +550/-425MVAR STATCOM The bidder must guarantee the total losses of STATCOM Station, be less than 1% of the reactive power output individually at its inductive limit (STATCOM+MSRs) and capacitive limit (STATCOM+MSCs) for the cumulative highest reactive power output of STATCOM Station at PCC with worse combination of manufacturing tolerances. | Please note, for option-5, its not feasible to meet guaranteed loss clause of 1% at at capacitive/reactive full load output. We take the refrence of clause 10.28 of "Substation Package for STATCOM installations associated with Eastern Region Strengthening Scheme-XI (ERSS-XI). Spec. No.: CC-CS/419-ER1/STATCOM-2409/3/G8" where the "LOSSES REQUIREMENT & LOSS EVALUATION" clause was amended as: For bid evaluation purposes the losses will not be evaluated. In the bid the bidder must guarantee losses of STATCOM Station less than 1% of the reactive power output individually at inductive limit (STATCOM+MSRs) and capacitive limit(STATCOM+MSCs) for the worst combination of STATCOM, MSR/MSCs (worst case means highest reactive power output) with 1 pu voltage on 400kV Bus. For final acceptance the contractor must meet the guaranteed 1% losses by on-site measurement. However, in case of Ranchi, Rourkela & Kishanganj where MSC is not envisaged, the losses of STATCOM station shall be guaranteed 1.0% for fully inductive mode (i.e. including MSRs) and 1.5% for STATCOM in fully capacitive mode. In view of the above, for option 5 where MSC/MSR are not envisaged, Bidder request to amend the guaranteed loss clause to 1.5%. Bidder request to issue suitable amendment. | Bidder to quote as per provision of bidding document. |
|  |  | Specific Requirement rev08, Section SAS Rev 04, New Para added under Clause 4.1.5 | The bidder shall also provide 2 Nos. managed Ethernet switches with at least 16 copper RJ45 ports on each switch to form managed “Redundant System LAN” for connecting different NTAMC sub-systems devices (SCADA Gateways, VMS, VOIP etc.) as per revised system architecture (attached as Annexure S5). The specification of the switches is enclosed at Annexure-S6. | The typical architecture in Annexure S5 shows multiple connections to multiple AMCs. It is unclear whether all those connections needs to be established/ considered from STATCOM control room or if it will be considered in the Substation control room. Please clarify. | The typical architecture in Annexure S5 is pertains to Main S/s SAS. However, requisite integration of STATCOM SAS with Substation SAS shall be done as per requirement mentioned in clause no 8.2.2 f) of section STATCOM Station. |
|  |  | Tech Specification, Section: CRP, Rev.NO-09, 2.7 | Cable entries to the panels shall be from the bottom. | Fiber Optic Cables entry is only from Top. The Valve control cabinets will have both top & bottom entry. Top entry will be used for the fibres from the STACOM valves and cooling system. | Noted. |
|  |  | Tech Specification, Section: CRP, Rev.NO-09, 3.6 | No equipment shall be mounted on the doors | Some equipments like Control switches, Indication lamps, Push Buttons and Test Switches are mounted on the door. These equipments mounted on the door needs quick access to the operator or provide indications without opening the door. Test switches on control panel are mounted are the doors as there are no hinged frames in MACH3 design. Only in protection cubicles they are mounted in the inside hinged frame where there are numerical relays. | Noted . |
|  |  | Tech Specification, Section: CRP, Rev.NO-09, Clause 3.7 | Matching of Panel size, color, appearance and arrangement. | Not applicable for panels in STATCOM building. No existing panels in STATCOM building and it’s a separate building for STATCOM. | Noted. |
|  |  | Tech Specification, Section: CRP, Rev.NO-09, Clause 7.1 | Coloured mimic diagram and symbols showing the exact representation of the system shall be provided in the front of control panels. | MIMIC representation is available in HMI workstation. They are not available in the front of control panels. MIMIC representation is available in table mounted HMI workstation in STATCOM Control building and the Remote HMI workstation in Main control building | Noted. |
|  |  | Tech Specification, Section: CRP, Rev.NO-09, Clause 11 | Indicating Instrument & transducers for Control Panel | Not applicable for STATCOM control panels. All these information are available in the HMI workstation. | Noted. |
|  |  | Tech Specification, Section: CRP, Rev.NO-09, Clause 12 | Annunciator System for Control Panels | HMI system will have this information. All the status and alarms will be present in the HMI workstation located in the STATCOM Control building, the Remote HMI workstation located in Main control building will also have all status and alarms and these will be transferred to SCADA via IEC 61850 protocol. | Noted. |
|  |  | Tech Specification, Section: CRP, Rev.NO-09, Clause 16 | Synchronizing Equipment | Not applicable for STATCOM control panels. | Noted. However synchronization of HV side of coupling transformer bay with existing 400kV bays shall be included in BCU. |
|  |  | Tech Specification, Section: Battery and Battery Charger, Rev.NO-06, Clause 1.1 | General technical Requirements | Battery bank sizing, capacity and number of cells for STATCOM battery system will be provided as per its equipment’s requirement. Battery system is only for STATCOM station, not a complete substation. | Noted. |
|  |  | Tech Specification, Section: Battery and Battery Charger, Rev.NO-06, Clause 1.1.4 | 48V DC System | 48V DC is not applicable for STATCOM Stations. | Noted. |
|  |  | Annexure - B | Seismic Withstand test procedure | Not applicable for STATCOM & STATCOM control panels. | Noted. |
|  |  | 4.0 STATCOM Specification Rev-2 May-2020 - 6.1 f) | The STATCOM Station should be capable of repeating temporary operation as defined in any one of item (d) and (e) as above for at least 3 charging cycles in 60mins. | Please clarify the time duration to be considered in between the two consecutive charging cycles. Due to lack of information, Bidder assumes that the duration between two consecutive cycles is approximately 19 minutes. (3 cycles in 60mins). | Bidder may quote as per bidding document |
|  |  |  |  | The text in IEEE 1052-2018 8.1 i) also says "repeating temporary operation every ___min". Please confirm the duration between two consecutive cycles. |  |
|  |  | 4.0 STATCOM Specification Rev-2 May-2020 - 6.1.3 | It is essential that the STATCOM Station operates in a robust manner when transmission system under voltages appears. For transmission system voltages down to 0.3 pu, the STATCOM units must operate unrestricted, producing its rated capacitive current. The STATCOM must be designed to operate at transmission system under voltage, even considering that severe voltage unbalance scan appear. The STATCOM must not be restricted by short term negative sequence voltages upto1.5%, appearing in conjunction with under voltages. | During Unsymmetrical faults, the rated VSC capacitive current is not possible to deliver to grid. The STATCOM will support the grid by injecting maximum capacitive reactive current within its physical limitation. The amount of current an MMC valve can output during these scenarios is fault type dependent where the converter can output rated current for symmetrical faults but less current during unsymmetrical faults (since a portion of the converter capacity will be required for VSC valve DC capacitor balancing). Please confirm the understanding. | Insulation coordination study report as part of Basic Desing report to be submitted by contractor during detailed engineering. Same shall be finalized during detailed engineering stage |
|  |  | Section-STATCOM: 5. Power System Characteristic3. Scope of work Section-Project: 13.19 Power system parameters | Max, Min continuous voltage 420 kV, 380 kV. Steady state voltage range 360-440 kV. | Please confirm the max and min system continuous voltage whether 380-420 kV or 360-440 kV to consider for STATCOM design? | Kindly refer reply against similar query at Sl. No. 115. |
|  |  | Section-Project: | The necessary provision of switching of spare unit of transformer to be achieved through the help of isolator and associated switching of control & protection shall be automatic through isolator contacts. Isolator based switching is envisaged for both HV and MV side of coupling transformer. | For switching of spare transformer into the circuit, necessary site tests shall be conducted to confirm the healthiness of the transformer. Moreover, neutral formation is to be done manually. | Confirmed. |
|  |  | 2.2.1 b) Coupling Transformer Spare |  | In the Additional clarification dated 10.07.2023, Sl.No.23 says " TSP to meet the requirement of RfP either through option 1 or option 2". | Bidder to quote as per the requirement mentioned in the technical specification. |
|  |  |  |  | Accordingly Bidder requests to keep this spare transformer connection as option 1 or option 2 as per the clarifications to be selected by bidder. |  |
|  |  | 4.0 STATCOM Specification Rev-2 May-2020 - 6.4.1 a) | With the STATCOM Station operating at any load upto rated value and within the design range of firing angle, the radio interference level from electromagnetic or electrostatic inductions generated by the STATCOM station shall not exceed 100 micro-volts/m, under fair weather conditions, at any point outside the station fence. | Performing and evaluating radiated emission at a closer distance than the substation length (i.e., inside the near field) is not relevant nor reliable when comes to electromagnetic fields in the range of 100 kHz – 10 MHz (where a STATCOM typically is a considerable source of interference). Additionally, at this distance, corona discharges and sparking from the adjacent substation will heavily inflict on the measurements. Any radio interference requirements at the substation boundary can therefore not be considered by Hitachi Energy. | Bidder to comply the requirement mentioned in the technical specification. |
|  |  |  | The RIL criteria shall be achieved at all frequencies within the range of 150KHz to 300MHz and with the STATCOM operation at any level up to and including rated value, the design shall provide correcting measures, should the specified design not being realized in the final installation. | Hitachi Energy considers that Cigré Technical Brochure 391 is the only applicable standard to evaluate electromagnetic disturbance from a FACTS application and the proposed 300Mvar Hitachi Energy SVC Light will meet the requirements proposed by the same. This relates to levels, distances as well as measurement procedure. | Bidder to comply the requirement mentioned in the technical specification in conjunction with the amendment-I. |
|  |  |  |  | The RI limit levels will vary based on the frequency range., Hence the the limits specified in CIGRE 391 std will be fulfilled. |  |
|  |  |  |  | Further, it is assumed that the measurements will be done at a distance as clarified in earlier tender. |  |
|  |  |  |  | "The level of Radio Interference in the mentioned frequency range shall be guaranteed at the boundary of the overall substation or 500m from the `STATCOM station fence, whichever value is higher." |  |
|  |  | 4.0 STATCOM Specification Rev-2 May-2020 - 8.3.2 r) | STATCOM MV Bus Protection: | For Bus Differential protection (87): |  |
|  |  |  | i. Bus Differential protection (87) | In STATCOM branch measurement device of type Electronic Current Transducer(ECT) to measure current in VSC legs with high accuracy are used. | We understand said query is for VSC branch differential protection and in place of differential protection of VSC ranch Duplicate overcurrent protection & converter blocking at high Current in values offered is acceptable. |
|  |  |  | ii. Ground overcurrent protection(51N),used with neutral Grounding Transformer | * Conventional CT’s are not used due to required measurement accuracy and measurement of DC currents. |  |
|  |  |  | iii. Under/Over Voltage(59Ph-Ph) protection | * STATCOMs since 1996 have been designed without differential protection in the VSCs. Protection scheme is well-proven with excellent operational experience. |  |
|  |  |  | iv. Over voltage (Open Delta) protection | Further, IGBTs will quickly be turned-off (e.g. within 1-2 ms) in case high currents flowing through the delta connected VSC converter. Such IGBT action will effectively convert differential protection into a simple instantaneous OC protection which is anyhow provided. Contractor base solution for protection of VSCs are much faster than a conventional differential protection. Please also refer to IEEE1052TM-2018. |  |
|  |  |  | STATCOM Branch Protection: |  |  |
|  |  |  | i. Differential protection(87) |  |  |
|  |  |  | ii. Overload protection (49) | Overcurrent protection inside delta: |  |
|  |  |  | iii. Over current protection inside delta (50,51) | Valve overcurrent protection (VOCP) in statcom control system will provide the necessary overcurrent protection. |  |
|  |  |  | iv. Negative phase sequence protection(46) |  |  |
|  |  |  | v. STATCOM branch over current protection (50, 51, 50N,51N) |  |  |
|  |  | 6.1.2.13 Control of Direct Current | During STATCOM operations, any flow of direct current to transformer MV side must be less than 25% of transformer magnetizing current. | Please advise why 25% of magnetizing current limit is specified. | Bidder to comply the requirement mentioned in technical specifications. |
|  |  |  |  | Bidder suggests to modify it as below to be a realistic implementation: |  |
|  |  |  |  | "During STATCOM operations, any flow of direct current to transformer MV side must be minimized so that transformer saturation will not occur. " |  |
|  |  | Volume-II Part-3 of 7 folder: 4.0 STATCOM Specification Rev-2 May-2020, page 16 of 62, section 6.1.8 | The maximum overshoot should not exceed 120% of the total change | As per Technical specification, the maximum overshoot should not exceed 120% of the total change. Is it 120% of the total change or 20% of the total change? Contractor understands that the requirement is maximum overshoot should not exceed 20% of the final | Bidder understanding is in order. |
|  |  | Volume-II Part-3 of 7 folder: 4.0 STATCOM Specification Rev-2 May-2020, page 16 of 62, section 6.1.8 | STATCOM station response shall be such that the change in measured system voltage to small disturbance should reach 90% of the desired total change within 30ms of the initiating a 5% step change of voltage reference. | Step response is applicable for STATCOM only, not for slow switching devices like MSCs and MSR. The specification says "STATCOM station" response to be fulfilled. MSCs and MSR switching is associated with time delays. | Confirmed. |
|  |  | Volume-II Part-3 of 7 folder: 4.0 STATCOM Specification Rev-2 May-2020, page 55 of 62, section 9.2.1.IV 2. Technical specifications folder: 1.0 Sections_Project_Statcom Ramgarh.pdf, page 25 of 30, section 9.7 | Studies to evaluate the interaction of the STATCOM controls with the other nearby control systems, including high-voltage direct current (HVDC) controls, generator controls, and controls of other flexible ac transmission systems (FACTS) devices | To evaluate the interaction of the STATCOM controls with other nearby control systems including HVDC controls and FACTS devices, control interaction investigation studies will be performed. Also, the interaction of STATCOM controls with nearby active devices will be monitored during DPS studies and if any interaction will be observed between Ramgarh STATCOM controls and other nearby active devices then the proposed STATCOM controller will be tuned accordingly if this interaction is caused by the proposed STATCOM. Please confirm. Further, to evaluate the interaction between STATCOM controls and the generator controls, the UIF study will first be performed to determine the possible risk of sub-synchronous interaction with nearby generator plants. If that study shows a risk for sub-synchronous interaction, then further studies are conducted. If, however, the UIF is less than 0.1 for all studied cases, then further SSTI studies are not conducted. | Noted. |
|  |  | Volume-II Part-3 of 7 folder: 4.0 STATCOM Specification Rev-2 May-2020, page 55 of 62, section 9.2.1.IV 2. Technical specifications folder: 1.0 Sections_Project_Statcom Ramgarh.pdf, page 25 of 30, section 9.7 | Studies to evaluate the interaction of the STATCOM controls with the other nearby control systems, including high-voltage direct current (HVDC) controls, generator controls, and controls of other flexible ac transmission systems (FACTS) devices | To evaluate the interaction of the STATCOM controls with other nearby control systems including HVDC controls and FACTS devices, control interaction investigation studies will be performed. Also, the interaction of STATCOM controls with nearby active devices will be monitored during DPS studies and if any interaction will be observed between Ramgarh STATCOM controls and other nearby active devices then the proposed STATCOM controller will be tuned accordingly if this interaction is caused by the proposed STATCOM. Please confirm. | Bidder to comply the requirement mentioned in the Technical specifications. |
|  |  | 1. ‘Volume-II Part-3 of 7 folder: 4.0 STATCOM Specification Rev-2 May-2020, page 55 of 62, section 9.7.a 2. Technical specifications folder: 1.0 Sections_Project_Statcom Ramgarh.pdf, page 25 of 30, section 9.7 | The vendor should provide a detailed STATCOM Station dynamics model both in UDM & validated generic for use in (PSCAD and PSSE) power flow and stability simulation software. | For PSS/E, both Generic & User-defined block box models shall be shared by the bidder with the customer. Generic models can be shared by the customer with the concerned stakeholders without any NDA. For User Defined model, Bidder does not accept that the models can be provided to third parties without permission due to intellectual property and liability reasons. However, the model can be provided with a joint NDA between the third party and Bidder/contractor. For PSCAD, User defined block box model only will be shared by the bidder. For User Defined model, Bidder does not accept that the models can be provided to third parties without permission due to intellectual property and liability reasons. However, the model can be provided with a joint NDA between the third party and Bidder/contractor. | Please refer reply against similar query at sl. No.7. |
|  |  | Volume-II Part-3 of 7 folder: 4.0 STATCOM Specification Rev-2 May-2020, page 56 of 62, section 10.1 (b) | Verification of the protection system with reference to integrated protective functions included in the controllers and firing controllers. | All protective control functions will be considered for RTDS studies. However, the relay protections will not be considered for RTDS studies or verification. All relay protection tests can be done using OMICRON amplifier therefore the relay protections will be tested seperately using OMICRON amplifier. | Acceptable. |
|  |  | Volume-II Part-3 of 7 folder: 4.0 STATCOM Specification Rev-2 May-2020, page 11 of 62, section 6.1.2.1 | Voltage Control mode (Automatic and Manual) | Voltage control mode is automatic mode operation only. | Voltage control mode shall be automatic as per Technical specification and shall also additionally be settable on manual mode. |
|  |  | 2. Technical specifications folder: 1.0 Sections_Project_Statcom Ramgarh.pdf, page 28 of 30, section 13.19 | For the design purpose, following Power System parameters (at PCC) may be considered: | Bidder understand that Minimum three-phase fault current (10.2 kA) and Minimum single-phase fault current (6.2 kA) provided in the Table SL 21 and 25 of section 13.19 need to be followed for performance evaluation during project stage. Please confirm. | Confirmed. |
|  |  | 2. Technical specifications folder: 1.0 Sections_Project_Statcom Ramgarh.pdf, page 28 of 30, section 13.19 '2. Technical specifications folder: 1.0 Sections_Project_Statcom Ramgarh.pdf, page 14 of 30, section 2.3 | 2.3.a Ensuring that the STATCOM STATION system is integrated with the existing power system network to have a trouble-free operation of complete A.C. network also comprising of HVDC and other FACTS installations 13.18 Information regarding List of HVDC & FACTS devices in the Power System is enclosed as Annexure-IX | Bidder will take the responsibility to model, integrate the proposed Ramgarh STATCOM as per the technical specification requirements only. Bidder can't take the responsibility to model and integrate any other STATCOM and HVDC in the Employer's AC network. Bidder request the Employer to provide the final PSS®E network models should have flat start without any jumps and oscillations. 1. Employer needs to provide the PSS®E network cases (sav case, dynamic file, DLLs if any) along with the necessary instructions to initialize the files up to two network scenarios. 2. These network models will be complete and final otherwise it is Employer’s responsibility to provide any missing models/data, e.g., vendor specific models, any other HVDC and FACT devices in the appropriate format and PSS®E version. Sequence data for the elements needs to be provided. Sequence data is important for asymmetrical fault behavior. | (1) Noted. (2) Available data/ PSS/E file shall be shared with the bidder during detailed engineering.(File is provided?) |
|  |  | 2. Technical specifications folder: 1.0 Sections_Project_Statcom Ramgarh.pdf, page 15 of 30, section 2.5 | 2.5 System Engineering and studies | Design and studies related to Ramgarh STATCOM station under the scope of supply will be carried out. | Confirmed. |
|  |  | 2. Technical specifications folder: 1.0 Sections_Project_Statcom Ramgarh. pdf , page 15 of 30, section 2.5 | The contractor shall carryout all the studies which may be necessary for completion of the design and engineering whether, these have been mentioned in the Bid by the Bidder or not. | The bidder will list all the necessary studies to complete the design and engineering during the bid stage itself. Anything additional requested from Employer during the project stage will be agreed between bidder and customer under separate agreement on a need basis. | The provisions of the Technical Specification are amply clear and bidder shall follow the same. |
|  |  | 2. Technical specifications folder: 1.0 Sections_Project_Statcom Ramgarh. pdf, page 15 of 30, section 2.5 | The Employer shall have right to observe and participate in the studies performed as a part of the Contract and shall have access to all data necessary for complete understanding of the purpose of such studies as well as the validity of the results. | It will not be possible to have Employer to participate in every kind of study to be performed as part of the project. Also, it will not be possible for Employer to request additional studies without cost to give Powergrid further understanding of the Contractor control system. | The provisions of the Technical Specification are amply clear and bidder shall follow the same. |
|  |  | 2. Technical specifications folder: 1.0 Sections_Project_Statcom Ramgarh.pdf, page 20 of 30 and 21 of 30, section12.1 and 12.2 | Association and training of employer personnel scope and Training documentation. | Bidder will be able to provide normal training as our main offer, i.e. non-hands-on training, and this is our standard practice and we have received satisfactory feedback from our previous customers. To be clear, the bidder can ONLY commit and deliver a normal training as our main offer. | The provisions of the Technical Specification are amply clear and bidder shall follow the same. |
|  |  | 2. Technical specifications folder: 1.0 Sections_Project_Statcom Ramgarh. pdf, page 25 of 30, section 9.7.b | If any other proprietary softwares are used by the contractor for system control design, the contractor shall provide these softwares with perpetual license for use by the Employer. | Bidder will provide black box PCAD User-defined Ramgarh STATCOM model. Although, Bidder are not providing proprietary software, as this is not needed for operating, maintaining, or anything else related to our scope of supply. | For UUSER Defined model requirement mentioned in technical specification and further clarification shall be complied by the bidder. No Licence of STATCOM Software is envisage. Block diagram level details for all functionality to be provided for STATCOM STATION Control. |
|  |  | 2. Technical specifications folder: 1.0 Sections_Project_Statcom Ramgarh.pdf, page 26 of 30, section 13.11 | Transient Studies (including High frequency transients) need to be carried out for the STATCOM Station along with connected power system network for various fault (Ph-G, Ph- Ph, 3-ph etc.) condition on the MV Yard of STATCOM Station, | To model reduced power system network in PSCAD, Bidder requests Employer to provide Black box/User models of nearby other active devices (e.g., SVC, STATCOM, PV or wind turbine etc.) and HVDC links to be included in the PSCAD study. It shall be noted if actual dynamic models of nearby active devices (e.g. SVC and STATCOM) are not provided in the PSCAD format, the bidder will exclude the study in PSCAD as there is no value added by doing this study with using generic models/ assumed data, i.e. if the study outcome shows any interactions/resonance, no concrete decisions can be made as the models are not representative; thus, the bidder won't make any action to tune the STATCOM controller for any eventual interaction/resonance observed using generic models/ assumed data. | Available data/details shall be shared with bidder during detailed engineering. |
|  |  | 2. Technical specifications folder: 1.0 Sections_Project_Statcom Ramgarh.pdf, page 26 of 30, section 13.13 | For integration of STATCOM control and protection system, the configuration of hardware, software, its integrated testing (both dynamic and steady state) is to be carried out at the works. Simulation testing is required to be carried out on RTDS. | Please inform is control system hardware along with RTDS hardware to perform RTDS hardware in loop studies at works to be provided? Please RTDS hardware along with control replica to be delivered to customer location as part of scope of work. | The provisions of the Technical Specification are amply clear and bidder shall follow the same. |
|  |  | 2. Technical specifications folder: 1.0 Sections_Project_Statcom Ramgarh.pdf, page 26 of 30, section 13.13 | During RTDS testing and configuration, POWERGRID representative is required to be closely associated. | Employer is invited to witness RTDS studies during the FAT late in the project. It will not be possible to have Employer to participate in every kind RTDS testing and configuration to be performed as part of the project | Noted. |
|  |  | 2. Technical specifications folder: 1-4 Annexure-IV_Details of System Studies to be performed.pdf, Page 1 of 6, section 2.iii | STATCOM Station Dynamic response studies to verify its dynamic performance. | Bidder understand that step response requirements provided in section 6.1.8 of 4.0 STATCOM Specification Rev-2 May-2020.pdf to be considered for Dynamic response studies. Please confirm. | Noted. |
|  |  | 2. Technical specifications folder: 1-4 Annexure-IV_Details of System Studies to be performed.pdf, Page 1 of 6, section 3 | 3. studies to be carried out by the customer | PSS®E load flow (.sav files) and dynamic data (.dyr files) and supporting documents/ files are missing in technical specification folder. As per the previous practise, We understand that Employer shall provide the Peak Load and Light Load models to the bidder before the contract is awarded, which is essential to fulfill the performance requirement of STATCOM. Therefore, we request the Employer to provide the needful. Bidder request the Employer to provide the following regarding these PSS®E network models: 1. Employer needs to provide the PSS®E network cases (sav case, dynamic file, DLLs if any) along with the necessary instructions to initialize the files up to two network scenarios. 2. The PSS®E network models should have flat start without any jumps. 3. These network models will be complete and final otherwise it is Employer’s responsibility to provide any missing models/data, e.g., vendor specific models, in the appropriate format and PSS®E version. 4. Sequence data for the elements needs to be provided. Sequence data is important for asymmetrical fault behavior. Please be noted that bidder can support or coordinate with the Employer for the employer's network with the assumed data as a separate agreement, if needed. | Kindly refer amendment-I |
|  |  | 2. Technical specifications folder: 1-4 Annexure-IV_Details of System Studies to be performed.pdf, Page 1 of 6, section 3.II | POD controller needs to be tuned based on the present and future scenario. | 1. In order to tune and verify the operation of a POD functionality Bidder requires to receive a full network representation in PSSE including dynamic of all devices contributing to the interarea oscillations modes, a list of contingencies which excite the modes of oscillations, the observed oscillations in the network in the previous events in the real network. 2. Bidder request Employer to sum up all lines measurements to provide as input to the POD controller. | POD Studies shall be carried out by the bidder as per simulation files provided to the bidder. In case, additional study files, for real time frame, are required by the bidder for additional POD studies, same shall be provided by employer at that stage, if available. |
|  |  | 2. Technical specifications folder: 1-4 Annexure-IV_Details of System Studies to be performed.pdf, Page 2 of 6, section 3.III | b. Load flow and dynamic model for new STATCOM Station needs to be provided in both PSSE (version 33) and PSCAD format along with manual on how to use this model in further studies. | Bidder understand that STATCOM model of the Ramgarh is need to provided in PSS®E version 34 and PSCAD v4.6.3. IVF compiler 15 version will be used to run PSS®E versions 34. Intel® Visual Fortran Compiler XE 14 version will be used to run PSCAD v4 models Please confirm is intel fortan compilers should not be supplied from the bidder. | The requirement of Bidding document is to be complied. |
|  |  | 2. Technical specifications folder: 1-4 Annexure-IV_Details of System Studies to be performed.pdf, Page 2 of 6, section 3.2.h | To demonstrate & prove that the STATCOM Station generated non-characteristic harmonics do not excite resonances in the Owner’s network. | With reference to the requirements, UIF study will first be performed to determine the possible risk of sub-synchronous resonance with nearby generator plants. If that study shows a risk for sub synchronus resonance (SSR), then further PSCAD studies are conducted. Further, If SSR studies in PSCAD shows that there are problems associated to the sub-synchronous oscillation and the proposed STATCOM control, an gain parameters of the proposed STATCOM will be adjusted to improve the damping. | Noted. |
|  |  | 2. Technical specifications folder: 1-4 Annexure-IV_Details of System Studies to be performed.pdf, Page 2 of 6, section 3.III.c ''2. Technical specifications folder: 1-4 Annexure-IV_Details of System Studies to be performed.pdf, Page 1 of 6, section 3.I.iii | Standard Models for SVC/STATCOM of Northern Region provided below shall be considered by the bidder for tendering purpose. Details of the dynamic models shall be discussed during detailed engineering The load flow and dynamic file available with the owner shall be provided to the contractor in PSSE version 34 format. If additional data is required it shall be intimated to owner at least 3 weeks before study commencement. If data is not available (same shall be confirmed by owner), typical data shall be assumed by the contractor. | PSS®E load flow (.sav files) and dynamic data (.dyr files) and supporting documents/files are missing in technical specification folder. Bidder will take the responsibility to model, integrate the proposed Ramgarh STATCOM as per the technical specification requirements only. Bidder can't take the responsibility to model, and integrate any other STATCOM, SVC and HVDC in the Employer's AC network. Bidder request the Employer to provide the final PSS®E network models should have flat start without any jumps and oscillations. 1. Employer needs to provide the PSS®E network cases (sav case, dynamic file, DLLs if any) along with the necessary instructions to initialize the files up to two network scenarios. 2. These network models will be complete and final otherwise it is Employer’s responsibility to provide any missing models/data, e.g., vendor specific models, any other HVDC and FACT devices in the appropriate format and PSS®E version. Sequence data for the elements needs to be provided. Sequence data is important for asymmetrical fault behavior. Please be noted that bidder can support or coordinate with the Employer for the employer's network with the assumed data as a separate agreement, if needed. | Please refer amendment-I for PSSE files. |
|  |  | 2. Technical specifications folder: 1-4 Annexure-IV_Details of System Studies to be performed.pdf, Page 2 of 6, section 3.II.e | Demonstrate the ability of the STATCOM to withstand the effects of negative & zero sequence unbalanced currents present in the 400 kV & 765 kV systems. | The performance of the STATCOM will be demonstrated by considering the point of connection only. | Noted. |
|  |  | 2. Technical specifications folder: 1-4 Annexure-IV_Details of System Studies to be performed.pdf, Page 3 of 6, section V.A | Contingency Cases for Ramgarh STATCOM | Balanced faults can be Investigated in PSSE. Whereas balanced faults and unbalanced faults will be investigated in PSCAD/EMTDC. | Noted. |
|  |  | 2. Technical specifications folder: 1.0 Sections_Project_Statcom Ramgarh.pdf, page 16 of 30, section 5 | The Contractor shall supply at no extra cost to the Employer any additional material/equipment/services not covered by these lists | The bidder will list all the necessary studies to complete the design and engineering during the bid stage itself. Anything additional requested from Employer dure the project stage will be agreed between bidder and customer under separate agreement on a need basis. | The provisions of the Technical Specification are amply clear and bidder shall follow the same. |
|  |  | Volume-II Part-3 of 7 folder: 4.0 STATCOM Specification Rev-2 May-2020, page 55 of 63, section 9.2.1 | Pre-manufacturing engineering design and verification studies should be performed by the contractor within the scope of supply after contract awarded. | Dynamic Performance Studies have been listed under "Pre-manufacturing" studies. It is noted that the Dynamic Performance Studies are not critical for ordering of components and therefore will not be tied to the manufacturing of equipment. | Noted. |
|  |  | Volume-II Part-3 of 7 folder: 4.0 STATCOM Specification Rev-2 May-2020, page 55 of 63, section 9.2.1 | These studies are in addition to the actual STATCOM Station design simulator and field performance tests. | There is no value to verification studies the model against field performance results as our previous experience shows that it would be very difficult, if not impossible, to model the behavior/impact of the actual network and other available active devices in the simulated network. | The provisions of the Technical Specification are amply clear and bidder shall follow the same. |
|  |  | Volume-II Part-3 of 7 folder: 4.0 STATCOM Specification Rev-2 May-2020, page 57 of 63, section 10.1.b | The simulator should provide an accurate network representation including network harmonic behavior. | The harmonic frequencies vary from the full network equivalent to reduced network equivalent. Depending upon the network size, the presence of harmonic frequencies in the network will change over time due to different operating conditions. Bidder would like to confirm that accurate network representation including network harmonic behaviour is compromised and can't guarantee network harmonic behavior in the RTDS. | The provisions of the Technical Specification are amply clear and bidder shall follow the same. |
|  |  | Volume-II Part-3 of 7 folder: 4.0 STATCOM Specification Rev-2 May-2020, page 57 of 63, section 10.1.b | The simulator should provide an accurate network representation including network harmonic behavior, as well as synchronous condensers, power stations, generators (with AVRs), and pump storage schemes, existing HVDC, SVCs and STATCOMs, future SVCs and STATCOMs, FSC (fixed series capacitors), and shunt reactors/capacitors/filters. | Bidder requests to provide the representative detailed models of synchronous condensers, generators (with AVRs), existing HVDC, SVCs and STATCOMs, future SVCs and STATCOMs models in RSCAD format without any need for additional tuning and adjustment. Please be noted that, RSCAD does not have generic models. In RSCAD network equivalent, Bidder doesn't create generic models for STATCOM models and PV/solar control models from other manufactures as generic models provide inaccurate performance, Bidder request to provide these models and make sure that these models give the accurate network representation. And, Bidder will not take any action to adjust the STATCOM control system based on the results on the reasoning that the results are not representative of the actual devices | The required data/details shall be shared with bidder during detailed engineering. |
|  |  | Volume-II Part-3 of 7 folder: 4.0 STATCOM Specification Rev-2 May-2020, page 55 of 63, section 9.2.1.ii | Study of response time and of the STATCOM Station’s behavior and contribution to the system’s recovery from faults | We understand that although the STATCOM station includes switching devices like MSC/MSRs, Step response study is applicable for STATCOM only as switching devices like MSCs/MSRs are associated with delayed Mechanical operation. | Confirmed. |
|  |  | Volume-II Part-3 of 7 folder: 4.0 STATCOM Specification Rev-2 May-2020, page 56 of 63, section 9.4.b | Study of STATCOM Station protection and protection coordination. | 1. Protection coordination study report based on the certain calculation will be provided. No protection coordination study executed using the PSCAD. 2. Bidder would like to inform that the protection refer to physical relays that are outside the control system will be excluded in the model. | Noted. |
|  |  | Section 1 Technical specification: Section-Project- Rev-00 clause 13.7 4.0 STATCOM Specification Rev-2 May-2020 - 8.9 Couplig Transformer | The Coupling Transformer shall be designed based on the design of similar type of Transformer which has been tested successfully for dynamic short circuit type test. | As per Cl.no: 13.7 of Technical specification: Section-Project- Rev-00; Only SC test report of transformer meeting two conditions absorbed power (30-130%) and Impulse level 1425kVp will be provided and as per IEC 60076-5 Annexure-A, Cl.no: A.3.3.3, design review document based on manufacturer’s design rules for short-circuit strength will be provided. SC similarity as per annexure A&B of IEC 60076-5) is not applicable. Please confirm the acceptance. | Bidder to comply the requirement mentioned in technical specifications. |
|  |  | Technical Specification: Section -Transformer (Upto 400kV Class) Clause 10.2 | Bushing type LV side | LV side bushing insulation level will be of LI/PF 325/140kVrms, we propose to use OIP type bushing for LV side, kindly confirm. | Rating (voltage/current) of LV side bushing shall be finalised during detailed engineering, based on basic design report, however type of bushing shall be in line with TS requirement. |
|  |  | Technical Specification: Section-STATCOM Station, Rev02 (May, 2020) clause 8.9.2 | Transformer Characteristics, insulation level for HV: LI/PF: 1425/630kVrms | For 400kV class transformers, customer standard insulation will be LI/PF: 1300kVp/570kVrms. Kindly confirm. | Bidder to comply the requirement mentioned in the technical specification. |
|  |  | Section 1 Technical specification: Section-Project- Rev-00 clause 8.1.7. Tests on STATCOM Unit Valve | Tests on STATCOM Unit Valve | The repetition of Type test for STATCOM valve is not envisaged under the present package . We will submit valid type test reports from Principal/parent of the bidder .However the type tested valve and offered valve from Indian manufacturing facility shall have same design , sourcing of key component like semiconductor devices , DC capacitor . Kindly confirm. Ay repetition of type test will have time impact & considering the overall project duration. Please con | Please refer amendment-I. |
|  |  | General | Firefighting System | PGCIL to inform substation contractor that design calculation of fire protection system shall also consider STATCOM area as STATCOM contractor has to tap water supply from existing system. Please confirm our understanding | Confirmed. |
|  |  | General | CRP & SAS | Kindly provide the make of CRP & SAS for Substation | Make and model of existing substation shall be provided during detailed engineering to successful bidder. |
|  |  | Price Schedule , Mandatory Spares | Item "Semiconductor based Power module (sub-module) of Multimodule valve of each rating and type " in price schedule | We understand bidder can recommend the quantity of spares as per OEM specific design. | Please refer clarification against similar query at sl no 103. |
|  |  | General | Civil Works | We understand that from the prebid meeting that a levelled land meeting the PGCIL design conditions will be provided to the successful bidder by the Employer . Please confirm | Please refer Clause 2.2.2.3 a) of Section project wherein it is mentioned that - Site levelling of STATCOM Yard & 400 kV Yard as per contours provided by the contractor. HFL (Highest Flood Level) data shall be arranged by contractor duly verified by employers site officials for finalization of FGL (Finished Ground Level). |
|  |  | General | SLD & Drawings | Kindly provide the SLD of the Substation portion indicating the STATCOM 400kV Bays in the SLD as it is essential for engineering works . Kindly provide the overall layout and plot plan indicating STATCOM area and the interconnection to Substation with clear mention of 400kv bays position in substation area. | Please refer clarification against similar query at sl no 107. |
|  |  | Civil Works |  |  |  |
|  |  | Site location | Site location & Coordinates of the land | We reqeust you to kindly furnished the Site location & coordinates of the land identified for STATCOM at Ramgarh-3 | The Required details/document shall be provided to successful bidder during detailed engineering. |
|  |  | Plot Plan & 400kV SS layout | Plot Plan & 400/220kV Layout | We request you to kindly furnished the Plot plan & Layout of 400/220kv Substation enabling us to understand the interconnection with STATCOM . Layout is essential to estimate the quantities of work to be performed related to 400kV bay interconnection works with STATCOM | Please refer clarification against similar query at sl no 107. |
|  |  | Soil investigation & Contour drawing | Soil investigation & Contour drawing | We request you to kindly furnished the Soil investgiation & Contour drawing for the proposed 400/220kv S & STATCOM area | Soil Investigation and contouring and site leveling is in the scope of the contractor. Bidder may qoute as per the provisions of the bidding documents. |
|  |  | Terrace level of STATCOM & 400kV SS | Terrace level of STATCOM & 400kv SS | Kindly indicate whether 400k/220kv SS and STATCOM is planned in Single Terrace Level or Multilevel. | Finalisation of the FGL shall be done during detailed engineering. |
|  |  | Site Levelling /Site Grading works | Site Levelling /Site Grading works | We understand that for Propsoed STATCOM area & 400kv Interconenction area PGCIL Shall hand over Levelled Site at Single Level & No Site grading works/ Slope protection/Retaining works are in Bidder's scope kindly confirm the same. | Kindly refer Section Project, contouring and site levelling is in the scope of the contractor. |
|  |  | General | Approach upto STATCOM location | We understand that PGCIL Shall be provide Motorable approach road suitable to transport the heaviest equipment to the site location, without any hurdles from the Manufacturing unit to the site including Civil Contractor's Construction machinery & Construction Material be reachable to site for mobilization & Start of Civil works | Bidder may qoute as per the provisions of the bidding documents. |
|  |  | Tranformer Foundation | Transformer Foundation | We understand that Foundation of all Power Transformers shall be with raft and wall type support with gravel filling excluding grating. 1 No. common burnt oil tank has been considered with Provision of 1 No Common Burnt oil Tank. Kindly Confirm our understanding | Technical Specification, Secction: Civil Works, Rev 11A is amply clear wrt to the specification of a transformer/ reactor foundation. Kindly refer the same. |
|  |  | Rail Cum Road in front of Serires of Transformer | Rail Cum Road in front of Series of Transformer | Rail cum Road: Rail cum road shall only be provided between edge of near by road to edge of soakpit of transformer. No Rail cum road is required to be provided for full length in front of series of transformers. Kindly Confirm our understanding | Bidder may qoute as per the provisions of the bidding documents. |
|  |  | General | Civil Works Price Schedule | We request you to convert civil works Price schedule on Unit rate basis for the entire scope of works in the absence of Key inupts such as exact location etc. | Bidder may qoute as per the provisions of the bidding documents. |
|  |  | Additional Clarifications |  |  |  |
|  |  | Volume -II Part 1 of 7_ 1.0 Sections_Project_Statcom Ramgarh Clause: 4.0, II | Meteorological data | The below mentioned data are not covered in the specification. 1. Relative humidity 2. Maximum solar constant 3. Corrossion level 4. GPS coordinates | The design of equipment shall be as per meteorological data from the Authorized government department. However, ambient Temperature shall be considered as per clause 4.0 of Section project |
|  |  | Volume -II Part 1 of 7_ 1.0 Sections_Project_Statcom Ramgarh Section GTR, Rev-15 clause 2.1 (a) | All equipment/materials/items, as per Annexure-K (Rev 01), as applicable under present scope of works, shall be procured and supplied from domestic manufacturers only with Minimum Local Content for individual items as listed | We noted the items which mentioned in the annexure-K_R01.However,apart from Annexure-K_R01, we will supply from domestic manufactures / overseas manufactures. | Noted, Subject to meeting the GFR guidelines notified by Govt. of India. |
|  |  | Volume -II Part 1 of 7_ 1.0 Sections_Project_Statcom Ramgarh Annexure-III | Portable Earthing kit | Pl confirm that the poratble earthing kit should be of Catu France make or any other country make. | Kindly refer amendment-I Make shall be finalized during detailed engineering stage based on submitted details by contractor. |
|  |  | Volume -II Part 2 of 7_ GTR GTR-Annexure B | The seismic withstanding test on the complete equipment (for 400kV and above) shall be carried out along with supporting structure. Seismic Withstand Test carried out using either lattice or pipe structure is acceptable.” Seismic Calculations certified by NABL Labs shall also be acceptable | As STATCOM area equipment are rated with less than 400kV, no seismic test are considered. | Noted. |
|  |  | Volume -II Part 3 of 7_ 3.0 400kV Transformer _Rev 13, 1.1 | Spare Transformer Unit Storage & Connection Arrangement, 1) Transformer with Isolator switching arrangement: 2) Transformer without isolator switching arrangement: | We shall follow as per the details provided in"4.0 STATCOM Specification Rev-2 May-2020". | Kindly refer clause no 2.2.1 b) of section project for spare coupling transformer switching arrangement . |
|  |  | Volume -II Part 3 of 7_ 3.0 400kV Transformer _Rev 13, 1.1 | Spare Transformer Unit Storage & Connection Arrangement, 1) Transformer with Isolator switching arrangement: 2) Transformer without isolator switching arrangement: | We shall follow as per the details provided in"4.0 STATCOM Specification Rev-2 May-2020". | Please refer reply above. |
|  |  | Volume -II Part 3 of 7_ 4. Section-STATCOM Station Clause: 6.7.5 & 8.10.2.4 | However, the leakage distance for all AC insulators for outdoor installation shall not be less than 25 mm/kV of the maximum operating phase to earth rms voltage at the insulator. | As per specification clause no: 8.10.2.4 the creepage distance value for insulator mentioned as 31mm/kV. Kindly check and confirm. | Clause no 6.7.5 of Technical Specification STATCOM Station rev 02 is being referred for 400kV System except for Bushing & long rod polymer insulator, however clause no 8.10.2.4 is referring above MV switchyard. |
|  |  | Volume -II Part 3 of 7_ 4. Section-STATCOM Station Clause 6.5 | Audible Noise | Sound prediction calculation covers outdoor emissions only. Indoor propagation is not to be modelled since it does not have contribution to the outdoor sound. Information on indoor noise levels can be found below. * Indoor sound for cooling pumps: Cooling pump unit will not be located in a room where people work permanently. Therefore, higher sound levels can be allowed in this room than in rooms where people work permanently. Bidder has designed cooling pumps to have a maximum sound pressure level of 75 dB(A) at 2 m distance. Signage warning personnel of higher audible noise levels in the rooms and of temporary ear protections are recommended. * Indoor sound for control and protection: Bidder recommends a maximum sound level of 65 dBA in this kind of rooms, which allows a normal conversation held in normal voice. *Access to Valve room is NOT allowed during operation. Hence, the sound in this room during operation should not be of interest and during maintainance all the equipments will be in OFF condition. | In case Valve hall is not accessible during operation, then measurement inside value hall shall not be applicable, however calculation for noise level inside valve hall shall be provided. For other locations, bidder shall comply the requirement of TS and measurement shall be done to meet the requirements. |
|  |  | Volume -II Part 3 of 7_ 4. Section-STATCOM Station 6.3 | To minimize the probability of electrical fault suitable arrangement i.e. electrified fence shall be done to prevent the encroachment of unwanted animal or other to minimize the probability of electrical faults (Ph-E, Ph- Ph). | We understand that, the electrified fence will be applicable for only outdoor boundry fence not branch fences. | Confirmed. |
|  |  | Volume -II Part 3 of 7_ 4. Section-STATCOM Station 8.3.2 | The Contractor shall provide the necessary wiring from existing Switchgear to its control room. | Request to provide the scope of interconnections and tentative routing as to finalize the battery limit. | The required details/data shall be provided to the successful bidder during detailed engineering. |
|  |  | Volume -II Part 3 of 7_ 4. Section-STATCOM Station 8.10.2.3 | Blades | With reference to that clause, we understand that blades should be copper.pl confirm | Bidder may quote as per bidding document. |
|  |  | Volume -II Part 3 of 7_ 4. Section-STATCOM Station 9.6 | Other studies - d) Magnetic field strength | We understand that, Magnetic field strength will be B Field calculation with our in house software.pl confirm. Also we will follow ICNIRP 2010. Please confirm. | Bidder to comply the requirement mentioned in the Technical specifications. |
|  |  | Volume -II Part 3 of 7_ 6. Switchgear - ISOLATOR: C/ENGG/SPEC/SWGR/R12 Clause: 7.0 | The terminal pad shall be suitable for horizontal plane connection with terminal connector. The terminal pads for all isolators with 3150A & above rating shall have six holes for terminal pad. | For terminal pad hole arrangements will be as per NEA CC1. For Imax<2000Amps - 4holes. 2000Amps<Imax<3000Amps - 6holes. Imax>3000Amps - 8holes. | Bidder understating is generally in order. |
|  |  | Volume -II Part 3 of 7_ 10.0 LT Switchgear_R5 | Suitable arrangements shall be provided at each end of the horizontal earth bus for bolting to Purchaser's earthing conductors. | Pl confirm the scope of earthing for this panels as this will be part of above ground earthing. | Please refer clause 1.4.3 of Section LT Switchgear wherein requirements of earth bus is specified Confirmed. |
|  |  | Volume -II Part 3 of 7_ 10.0 LT Switchgear_R6, 1.1.1 | for supply for colony lighting from control room. | Pl note, Any type of work for Colony lighting will be excluded from our scope. | Confirmed. |
|  |  | Volume -II Part 4 of 7_ 14. Diesel Generator 1. Section-Diesel Generator, Clause: 1,0 2. Section project, Rev-0, Clause: 4, II | The scope covers supply, erection testing and commissioning of Diesel Generator set of stationary type. The D.G. Set shall have a net electrical output as specified in the BPS, under the site conditions of 40deg.C ambient temperature & 1000 meters altitude. This net electrical output shall be measured after reducing all power consumptions for D.G. Set auxiliaries. | In the technical specification: Section project, Rev-0, Clause: 4, II(Meteorological data), the design ambient temperature mentioned as 50deg. C. please confirm the design ambient for DG. | Bidder to comply with the ambient temperature requirement i.e., 40deg. C mentioned in Technical Specification, Section: D.G. SET, no: 5 regarding. However overall requirements of auxiliary power to be met by bidder as per technical specification and confirming the ambient temperature requirement mentioned in the Section project. |
|  |  | Volume -II Part 5 of 7_"17.0 Section Structure Rev 6", 2 | Structural Loading | 1) As per spec all loading calc to be followed as per IS 875:1 to 5 and IS1893. Then what is the significance of "Vulnerabilty atlas of India" 2) Since this station is located in High temp variation zone, is there any specific the temperature load requirement for structure design? | Bidder may qoute as per the provisions of the bidding documents. |
|  |  | Volume -II Part 5 of 7_"17.0 Section Structure Rev 6", 4.4 | Fabrication and Erection | Guidlines for site modification is not available. | Bidder may qoute as per the provisions of the bidding documents. |
|  |  | Volume -II Part 6 of 7_"18.0 Civil Works Rev 11A-Cor slip-5" 3 | Standard Drawings | As per spec many standard drawings are available, but we have very limited drawings. How to get the other standard drawings | Drawings necessary at the stage of bidding are provided as a part of the tender drawings. Other darwings to be issued by POWERGRID shall be issued to the successful bidder. Designs and drawings to be prepared by the contractor during the detailed engineering are mentioned in the Section Project. |
|  |  | Volume -II Part 6 of 7_"18.0 Civil Works Rev 11A-Cor slip-5" 11.1.2 | Primary members are fabricated from plates and sections with minimum yield strength of 340 Mpa to suit design by continuous double side welding. | a) What is the min structural steel grade to be used for the Primary hot rolled structural members / Hollow sections / Pipe sections? b) hat will be the min steel garde for miscellanious steel members? c) Is the structural profiles should be of IS or EN profiles can also be used? Please confirm | Technical Specification, Section: Civil Works, Rev 11A is amply clear wrt the query. Bidder may qoute as per the provisions of the bidding documents. |
|  |  | General | Standard Fence | Stanadard Fence drawing is not available | Drawings necessary at the stage of bidding are provided as a part of the tender drawings. Other darwings to be issued by POWERGRID shall be issued to the successful bidder. |
|  |  | General | Standard Steel Drawings | This any standard format for steel drawings to be followed ? or Hitach Energy standard practise can be followed? Please clarify | Query is not clear. Bidder may qoute as per the provisions of the bidding documents. |
|  |  | Price Schedule-S.No 15.9 Sch 1b | Auxiliary supply system as per clause 2.2.1 of section project, technical specifications | As per 2.2.1 of section project, technical specifications the LV winding voltage level is mentioned as 415V. However, Appendix A of Technical Specification, Section: LT Transformer C/ENGG/SPEC/LT-TRF Rev. No. 5 mentions 433 V as the LV side voltage. Kindly clarify the LV side voltage requirement. | Both type of configuration in LV side either 415V & 433V are acceptable, subject to meeting the requirement of technical specifications. |
|  |  | Section 8.11 of 4.0 STATCOM Specification Rev-2 May-2020 | Auxiliary supply at 33 kV side | The bidder wants to know the source of auxiliary supply to the STATCOM station from the customer side. What is the configuration(delta, star) of the ICT at 33kV side. Please specify the surge arrester rating at the tertiary winding of the ICT if there any surge arrestors for restricting the surges to the auxiliary supply. And please specify the distance of any cable in between the source of supply to the STATCOM station. | Please refer clause no 3.12 of -Transformer (Upto 400kV Class) Rev. 13 for specification of tertiary winding of 500MVA, 400/220/33kV transformer. Further, other details like distance etc. shall be provided to successful bidder during detailed engineering. |
|  |  | Volume-II Part-3 of 7 "4.0 STATCOM Specification Rev-2 May-2020" Clause 8.11 | One of the main incomer shall be supplied from 33kV tertiary winding of 400/220/33kV ICT existing at the substation as per the detail provided in Section Project. | Bidder requests the customer to provide the 33kV incomer from tertiary winding of 400/220/33kV ICT that is closest to the STATCOM station layout. | Bidder may Quote as per bidding document |
|  |  | Technical specification: Section-Project- Rev-00, Clause 8 | ii) Availability Spares The contractor shall supply the spare parts required to meet the specified guaranteed availability and shall include such spare parts in the scope of supply | The bidder doesn’t envisage supply of any separate availability spares because the guaranteed availability is being met considering the mandatory spares listed in the price schedule. Please confirm. | Please refer reply against similar query at sl no 103. |
|  |  | Volume-II Part-3 of 7 “4.0 STATCOM Specification Rev-2 May-2020” Clause 8.11 | Auxiliary supply from 33 kV side of ICT | Please provide the SLD with the details of “33kV tertiary winding of 400/220/33kV ICT existing at the substation”. | Please refer reply against similar query a Sl no 3. |
|  |  | Technical Specification: Section -Transformer (3.0 400kV Transformer _Rev 13) clause 10.2 | Bushing Type | Bidder requests proposal similar to amendment provided in previous tender "HV Bushing of coupling transformer shall be RIP bushing with Polymer/composite insulator, MV Bushing of Coupling Transformer shall be of OIP/RIP type with porcelain/Polymer/ composite type insulator and Neutral bushing shall be solid porcelain or oil communicating type." Please confirm acceptance. | Bushing type for coupling transformer shall be as per clause no 10.0 of Section Section -Transformer (Upto 400kV Class) Rev. 13. |
|  |  | Volume-II Part-3 of 7 "4.0 STATCOM Specification Rev-2 May-2020" Clause 6.1.4 d | The contractor shall demonstrate to the satisfaction of the Employer that STATCOM Station will not excite ferro-resonance and sub-synchronous oscillation in the AC system. | In our design we have following design actions for minimizing the Ferro-resonance risk· . Resistor across open-delta connection of secondary VT in our design. · Wye grounded transformer at HV side. Therefore, STATCOM Station will not excite ferro- resonance. UIF study will first be performed to determine the possible risk of sub-synchronous resonance with nearby generator plants. If that study shows a risk for SSR (UIF values above 0.1), then further PSCAD studies are conducted. Further, If SSR studies in PSCAD shows that there are problems associated to the sub-synchronous oscillation and the proposed STATCOM control, an SSDC will be developed to improve the damping. | Noted. |
|  |  | Volume-II Part-3 of 7 "4.0 STATCOM Specification Rev-2 May-2020" Clause 8.1.3 | Sub module shall be designed to guarantee high maintainability with self-sealing type hydraulic valves and electrical plugs for ease of installation or un-installation. | Design requirement on submodule design with self- sealing type hydraulic valves and electrical plugs is not applicable for valve design because we do not have any hydraulic valves. Because we do not have any hydraulic valves in our design. | Acceptable provided offered design meets the functional requirements. |
|  |  | Volume-II Part-3 of 7 "4.0 STATCOM Specification Rev-2 May-2020" Clause 8.9.2 – 1.19 | Max Noise level at rated voltage and at principal tap at no load and all cooling active: 80 dB | The requirement is not clear, could you kindly clarify whether this is a sound power level or a sound pressure level. If sound pressure level, then please confirm the distance. | The value specific corresponds to Sound pressure level. |