| SN |  | Clause reference | Provision in Specification | Bidder’s Query | POWERGRID Reply |
| --- | --- | --- | --- | --- | --- |
|  |  | M/s Hitachi |  |  |  |
| 1. |  | Tech Specification, Section: CRP, Rev.NO-09, Clause 12 | Annunciator System for Control Panels | Audible annunciator is not available. However, the alarms and status can be viewed on HMI. All the status and alarms will be present in the HMI workstation located in the STATCOM Control building, the Remote HMI workstation located in Main control building will also have all status and alarms and these will be transferred to SCADA via IEC 61850 protocol. | Auditable Annunciator in HMI is to be provided. |
| 2. |  | 4.0 STATCOM Specification Rev-2 May-2020 - 6.1 f) | The STATCOM Station should be capable of repeating temporary operation as defined in any one of item (d) and (e) as above for at least 3 charging cycles in 60mins. | Please clarify the time duration to be considered in between the two consecutive charging cycles. Due to lack of information, Bidder assumes that the duration between two consecutive cycles is approximately 19 minutes. (3 cycles in 60mins). The text in IEEE 1052-2018 8.1 i) also says "repeating temporary operation every ___min". Please confirm the duration between two consecutive cycles. | Bidder may quote as per bidding document. |
| 3. |  | 4.0 STATCOM Specification Rev-2 May-2020 - 8.3.2 r) | STATCOM MV Bus Protection: i. Bus Differential protection (87) ii. Groundovercurrentprotection(51N),usedwithneutralGroundingTransformer iii. Under/Over Voltage(59Ph-Ph)protection iv. Over voltage (Open Delta)protection STATCOM Branch Protection: i. Differential protection(87) ii. Overload protection(49) iii. Over current protection inside delta (50,51) iv. Negative phase sequence protection(46) v. STATCOM branch over current protection (50, 51, 50N,51N) | For Bus Differential protection (87): In STATCOM branch measurement device of type Electronic Current Transducer(ECT) to measure current in VSC legs with high accurracy are used. * Conventional CT’s are not used due to required measurement accuracy and measurment of DC currents. * STATCOMs since 1996 have been designed without differential protection in the VSCs. Protection scheme is well-proven with excellent operational experience. Further, IGBTs will quickly be turned-off (e.g. within 1-2 ms) in case high currents flowing through the delta connected VSC converter. Such IGBT action will effectively convert differential protection into a simple instantaneous OC protection which is anyhow provided. Contractor base solution for protection of VSCs are much faster than a conventional differential protection. 4.Please also refer to IEEE1052TM-2018. 5. 6. Overcurrent protection inside delta: Valve overcurrent protection(VOCP) in statcom control system will provide the necessary overcurrent protection | Kindly refer reply against similar query in Clarifications-I (Technical Portion-Part 1) sl no 185 attached herewith. |
| 4. |  | Volume-II Part-3 of 7 folder: 4.0 STATCOM Specification Rev-2 May-2020, page 16 of 62, section 6.1.8 | STATCOM station response shall be such that the change in measured system voltage to small disturbance should reach 90% of the desired total change within 30ms of the initiating a 5% step change of voltage reference. | Bidder understands that, As per IEEE 1052-2018, the step response requirements of STATCOM shall be fullfilled in Thevenin network only. Kindly confirm. | Bidder to quote as per provisions of bidding documents. |
| 5. |  | Volume-II Part-3 of 7 folder: 4.0 STATCOM Specification Rev-2 May-2020, page 55 of 62, section 9.2.1.IV 2. Technical specifications folder: 1.0 Sections_Project_Statcom Ramgarh.pdf, page 25 of 30, section 9.7 | Studies to evaluate the interaction of the STATCOM controls with the other nearby control systems, including high-voltage direct current (HVDC) controls, generator controls, and controls of other flexible ac transmission systems (FACTS) devices | Interaction study will be performed. And if the source of interaction is from Ramgarh STATCOM the same will be tuned to avoid such scenario. However, if the interaction is caused by other devices other than, RAMGARH STATCOM station, the same shall not be under contractor scope. | Bidder to comply the requirement mentioned in the Technical specifications. |
| 6. |  | 1. 'Volume-II Part-3 of 7 folder: 4.0 STATCOM Specification Rev-2 May-2020, page 55 of 62, section 9.7.a 2. Technical specifications folder: 1.0 Sections_Project_Statcom Ramgarh.pdf, page 25 of 30, section 9.7 | The vendor should provide a detailed STATCOM Station dynamics model both in UDM & validated generic for use in (PSCAD and PSSE) power flow and stability simulation software. | Kindly confirm that the Additional clarifications dated 22.07.2023 on RFP Project Documents for selection of Bidder as Transmission Service holds good. i.e., For PSS/E, both Generic & User-defined models shall be shared by the TSP with the CEA, CTU & Grid-India. Generic model response shall be benchmarked with user-defined model to the extent possible by the TSP. Generic models can be shared by the CEA, CTU & Grid-India with the concerned stakeholders e.g., STUs etc. For User Defined model, confidentiality shall be maintained by the CEA, CTU & Grid-India. For PSCAD/EMTP-RV, User Defined model shall be provided by the TSP for which confidentiality shall be maintained by the CEA, CTU & Grid-India. As per latest techncial specification amendments, Bidder understand that EMTP RV Model is not part of the scope of supply during the project phase. Please confirm. | Bidder may Quote as per bidding document. Further in regard to confidentiality by CEA/CTUIL shall be maintained by them in line with RFP document issued by BPC. |
| 7. |  | Volume-II Part-3 of 7 folder: 4.0 STATCOM Specification Rev-2 May-2020, page 11 of 62, section 6.1.2.1 | Voltage Control mode (Automatic and Manual) | Bidder understands that Voltage control mode operation will be in automatic mode only and not in Manual mode. Kindly confirm. Kindly note, as per specification clause 6.1.2.2 fixed reactive power control will be provided. | Voltage control mode shall be automatic as per Technical specification and shall also additionally be settable on manual mode. However for other, bidders to quote as per provisions of bidding documents. |
| 8. |  | 2. Technical specifications folder: 1.0 Sections_Project_Statcom Ramgarh.pdf, page 28 of 30, section 13.19 | For the design purpose, following Power System parameters (at PCC) may be considered: | Bidder understand that Minimum three-phase fault current (10.2 kA) and Maximum three-phase fault current (12.7 kA) under nominal system voltage level (400 kV) as provided in the Table SL 21 and 25 of section 13.19 need to be followed for performance evaluation during project stage. Please confirm. | Kindly refer reply against similar query at Sl no 194 in Clarifications-I (Technical Portion-Part 1) |
| 9. |  | 2. Technical specifications folder: 1.0 Sections_Project_Statcom Ramgarh.pdf, page 28 of 30, section 13.19 '2. Technical specifications folder: 1.0 Sections_Project_Statcom Ramgarh.pdf, page 14 of 30, section 2.3 2. Technical specifications folder: 1-4 Annexure-IV_Details of System Studies to be performed.pdf, Page 1 of 6, section 3 | 2.3.a Ensuring that the STATCOM STATION system is integrated with the existing power system network to have a trouble-free operation of complete A.C. network also comprising of HVDC and other FACTS installations 13.18 Information regarding List of HVDC & FACTS devices in the Power System is enclosed as Annexure-IX | Bidder will be responsible for RAMGARH STATCOM Station control and operation. The other HVDC/FACTS existing on the network shall be customers responsibility. Bidder request the Employer to provide the final PSS®E network models should have flat start without any jumps and oscillations. 1. Employer needs to provide the PSS®E network cases (sav case, dynamic file, DLLs if any) along with the necessary instructions to initialize the files up to two network scenarios. 2. These network models will be complete and final otherwise it is Employer’s responsibility to provide any missing models/data, e.g., vendor specific models, any other HVDC and FACT devices in the appropriate format and PSS®E version. 3. Sequence data for the elements needs to be provided. Sequence data is important for asymmetrical fault behavior. | Kindly refer reply against similar query at Sl no 195 in Clarifications-I (Technical Portion-Part 1) |
| 10. |  | 2. Technical specifications folder: 1.0 Sections_Project_Statcom Ramgarh.pdf, page 15 of 30, section 2.5 | The contractor shall carryout all the studies which may be necessary for completion of the design and engineering whether, these have been mentioned in the Bid by the Bidder or not. | Bidder understands that all required studies are included in specification. If any additional studies to be performed, the same shall be amended with specification, so that bidder can consider it in project schedule and cost. | Kindly refer reply against similar query at Sl no 197 in Clarifications-I (Technical Portion-Part 1) |
| 11. |  | 2. Technical specifications folder: 1.0 Sections_Project_Statcom Ramgarh.pdf, page 20 of 30 and 21 of 30, section12.1 and 12.1.a | Association and training of employer personnel scope and Training documentation. | Bidder will be able to provide training for 1-2 weeks. The agenda for the same can be mutually discussed and agreed during order stage. The tentative number of participants from customer side shall be provided and the plan can be accrodingly updated in project time schedule. | Kindly refer reply against similar query at Sl no 199 in Clarifications-I (Technical Portion-Part 1) |
| 12. |  | 2. Technical specifications folder: 1-4 Annexure-IV_Details of System Studies to be performed.pdf, Page 2 of 6, section 3.III | b. Load flow and dynamic model for new STATCOM Station needs to be provided in both PSSE (version 33) and PSCAD format along with manual on how to use this model in further studies. | Bidder understand that STATCOM model of the Ramgarh to be provided in PSS®E version 34 and PSCAD v4.6.3. | Kindly refer reply against similar query at Sl no 207 in Clarifications-I (Technical Portion-Part 1) |
| 13. |  | 2. Technical specifications folder: 1-4 Annexure-IV_Details of System Studies to be performed.pdf, Page 2 of 6, section 3.II.e | Demonstrate the ability of the STATCOM to withstand the effects of negative & zero sequence unbalanced currents present in the 400 kV & 765 kV systems. | The performance of the STATCOM will be demonstrated at PCC, However it is requested to customer to provide the contingency list which creates such scenario.. | Kindly refer reply against similar query at Sl no 210 in Clarifications-I (Technical Portion-Part 1) . |
| 14. |  | Volume-II Part-3 of 7 folder: 4.0 STATCOM Specification Rev-2 May-2020, page 56 of 63, section 9.4.b | The simulator should provide an accurate network representation including network harmonic behavior. | The RTDS network equivalent size (bidder proposed to be maximum up to 10 buses) will be decided by Bidder and Employer with the limitations considering availability of hardware and it's compatibility to model and run the real time simulation. | Bidder to quote asper provisions of bidding documents |
| 15. |  | Volume -II Part 1 of 7_ 1.0 Sections_Project_Statcom Ramgarh Clause: 4.0, II | Meteorological data | The below mentioned data are not covered in the specification. It is requested to customer to provide below info. 1. Relative humidity 2. Maximum solar constant 3. Corrossion level 4. GPS coordinates 5. Lightning ground flash density 6. Seismic design: Peak Ground Acceleration: (horizontal / vertical) [g/zone] | Kindly refer reply against similar query at Sl no 6 in Clarifications-I (Technical Portion-Part 1) |
| 16. |  | Volume -II Part 3 of 7_ 4. Section-STATCOM Station 8.3.2 | The Contractor shall provide the necessary wiring from existing Switchgear to its control room. | It is request to kindly provide the interconnections to be considered and tentative routing for cable trench assessment and to have clarity on delivery limit. | Bidder to quote as per provisions of bidding documents. |
| 17. |  | Volume-II Part-3 of 7 "4.0 STATCOM Specification Rev-2 May-2020" Clause 8.11 | One of the main incomer shall be supplied from 33kV tertiary winding of 400/220/33kV ICT existing at the substation as per the detail provided in Section Project. | Bidder requests the customer to provide the 33kV incomer from tertiary winding of 400/220/33kV ICT that is close to the STATCOM station layout. Customer to advise the distance from ICT to STATCOM site area. | Kindly refer reply against similar query at Sl no 145 in Clarifications-I (Technical Portion-Part 1) |
| 18. |  | Technical Specification: Section 2.2.1, Clause H | Integration of STATCOM station to substation SAS via IEC 61850 | It is reqiested to customer to clarify, if the Ramgarh substation SAS be designed with IEC 61850 supporting PRP configuration? | Bidder to quote as per provisions of bidding documents. |
| 19. |  | General | Clarifications and amendments | Bidder understands that the clarifications/Amendments received from REC/CEA/CTUIL for the subject project has the highest order of precedence. | Bidder to quote as per provisions of bidding documents. |
| 20. |  | Volume-II Part-3 of 7 "4.0 STATCOM Specification Rev-2 May-2020" Clause 6.7.5 | The leakage distance for all AC insulators for outdoor installation shall not be less than 25 mm/kV of the maximum operating phase to earth rms voltage at the insulator. | Bidder understands that all equipment bushings, except Power Transformer shall be of creepage “25mm/kVph-ph” corresponding to “Heavy” pollution. Power Transformer bushings, string insulators, long rod etc, shall be of minimum “31 mm/kVph-ph” creepage distance corresponding to “Very Heavy” pollution. Please confirm. | Kindly refer reply against similar query at Sl no 243 in Clarifications-I (Technical Portion-Part 1) |
| 21. |  | Volume-II Part-3 of 7 "4.0 STATCOM Specification Rev-2 May-2020" Clause 8.3.2.r | All CBs shall be provided with individual Breaker Failure protection relay. | Bidder proposes to offer breaker failure for Circuit breakers as part of respective bay main protection relay or Busbar protection relay such that each relay is not provided with more than one BF protection. Standalone relay/Dedicated relay for LBB is not considered. Kindly confirm. | Bidder to quote as per provisions of bidding documents. |
| 22. |  | 1-4 Annexure - IV DETAILS OF SYSTEM STUDIES TO BE PERFORMED Clause h | For the Network Harmonic Impedance and further harmonic calculations, based on the information in PSSE files provided refer to Section: STATCOM Station. | Bidder requests customer to provide the PSS/E files. | Kindly refer amendment-I (Technical Portion) attached herewith. |