| SN |  | Clause reference | Provision in Specification | Bidder’s Query | POWERGRID Reply |
| --- | --- | --- | --- | --- | --- |
|  |  | Electrical |  |  |  |
| 1. |  | Section Project SCOPE OF WORK (2.1) | The scope of this specification covers the following at 765/400/220kV Ramgarh PS S/s • STATCOM Station, having following rated capacity in 400kV Bus Section-1 (a) ±300MVAR STATCOM in 400kV Bus Section-1 (b) 2 x125MVAr Mechanically switched Shunt Capacitor(MSC) (c) 1 x125MVAr Mechanically switched Shunt Reactor(MSR) • STATCOM Station, having following rated capacity in 400kV Bus Section-2 (a) ±300MVAR STATCOM in 400kV Bus Section-1 (b) 2 x125MVAr Mechanically switched Shunt Capacitor (MSC) (c) 1 x125MVAr Mechanically switched Shunt Reactor (MSR) | Please reconfirm the requirement as we understand, STATCOM Station in 400kV Bus Section-2 shall be having ±300MVAR STATCOM in 400kV Bus Section-2. | On each 400kV bus section requirement of STATCOM is as under (a) ±300MVAR STATCOM (b) 2 x125MVAr Mechanically switched Shunt Capacitor(MSC) (c) 1 x125MVAr Mechanically switched Shunt Reactor(MSR) |
| 2. |  | SCOPE OF WORK (2.2.1-d) | Controlled Switching device (CSD) for 400kV Main breakers under present scope and Tie Breakers for which make shall be provide during detailed engineering | We understand the TIE breaker CSD shall be used to control Transformer / Reactor only. Pls confirm. | As there shall 2nos of Tie breaker CSD, they can be used to control transformer/reactor/coupling transformer as required. |
| 3. |  | SCOPE OF WORK (2.2.1-e) | 33/0.415 kV XXX kVA Auxiliary LT transformer along with associated 72.5kV out door switchgear equipment’s to be installed on tertiary of existing 500 MVA, 400/220/33 kV Auto transformer including cable for interconnection. | C&P of 72.5kV outdoor switchgear equipment can be incorporated in existing 500 MVA, 400/220/33 kV Auto transformer CRP. Please confirm. | Noted. |
| 4. |  | SCOPE OF WORK (2.2.1-i) | Complete relay and protection system as per Section – STATCOM for STATCOM Station installation and as per Section – CRP for the associated 400kV bays which inter-alia includes Circuit breaker protection and Bus bar protection augmentation. | We understand, Coupling Transformer Protection can be considered as part of 400kV bays Circuit Breaker protection. Pls confirm. | Bidder to quote as per provision of bidding documents. |
| 5. |  | SCOPE OF WORK (2.2.1-k) | Interface panel (if required) shall be provided for exchange of signals from the existing 400KV substation equipment (available in the form of potential free contacts) with control and protection system of STATCOM STATION, services and facilities | As an alternative option please confirm wheather the soft signals can be taken from existing switchyard? | Bidder to quote as per provision of bidding document. |
| 6. |  | SCOPE OF WORK (13.15-h) | The STATCOM Station System shall provide remote communication interface (RCI) in the form of gateways for simultaneous communications with multiple independent remote control centers as defined here. | Please share the number of remote-control centers, and the Communication protocol with them. | Bidder to quote as per provision of bidding document. |
|  |  | CIVIL |  |  |  |
| 7. |  | Civil Works | Layout | Please provide the Plot plan, layout if any. | Plot plan shall be provided to successful bidder during detailed engineering. |
| 8. |  | Civil Works | SBC & ERT Report | Please provide the Geotechnical Investigation Report (SBC) and ERT Report. | Soil Investigation is in the scope of the bidder. |
| 9. |  | Civil Works | Contouring Data | Contour drawing and proposed FGL is required for estimation of earth work for Land development. Please provide the level(s) - HFL, FGL & FFL? | Kindly refer Section Project. Contouring is in the scope of the bidder. HFL (Highest Flood Level) shall be arranged by the contractor. FGL shall be decided during detailed engineering. |
| 10. |  | Civil Works | Drainage System | Kindly confirm the distance of outfall for drainage system, if any. | The same shall be decided during detailed engineering. Bidder to quote as per the provisions of the tender documents. |
| 11. |  | Civil Works | Building Requirement | Kindly provide the STATCOM building minimum area & height requirement, if any. | Area & height of STATCOM building shall be decided during detailed engineering complying the requirement of technical specifications. |
| 12. |  | Civil Works | Building Requirement | The specific area requirement for rooms like Valve Hall, conference room, service room cum workshop, etc required, if any. | Please refer reply against query sl no11. |
| 13. |  | Civil Works | Factor of Safety | FOS for switchyard structure & STATCOM structure shall be 1.5 for normal condition and 1.2 for short circuit conditions. Please confirm. | Confirmed. |
| 14. |  | Civil Works | Transit Camp | Kindly confirm the staff quarter is required or not, if required, type and no. of dwelling unit required for each type along with the minimum area requirement of each type of units. | Staff quarters are not envisaged. Bidder to quote as per the provisions of the tender documents. |
| 15. |  | Civil Works | RCC M25 | The Grade of RCC shall be M25 for all foundation & super-structure work, Please confirm | Confirmed. |
| 16. |  | Civil Works | Dismantling | The quantity of dismantling work, if any, need to be clarified. | Bidder to quote as per the provisions of the tender documents. |
| 17. | 1 | General | General | Hitachi energy offered solutions of single 300MVAr branch has many advantages such as low losses------------------------------------------------------------------------------------------------------------- Hitachi Energy as OEM of semiconductor (IGBT) as well as the STATOM’s solutions provider are manufacturing the STATCOM valves which are modular in nature and any failed module does not require complete replacement of submodules/valves section. As per our files data the failure of IGBT cells is very low and the higher number of spare which are kept at inventory may not be used in the STATOCM life time. With respect to STATCOM projects executed globally, it is recommended to have 5-10% cells as spares. Therefore kindly request you to specify the spare requirement in terms of percentage which will provide the equal and fair opportunity/competition for all the bidders. | For spare requirement of valves kindly refer Sl. No. 113 clarifications-I (part-1 of 2) |