| Sn | Reference | Existing provisions | Amended Provisions |
| --- | --- | --- | --- |
| 1 | Volume-II, Technical Specifications Appendix-A Table A3 |  | POWERGRID region wise : Anticipated List of Links and Indicative OPGW requirements. Region; Description of requirements; Anticipated Length; Anticipated List of Links for OPGW implementation; Tentative delivery destination in region. NR1; (i) 24F OPGW (400kV & 765kV) (ii) 24F OPGW (800kV HVDC) (iii) 48F OPGW (220kV & below) (iv) 48F OPGW (400kV & 765kV) (v) 96F OPGW (220kV & below); 3km 3km 3km 3km 5km; Ballabhgarh. NR2 (Hilly); (i) 24F OPGW (400kV) (ii) 24F OPGW (220kV & below) (iii) 24F OPGW (OPGW dia 14.7mm, UTS-195.6kN) (iv)48F OPGW (220kV and below) (v) 48F OPGW (400kV and below) (vi) 96F OPGW (220kV and below); 3km 3km 6km 68km 182km 5km; (a)220kV Salal (NHPC)-Jammu (JKPTCL): 62km (b) 400kV Moga– Hissar: 209km (c) 400kV Hamirpur II-Jalandhar: 135km; Wagoora. NR3; (i) 24F OPGW (400kV & 765kV) (ii) 24F OPGW (220kV & below) (iii) 24F OPGW (800kV HVDC) (iv) 48F OPGW (400kV & 765kV) (v) 48F OPGW (220kV & below); 3km 3km 6km 563km 3km; (a)765kV S/c Fatehpur-Varanasi: 223km (b)765kV S/c Fatehpur-Sasaram: 356km (NR3 Portion approx. 276km); Fatehpur. WR1; (i) 24F OPGW (400kV & 765kV) (ii) 24F OPGW (220kV & below) (iii) 24F OPGW (River crossing- OPGW dia 14.7mm, UTS-195.6kN) (iv) 48F OPGW (220kV & below) (v) 48F OPGW (400kV & 765kV); 3km 3km 5km 3km 3km; Wardha. WR2; (i) 24F OPGW (400kV & 765kV) (ii) 24F OPGW (220kV & below) (iii) 48F OPGW (400kV & 765kV) (iv) 48F OPGW (220kV & below) (v) 96F OPGW (220kV & below) (vi) 24F OPGW (HVDC); 3km 3km 374km 3km 5km 3km; (a)765kV S/c (circuit-2) Satna-Gwalior: 340km; Dehgam. NER (Hilly); (i) 24F OPGW (400kV) (ii) 24F OPGW (220kV & below) (iii) 48F OPGW (220kV & below) (iv) 48F OPGW (400kV) (v) 96F OPGW(220kV & below); 3km 3km 219km 3km 5km; (a)132kV Kahilipara -Umtru- Umiam Stg. III – Umiam Stg.I -Umiam S/s – NEHU (including Umtru and 132kV Umiam S/s connectivity): 89.26km (b)132kV Sarusujai to Umtru line: 37km (c)132kV NEHU-Khliehriat ckt-1 (132 kV NEHU –NEIGRIHMS – Khliehriat line): 73km (d)Laying of 48F underground fiber optic (UGFO) cable from Tower 25 of 132 kV NEHU –Mawlyndep line to NERLDC Shillong: 3.5km (e)Laying of 48F underground fibre optic (UGFO) from NERLDC Guwahati to Gantry of Kahilipara: 2km; Khelrihat. SR1; (i) 24F OPGW (400kV & 765kV) (ii) 24F OPGW (220kV & below) (iii) 24F OPGW (River crossing- OPGW dia 14.7mm, UTS-195.6kN) (iii) 48F OPGW (400kV & above) (iv) 24F OPGW (HVDC); 3km 3km 5km 362km 3km; (a) 400kV Ramangundam-Warrangal: 98km (b) 400kV Warrangal-Khammam: 117km (c) 400kV Khammam-Vijaywada : 114km; Maheshwaram. SR2; (i) 24F OPGW (400kV & 765kV) (ii) 24F OPGW (220kV & below) (iii) 48F OPGW (400kV & 765kV); 3km 3km 3km; Yelanka. Odisha; (i) 24F OPGW (400kV & 765kV) (ii) 24F OPGW (220kV & below) (iii) 48F OPGW (400kV & above); 3km 3km 3km; Angul. ER1; (i) 24F OPGW (400kV & 765kV) (ii) 24F OPGW (220kV & below) (iii) 48F OPGW (400kV & 765kV); 3km 3km 88km; (a)765kV S/c Fatehpur-Sasaram: 356km (ER1 Portion approx. 80km); Gaya. ER2; (i) 24F OPGW (400kV & 765kV) (ii) 24F OPGW (220kV & below) (iii) 48F OPGW (400kV & 765kV); 3km 3km 3km; Rajarhat. Terrain Breakup:- Hilly= 500km & Plain= 1500km Fiber variant breakup:- 24F OPGW= 94km, 48F OPGW= 1886km & 96F OPGW=20km Cumulative Quantity=2000km. UGFO Pan-India; 48F UGFO; 10km; For connectivity of NERLDC in Guwahati, WRLDC in Mumbai and SRLDC in Bengaluru, however actual links may change based on requirements. Note:- The subject package covers pan-India supply, installation & commissioning of OPGW based fibre optic system. Tentative delivery destination is mentioned in region along with anticipated requirements for new links and O&M spares. However, actual locations & quantities as envisaged above may vary and will be intimated to contractor in post-award stage. Anticipated List of Links for implementation are mentioned above. Actual Links details for OPGW & UGFO implementation will be intimated during detailed engineering. |
| 2 | Bid Price Schedule (BPS)-2nd Envelope | Supply & Installation for 24F OPGW and 48F OPGW along with associated items. | Supply & Installation for 24F OPGW, 48F OPGW & 96F OPGW along with associated items. Revised BPS may be referred. |
| 3 | ITB 29, Section-III, BDS Volume-I of bidding documents | 29. e-Reverse Auction (e-RA) 29.1 The Employer reserves the right to conduct e-Reverse Auction (e-RA) for further reduction in the price. In case e-RA is conducted, same shall be done in the manner as indicated at Annexure-B(BDS). For the purpose of the aforesaid, the ‘Indicative Estimated Cost for e-RA’ is Rs. 69.08 Crore. | 29. e-Reverse Auction (e-RA) 29.1 The Employer reserves the right to conduct e-Reverse Auction (e-RA) for further reduction in the price. In case e-RA is conducted, same shall be done in the manner as indicated at Annexure-B(BDS). For the purpose of the aforesaid, the ‘Indicative Estimated Cost for e-RA’ is Rs. 89.90 Crore. |
| 4 | Annexure-A BDS Volume-I of bidding documents | Qualifying Requirement (QR) for Package OPGW-04: OPGW Supply & Installation Package for various transmission lines pan India locations under BULK IMPLMENTATION (Supply + Erection) for OPGW and Communication Equipment Specification Number: CC/NT/W-OPGW/DOM/A00/24/13348 ….. 2.0 FINANCIAL POSITION …. (b) Minimum Average Annual Turnover^(MAAT) of the bidder for best three years i.e. 36 months out of last five financial years of the bidder should be Rs. 441.300 million. (c) Bidder shall have Liquid Assets (LA) and/or evidence of access to or availability of credit facilities of not less than Rs. 73.550 million or equivalent. | Qualifying Requirement (QR) for Package OPGW-04: OPGW Supply & Installation Package for various transmission lines pan India locations under BULK IMPLMENTATION (Supply + Erection) for OPGW and Communication Equipment Specification Number: CC/NT/W-OPGW/DOM/A00/24/13348 ….. 2.0 FINANCIAL POSITION …. (b) Minimum Average Annual Turnover^(MAAT) of the bidder for best three years i.e. 36 months out of last five financial years of the bidder should be Rs. 574.275 million. (c) Bidder shall have Liquid Assets (LA) and/or evidence of access to or availability of credit facilities of not less than Rs. 95.713 million or equivalent. In view of the above: 04-Annexure-A (BDS) stands replaced with 04-Annexure-A (BDS)_rev01 (attached herewith), and Attachment 3(QR) stands replaced with Attachment 3(QR)_rev01 (attached herewith). |
| 5 | Section-2 Clause 2.1.3.2 | # OPGW Parameters to be considered for different line voltage and wind zones Transmission Line Voltage and wind zone; OPGW Cable Parameters. UTS (Kg); Area (sqmm); Wt. (Kg/m); Dia. (mm); Modulus of Elasticity (Kg/sqmm); Coeff. Of linear Expansion (per deg C); Central Fibre optic unit design. 765 kV S/C & D/C WZ 1-4 765kV S/C & D/C WZ 5 400kV M/C WZ 1-5 400kV S/C & D/C WZ 1-5; 9350± 150; 56.5± 2.5; 0.45± 0.01; 12 ± 0.2; 14290±110; 0.0000138± 0.0000003; Al tube. 765 kV WZ 5; 9098± 150; 57.5±2.5; 0.49 ± 0.01; 11.5 ± 0.2; 14114 ± 110; 0.0000136 ± 0.0000003; Stainless Steel Tube. 220 kV S/C & D/C WZ 1-4 132kV S/C & D/C WZ 1-5; 7376±50; 51±2; 0.355±.01; 11.4±.02; 12344±100; 0.0000149± 0.0000003; Al Tube. River Crossing Section; 20059±100; 118±5; 0.884±0.01; 14.7±0.2; 16355±100; 0.0000127± 0.0000003; Stainless Steel Tube. 800kV HVDC; 10369.0112; 72.66; 0.5719; 13.5; 13788.99; 0.00001404; Al tube. Or suitable to tower design; Or suitable to tower design. Special cable (For Ladakh WZ-6 with snow, 25mm snow in Arunachal Pradesh, high UTS special applications, etc); 15316 to 15300.72; 90.50 to 107; 0.715 to 0.750 (Mass tolerance of 2% ); 13.6 (tolerance of 3%); 15973.4 to 15989; 0.0000125; Stainless Steel Tube. For Al tube & Stainless steel tube design details refer clause 2.1.3.1 above.. | # OPGW Parameters to be considered for different line voltage and wind zones Transmission Line Voltage and wind zone; OPGW Cable Parameters. UTS (Kg); Area (sqmm); Wt. (Kg/m); Dia. (mm); Modulus of Elasticity (Kg/sqmm); Coeff. Of linear Expansion (per deg C); Central Fibre optic unit design. 765 kV S/C & D/C WZ 1-4 765kV S/C & D/C WZ 5 400kV M/C WZ 1-5 400kV S/C & D/C WZ 1-5; 9350± 150; 56.5± 2.5; 0.45± 0.01; 12 ± 0.2; 14290±110; 0.0000138± 0.0000003; Al tube*. 765 kV WZ 5; 9098± 150; 57.5±2.5; 0.49 ± 0.01; 11.5 ± 0.2; 14114 ± 110; 0.0000136 ± 0.0000003; Stainless Steel Tube. 220 kV S/C & D/C WZ 1-4 132kV S/C & D/C WZ 1-5; 7376±50; 51±2; 0.355±.01; 11.4±.02; 12344±100; 0.0000149± 0.0000003; Al Tube*. River Crossing Section; 20059±100; 118±5; 0.884±0.01; 14.7±0.2; 16355±100; 0.0000127± 0.0000003; Stainless Steel Tube. 800kV HVDC; 10369.0112; 72.66; 0.5719; 13.5; 13788.99; 0.00001404; Al tube. Or suitable to tower design; Or suitable to tower design. Special cable (For Ladakh WZ-6 with snow, 25mm snow in Arunachal Pradesh, high UTS special applications, etc); 15316 to 15300.72; 90.50 to 107; 0.715 to 0.750 (Mass tolerance of 2% ); 13.6 (tolerance of 3%); 15973.4 to 15989; 0.0000125; Stainless Steel Tube. *-Note: In case of 96Fiber OPGW, Stainless Steel tube is also acceptable. For Al tube & Stainless steel tube design details refer clause 2.1.3.1 above.. |
| 6 | Second Envelope Bid, Volume-III bidding document | # Existing File # “Price_Schedule OPGW_04” | # The existing File # “Price_Schedule OPGW_04” # Stand replaced as # “Price_Schedule OPGW_04_rev1” |