| SN | Clause No. | Provision in the Bidding Documents | Bidder’s Query/Comments | POWERGRID’S Reply/Clarification |
| --- | --- | --- | --- | --- |
| 1. | Sr.No.1 of Amendment No.3 (technical portion) dated 06.04.22 and Sch-1 of BPS-Rev-02 (TW03 & TW04) | Details of Conductor & Earthwire/OPGW | As per the Amendment no.3, the details of conductor & Earthwire clause was removed and in the sch-1 under tower supply the conductor type was mentioned as Hexa Zebra. Also under the conductor accessories the conductor type was mentioned as ACSR Zebra in PKG-TW03 and it was mentioned as ACSR/AAAC/AL59 Zebra in PKG-TW04. Kindly confirm the type of conductor to be used in both the packages. | ACSR Zebra conductor has envisaged for subject transmission line. All conductor accessories for ACSR Zebra conductor has provided in BPS of subject packages. T-Connector under package TW04 shall be of ACSR Zebra conductor. Please refer amendment. |
| 2. | Sr.No.3 of Amendment No.3 (technical portion) dated 06.04.22 | To take care of cyclonic wind loading, design of towers in coastal areas (wherever mentioned in BPS), shall be carried out considering design wind speed based on multiplying an additional factor K4 = 1.3 to the reference wind speed. The increased wind pressure so calculated, shall be applied to Tower structure only and normal wind as per IS:802 shall be applied on Conductor/Earthwire/OPGW/Insulator. | As per this clause, the increased wind pressure which is to be applied on tower body will be calculated as follows, Pd=0.6 Vd2 where Vd = VR.K1.K2.K4. Hope our understanding is correct. Kindly confirm? | Confirmed |
| 3. | BPS - Sch-3 - Foundation Works-TW03 & TW04 | "Design & Installation of DFR foundation…." and "Design & Installation of PS foundation with soil properties of Maharashtra …." | For some of the foundations in TW04 it was asked to consider the soil properties of Maharashtra and for the other foundations there is no mention about the soil properties. Kindly confirm whether Gujarat soil properties is to be considered for foundation design in both the packages where there is no specific mention about the soil properties in Sch-3 of BPS. | Transmission line under Package TW04 is passing through Maharashtra region. All the soil properties for Maharashtra state as stipulated in Technical specification to be considered for design of foundation. |

****************