| Sl. No. | Clause ref | Existing clause | Queries asked by the bidder | POWERGRID’s clarification |
| --- | --- | --- | --- | --- |
|  | Clause No. 1.4.10, Section-IV A “Tower Design”, Technical Specifications |  | Maximum temperature 85°C provided for ACSR / AL59 / AAAC conductor. No information provided regarding AACSR conductor. We understand that for AACSR Zebra conductor maximum temperature to be considered is 85° C. Please confirm. | For AACSR Zebra conductor also, maximum temperature to be considered is 85° C. Refer Amendment No. 1 (technical portion) to the Bidding Documents attached herewith. |
|  | Technical Specifications |  | Please provide the values of Young’s Modulus (E) and Coefficient of Expansion (α) for AACSR Zebra conductor. | Refer Amendment No. 1 (technical portion) to the Bidding Documents attached herewith. |
|  | Clause No. 2.4.1, Section-IA A, Technical Specifications | One AACSR Earthwire and one OPGW with mechanical & electrical properties equivalent to the used AACSR earthwire. | As per Technical Specifications Section 1-A, Clause 2.4.1, Page 7 of 9 mentioned that AACSR Earth wire is to be used in the line. The diameter of AACSR earth wire is more than 15.8 mm. Therefore, as per CBIP manual referred, we understand that the drag coefficient is to be considered 1. Please confirm | As per IS 802 2015, Drag coefficient for groundwire/OPGW is 1.2. |
|  | Cl. No 1.6.5.10 Table 2.1 of Sec-IV D– Technical specification |  | Soil properties for NDS soil as given in the table is bearing capacity 50000 kg/m2 for Maharashtra region. We request you to confirm bearing capacity for soil in dry condition for Maharashtra region. | Confirmed. Soil properties for Normal Dry soil shall be bearing capacity 50000 kg/m2 for Maharashtra region, refer Cl. No 1.6.5.10 Table 2.1 of Sec-IV D of Technical specification, |
|  |  |  | We understand that the said transmission lines pass through coastal region as also mentioned in Price Schedule. Kindly confirm whether galvanizing of 900 gm/sqmm is required for tower parts and whether epoxy coated reinforcement steel shall be used in the said lines since the same is not mentioned in price schedules. | Confirmed. Pl. refer Cl.1.6.1 of Sec-IVC for galvanizing of tower parts & Cl. 1.7.12 of Sec-IVD for use of epoxy coated reinforcement steel in coastal region. |
|  | Technical Specifications |  | We understand from the Tender documents that supply of AACSR Zebra is in the scope of Client and scope of design of Tower parts is in the scope of Bidder. In view of the same, please provide modulas of elasticity & coefficient of thermal expansion of said Conductor required for design purpose. | Refer Amendment No. 1 (technical portion) to the Bidding Documents attached herewith. |
|  | Clause No. 1.4.9, Section-IVA A, Technical Specifications | Tower Loading Conditions: The design of towers shall be carried out by the Contractor as per IS 802 (Part 1/section-1)2015* except for drag coefficients which shall be as per IS 802 (Part 1/section-1) 1995 and considering Wind Zone as per Section-I of the TS. | As per IS 802 2015 P1S1 , the drag factor for GW is to be taken as 1.2, however referring to CBIP manual 523, the drag coefficient of EW varies with change in diameter. As per Diameter of AACSR EW (18.12 mm), the drag coefficient shall to be taken as 1 as per CBIP. The wind pressure on EW with drag factor 1.2 shall come as 384 kg/sqm, and with drag factor 1, it shall come as 320 kg/sqm. Please confirm the drag factor to be considered for design purpose | Refer Clarification at Sl. No. 3. |
|  | Price Schedules |  | In both the Packages TW03 & TW04, please refer to Supply Schedule 1 wherein description for stubs for raised chimney locations is not mentioned however, we understand that Raised Chimney locations are present in both the Packages as observed in Schedule 3 of Price Schedule. Request you to kindly mention quantities for tower and stub locations in Raised chimney locations separately in Schedule 1 and also kindly mention spare towers if mentioned in the said Price Schedules | Refer Amendment No. 1 (technical portion) to the Bidding Documents attached herewith. |
|  | Cl. No. :1.4.9 (f) & (b), Sec-IVA, Technical specification | For towers in coastal areas (wherever mentioned in BPS), an additional factor viz.K4:1.3 shall be considered for design of towers to take care of cyclonic wind conditions . Terrain category shall be considered as 2, unless otherwise mentioned in Section-1A. | For towers in coastal areas (wherever mentioned in BPS), an additional factor viz.K4:1.3 shall be considered for design of towers to take care of cyclonic wind conditions . Terrain category to consider as 2. But as per price schedule, towers are located in plain terrain in coastal region. Please confirm factor K4 =1.3 needed to be considered for this project. As per IS 802-part-1-sec-1-2015, Design wind speed: Vd= Kl*K2*VR. Please confirm with factor K4, formula for Design wind speed is: Vd=K1*K2*K4*VR. | As the transmission line passes throgh coastal region, factor K4 =1.3 needed to be considered for this project in line with Cl. 1.4.9-Sec-IVA of technical specification. Designed wind speed shall be: Vd=K1*K2*K4*VR. |
|  | Price Schedule |  | As per price schedule Extensions to be designed as leg extensions and all the leg extensions (0m/+3m/ +6m/ +9m/ +12m/ +15m) to be attached from basic body level. Please confirm that 0m & +3m leg extensions can be attached from basic body level, whereas +6/ +9/ +12/ +15m leg extensions can be attached from 0m (normal tower level). | Leg extension wise quantity required for package TW04 only. Refer Amendment No. 1 (technical portion) to the Bidding Documents attached herewith. Bidders may refer BPS and Cl. 2.4.2.3 of Sec-IA (refer amendment) for quoting prices. In the BPS, bidders are required to quote prices for leg extensions which shall include all panel(s)/parts of common plan for one quadrant of tower other than that at basic level, required to be connected from basic body level. Further, bidders may refer Sl No. 17 wherein it is mentioned that the leg scheme attached in Drawing section, is for indicative purpose only. Bidders are permitted to offer leg extension combination suiting to their proposed design. |
|  | Clause No. 2.4.1, Section-IA, Technical Specifications | Six AACSR ZEBRA conductor per phase with sub-conductor spacing of 457 mm in vertical configuration. One AACSR Earthwire and one OPGW with mechanical & electrical properties equivalent to the used AACSR earthwire. | Please provide the value of coefficient of linear expansion and modulus of elasticity for conductor and property for AACSR earth wire and properties OPGW of equivalent to AACSR earth wire. | Refer Amendment No. 1 (technical portion) to the Bidding Documents attached herewith. |
|  | Clause No. 1.2.1, 1.2.2 Section-IVA , Technical Specifications | Further, in addition to above, D/DD/QD towers shall also be suitable for adding +30m/+35m body truncations/ extensions/ leg extensions without reducing the factor of safety (actual stress / allowable stress) available for the members of tested extensions to the extent possible | Understand from the mentioned clause that DD+30m & DD+35m body extension towers are to be designed with reduced span of not less than 250m without reducing the factor of safety(actual stress / allowable stress) available for the members of tested extensions to the extent possible. Inorder to meet the above conditionwe need to reduce the deviation angle of DD tower. Kindly confirm is there any restriction regarding the reduced angle of deviation as same as that of span? If it so, kindly provide the values. Also, for these higher extension (+30/+35m) towers the base width will be very high if we extend the same base from normal tower. Moreover if these towers are used in hilly terrain, there will be huge reguirement of space for erecting of towers. Considering this condition, whether it is allowed to design this DD+30/DD+35m by adopting new tower configuration of DD tower (reduced base width) below waist level with increased factor of safety (for the members of the tower below waist level). Kindly confirm & also if it is allowed, kindly mention the increased FOS to be kept for the tower members. | As per Cl. 1.2.2 of Sec-IVA, DD+30m & DD+35m body extension towers are to be designed with reduced span of not less than 250m. Maximum reduction of 100 in deviation angle of DD type tower is permissible to achieve above condition. If the bidder proposes to design of DD+30/DD+35m as a new tower configuration of DD tower e.g. reduced base width below waist level etc., all the provisions of testing as stipulated in sec-IVB shall be applicable. Further, if not tested, towers shall be designed with reliability level-3. |
|  | Price Schedule-I |  | Understand that in price schedule, for body extensions/leg extensions the contractor needs to quote the rate for one corner only. However for the stubs & Raised chimney stubs it was not clearly mentioned whether the quantities mentioned are for one corner or for four corners. Kindly clarify. Also if it is for one corner, kindly indicate the same in price schedule. | Leg extension wise quantity required for package TW04 only, wherein individual stub/leg for one corner needs to be quoted. Refer Amendment No. 1 (technical portion) to the Bidding Documents attached herewith. |
|  | Price Schedule-I |  | We understand that the conductor is a free-issue material by PGCIL to the contractor. Conductor GTP is required to start the tower design work. Standard GTP is provided alongwith Tender Technical Specification. However, AACSR Zebra conductor's Young’s modulus of elasticity and coefficient of linear expansion is not provided in the Standard GTP. Kindly arrange to share the complete GTP of AACSR Zebra Conductor. | Refer Amendment No. 1 (technical portion) to the Bidding Documents attached herewith. |
|  | Vol-II/Sec-IA/clause no. 2.4/. Vol-I/Price schedule/Sch1 (Tower Supply). | Special requirements. | As per the clause 2.4 & price schedule, we understand that the line is passing through Coastal areas. Tower foundation-design mix concrete of M30 Grade conforming to IS456 and Epoxy coated reinforcement conforming to IS:13620 shall be used. Kindly confirm. | Confirmed. Pl. refer Cl. 1.7.12 of Sec-IVD for use of design mix concrete of M30 Grade and epoxy coated reinforcement steel in coastal region. |
|  | Vol-II/Sec-IA/clause no. 2.4/. Vol-I/Price schedule/Sch1 (Tower Supply). | Special requirements. | As per the clause 2.4 & price schedule, we understand that the line is passing through Coastal areas. Zinc coating to be done for the fabricated tower parts and stubs with minimum overall zinc coating of 900gm/sqm of surface area except for plates and section below 5mm which shall have minimum overall zinc coating of 610gm/sqm of surface area. Kindly confirm. | Confirmed. Pl. refer Cl.1.6.1 of Sec-IVC for galvanizing of tower parts & stubs in coastal region. |
|  | Volume-II_part11 11_Section XI Drawing_part3 | Extension application scheme | Do we have to follow the Extension scheme provided in the Technical Specification or can we use other alternate extension scheme | Leg extension scheme provided in Drawing section of TS is for indicative purpose. Bidder may provide extension schemes as per provisions of technical specification. |
|  | 07_1 Section VII A Conductor, Rev-2(Jan'2022) of Volume-II_part3 _ | Conductor and Earthwire Specifications | Co-efficient of Thermal Expansion & Modulus of Elasticity values of Conductor & Earthwire is required. | Refer Amendment No. 1 (technical portion) to the Bidding Documents attached herewith. |
|  | Price Schedule |  | In Price bid, fthedule-1, Tower types available for DA, DB, DC, DD45, DD60 Whereas in Schedule-3, Foundation types available for Tower DA, DB1, DB2, DC-1, DC2, DD45, DD60. Kindly confirm the types of Tower. | Towers shall be designed as per table stipulated in Cl. 2.2.1 of Sec-I of Technical specification. For DB & DC type towers, separate foundation quantities (wherever applicable) are indicated in BPS for following categories based on angle of line deviation: DB1- 0 to 7 deg, DB2- 7 to 15 deg, DC1- 15 to 22 deg, DC2- 22 to 30 deg. Further, foundations shall be designed separately for different categories of towers based on applicable design loads. |
|  | Price Schedule |  | In Price Bid, Schedule-l and Schedule-3, we assume that the quantity of Stub are mentioned of Leg extension quantity, but the same are not mentioned in Item description, Please confirm. | Leg extension wise quantity required for package TW04 only, wherein individual stub/leg for one corner needs to be quoted. Refer Amendment No. 1 (technical portion) to the Bidding Documents attached herewith. |
|  | Technical Specifications |  | Kindly provide Technical Specification & GTP for AACSR Conductor and Earthwire along with diameter, sectional area, unit weight, UTS, Modulus of elasticity, Coefficient of linear expansion as the same is required for tower design purpose and as wells for getting competitive offers from vendors for hardware items. | Refer Amendment No. 1 (technical portion) to the Bidding Documents attached herewith for Modulus of elasticity & Coefficient of linear expansion for AACSR ZEBRA & AACSR Earthwire. For other details pls refer Section-VIIA of technical specification. |
|  | Volume-II_part11 11_Section XI Drawing |  | Also kindly provide Insulator hardware dimensions. | Please refer Volume-II_part11 Section XI Drawing of technical specification. |
|  | Clause No. 2.4.1, Section-IA, Technical Specifications |  | We understand the entire line is passing through Wind Zone_3. please confirm. | Confirmed. |
|  | Clause No. 2.1.3.2 of OPGW technical specification |  | Please refer to Clause No. 2.1.3.2 of OPGW technical specification wherein OPGW parameters are provided in table for 765 KV lines from Wind Zone 1 to 4. However as mentioned in scope (Section IA) that electrical and mechanical properties of OPGW shall be equivalent to offered AACSR Earthwire. If the same is to be honoured then the parameters provided in technical specs is not getting fulfilled and in such a case new design is to be developed. Kindly confirm which is to be followed amongst parameters mentioned in technical specification and that of scope where equivalent to AACSR Earthwire is asked to be adhered to. | Standard OPGW design parameters mentioned for River Crossing Section at clause 2.1.3.2 of Section-X of OPGW TS has comparable parameters to AACSR Earthwire which is irrespective of voltage & wind zone of transmission line. OPGW electrical & mechanical requirements are further brought out at Table 2.2(a) of clause 2.1.3.4 of Section-X. Bidder to comply the TS. |
|  | Cl. 2.4.1 (i) (a) of Sec-IA & Cl.1.2 of Sec-X | One OPGW with mechanical & electrical properties equivalent to the used AACSR earthwire. It should be noted that parameters for OPGW cable design has been specified in the tender. The Contractor shall offer the product meeting the design accordingly. | As per the mentioned clause in Sec IA & Sec-X, it was understood that the OPGW should have the equivalent mechanical properties as that of AACSR earthwire & the vendor offered OPGW should in line with the Standard parameters mentioned in the technical specification. However, in Sec-X, Cl 2.1.3.2, Page 8 of 14, OPGW cable parameters had been provided but the mechanical parameters are not equivalent to AACSR Earthwire. Request you to kindly provide the OPGW parameters to be considered for this packages (TW03 & TW04) and also mention about central fibre optic design, i.e. Al tube or Stainless steel tube. | Bidder may kindly refer other provisions of clause 1.2 of Section-X. “The Bidder's proposal shall address all functional and performance requirements within this specification and shall include sufficient information and supporting documentation in order to determine compliance with this specification without further necessity for inquiries.” As already clarified above, Standard OPGW design parameters for River Crossing Section mentioned at clause 2.1.3.2 may be meeting the requirements envisaged in Section-IA of TS. Bidder to comply the TS. |
|  | general |  | Please confirm whether galvanization of Tower parts shall be with 900 gsm/sqm for estimation purpose for both the packages since the same is not explicitly mentioned in BPS | Refer Clarification at Sl. No. 5 |
|  | Section-IVA Clause1.4.9 Tower Loading condition | 1.4.9 - Tower Loading condition. | The query is regarding Wind on Tower. As per Clause 9.1 WIND ON TOWER of IS 802-part 1-sec 1 -2015 For Oblique Wind on Tower, the component of Fwt in Transverse Direction is given by, Fwt,Trans = Pd* (1 + 0.2 sin²2θ) (AeT*CdtT*sinθ) GT and Longitduinal direction is given by, Fwt LONGI = Pd *(1 + 0.2 sin²2θ) (AeL*CdtL*cosθ) GT. The factor of (1 + 0.2 sin²2θ) * cosθ & (1 + 0.2 sin²2θ) * sin θ for 30o oblique wind works out be 0.995 (in Trans direction) and 0.575 (in Long direction) respectively. Similary, the factor of (1 + 0.2 sin²2θ) * cosθ & (1 + 0.2 sin²2θ) * sin θ for 45o oblique wind works out be 0.8485 (in Trans direction) and 0.8485 (in Long direction) respectively. However, as per IEC 80626 and other International standards like EN50341, these components are used as Pd* (1 + 0.2 sin²2θ) (AeT*CdtT*Cos2θ) GT in Transverse direction & Pd* (1 + 0.2 sin²2θ) (AeT*CdtT*Sin2θ) GT in Long Direction. The factor (1 + 0.2 sin²2θ*Cos2θ) works out be 0.8625 in Trans direction & factor (1 + 0.2 sin²2θ*Sin2θ) works out be 0.2875 in Long direction. Silimary for 45o Oblique wind, these factors are 0.6 respectively. These are correct factors to be used in oblique Wind condition. Factor as per IS802; IEC 80626 /EN50341. Trans; Long; Trans; Long. 30 deg OW; 0.995; 0.575; 0.8625; 0.2875. 45 deg OW; 0.8485; 0.8485; 0.6; 0.6. Kindly confirm which factors to be used in Oblique wind condition for design of towers. | Wind Load on Tower shall be calculated as per following formula:- Fwt,Trans = Pd* (1 + 0.2 sin²2θ) (AeT*CdtT*cosθ)*GT Fwt Long = Pd *(1 + 0.2 sin²2θ) (AeL*CdtL*sinθ)*GT |
| 28 | Volume II / Section IA/ Clause 2.2.1- Classification of towers/ Page : 10 |  | Kindly confirm whether to consider DD45 (30-45d) tower as medium angle tower or large angle tower so as to decide whether to consider 2 wire or 3 wire broken for security condition. | As per Cl 6.1b) of IS 802 (Part 1/ Sec 1):2015, towers with angle 30-60 deg are classified as large angle towers. |
| 29 | Volume-II /Section XI/ Extension application scheme | Tower Typical drawing | Kindly confirm whether it is mandatory to follow extension application scheme or any other extension scheme can be adopted provided that it fulfills all leg extensions requirements. | Leg extension scheme provided in Drawing section of TS is for indicative purpose. Bidder may provide extension schemes as per provisions of technical specification. |
| 30 | Volume-II_part5,6,7,8 | OPGW Specifications | OPGW – Maximum % age of utilization under full wind condition 40% may not be possible for maintain the parallel factor (Sag of OPGW at 0 deg) | As per Section-X sub-section 2.1.2.3 “The Max Allowable Tension shall also be less than or equal to 0.45 times the UTS.” Bidder to comply the technical specification accordingly. |

************