## Total Estimated cost
BILL OF QUANTITIES(BOQ)-FOR REFERENCE ONLY
SUBJECT:Construction of RCC revetment wall for protection of 05 nos towers (L-82 & 83 of 400 kV D/C Meerut-Mandola Ckt-1 & 2, L-35 of 400 kV S/C Dadri-Panipat Ckt-1, L-98 of 400 kV S/C Dadri-Kaithal and Location-363 of 765 kV S/C Bhiwani- Meerut under Meerut TLM
Sl. No. | Ref of DSR 2023 Item No. | Particulars of Items | Unit | L-363 Qty | L 98 Qty | L 161 Qty | L 82 Qty | Total Qty | Rate in Rs. | Amount (Rs.)
1 | 2.1.1 | Earth work in surface excavation not exceeding 30 cm in depth but exceeding 1.5 m in width as well as 10 sqm on plan including getting out and disposal of excavated earth upto 50 m and lift upto 1.5 m, as directed by Engineer-in- Charge: All kinds of soil | sqm | 0 | 0 | 0 | 0 | 100 | Bidders hall be quoted on SRM portal
2 | 2.6.1 | Earth work in excavation by mechanical means (Hydraulic excavator)/manual means over areas (exceeding 30 cm in depth, 1.5 m in width as well as 10 sqm on plan) including getting out and disposal of excavated earth lead upto 50 m and lift upto 1.5 m, as directed by Engineer-in-charge. All kinds of soil | Cum | 485 | 110 | 185 | 116.325 | 896
3 | 2.26.1 | Extra for every additional lift of 1.5 m or part thereof in excavation / banking excavated or stacked materials. All kind of soil. | cum | 21 | 0 | 0 | 0 | 21
4 | 2.25 | Filling available excavated earth (excluding rock) in trenches, plinth, sides of foundations etc. in layers not exceeding 20cm in depth, consolidating each deposited layer by ramming and watering, lead up to 50 m and lift upto 1.5 m. | cum | 485 | 110 | 185 | 116.325 | 896
5 | 2.25 (a) | Excavating, supplying and filling of local earth (including royalty) by mechanical transport upto a lead of 5km also including ramming and watering of the earth in layers not exceeding 20 cm in trenches, plinth, sides of foundation etc. complete. | cum | 225 | 135 | 60 | 0 | 420
6 | 4.1.8 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering - All work up to plinth level :1:4:8 (1 Cement : 4 coarse sand (zone-III) : 8 graded stone aggregate 40 mm nominal size) | Cum | 23 | 6 | 10 | 7.425 | 46
7 | 5.1.2 | Providing and laying in position specified grade of reinforced cement concrete, excluding the cost of centering, shuttering, finishing and reinforcement - All work up to plinth level :1:1.5:3 (1 cement : 1.5 coarse sand (zone-III): 3 graded stone aggregate 20 mm nominal size) | Cum | 137 | 31 | 52 | 53.46 | 273
8 | 5.2.2 | Reinforced cement concrete work in walls (any thickness), including attached pilasters, buttresses, plinth and string courses, fillets, columns, pillars, piers, abutments, posts and struts etc. above plinth level up to floor five level, excluding cost of centering, shuttering, finishing and reinforcement :1:1.5:3 (1 cement : 1.5 coarse sand(zone-III) : 3 graded stone aggregate 20 mm nominal size) | Cum | 148 | 15 | 34 | 31.68 | 229
9 | 5.9.1 | Centering and shuttering including strutting, propping etc. and removal of form for :Foundations, footings, bases of columns, etc. for mass concrete | SqM | 437 | 85 | 145 | 125.4 | 790
10 | 5.9.2 | Centering and shuttering including strutting, propping etc. and removal of form for :Walls (any thickness) including attached pilasters, butteresses, plinth and string courses etc. | SqM | 900 | 150 | 315 | 343.2 | 1710
11 | 5.22.6 or 5.22A.6 | Steel reinforcement for R.C.C. work including straightening, cutting, bending, placing in position and binding all complete at all level.Thermo-Mechanically Treated bars of grade Fe-500D or more. | Kg | 23600 | 2650 | 4500 | 4680 | 40000
NON Schedule Items
12 |  | Providing and laying of filter media (53mm to 22.4mm size stone aggregate) confined in GI(hot dip galvanised- galvanizing/ zinc coating not less than 270g/Sq.m.) welded wire mesh (of average width of aperture 15mm and nominal dia of wire 1.6mm conforming to IS:4948(Latest)) of approximately 500mm size cuboid(typical) with edges(at junction of two faces) of cuboid strengthened with MS flat 15x3mm or Angle section 15x15x3 including labours, materials at all levels complete in all respect. (Unit in Each)- | Each | 86 | 30 | 50 | 44 | 210
13 |  | Providing and fixing of PVC Single socketed pipe of approved make of 110mm outer dia of class 3 (Working pressure 6 Kg/ Sq.Cm.) conforming to IS - 13592 at all levels for all types of masonry work(as weep holes) complete in all respect- | RM | 26 | 9 | 15 | 14 | 64
Grand Total Estimated cost excl. GST
Grand Total Estimated cost incl. GST

## Abtract of L363 (hidden)
Cost Estimate- RCC Retaining wall: Tower no. 363 of 765 kV Drg. Ref No.:
Sl. No. | Ref of DSR 2021 Item No. | Particulars of Items | Unit | Qty | Rate in Rs. | Amount (Rs.)
1 | 2.6.1 | Earth work in excavation by mechanical means (Hydraulic excavator)/manual means over areas (exceeding 30 cm in depth, 1.5 m in width as well as 10 sqm on plan) including getting out and disposal of excavated earth lead upto 50 m and lift upto 1.5 m, as directed by Engineer-in-charge. All kinds of soil | Cum | 485 | 177.5 | 86087.5
2 | 2.26.1 | Extra for every additional lift of 1.5 m or part thereof in excavation / banking excavated or stacked materials. All kind of soil. | cum | 21 | 126.8 | 2662.8
3 | 2.25 | Filling available excavated earth (excluding rock) in trenches, plinth, sides of foundations etc. in layers not exceeding 20cm in depth, consolidating each deposited layer by ramming and watering, lead up to 50 m and lift upto 1.5 m. | cum | 485 | 196 | 95060
4 | 2.25 (a) | Excavating, supplying and filling of local earth (including royalty) by mechanical transport upto a lead of 5km also including ramming and watering of the earth in layers not exceeding 20 cm in trenches, plinth, sides of foundation etc. complete. | cum | 225 | 700.5 | 157612.5
5 | 4.1.8 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering - All work up to plinth level :1:4:8 (1 Cement : 4 coarse sand (zone-III) : 8 graded stone aggregate 40 mm nominal size) | Cum | 23 | 6812 | 156676
6 | 5.1.2 | Providing and laying in position specified grade of reinforced cement concrete, excluding the cost of centering, shuttering, finishing and reinforcement - All work up to plinth level :1:1.5:3 (1 cement : 1.5 coarse sand (zone-III): 3 graded stone aggregate 20 mm nominal size) | Cum | 137 | 9045.75 | 1239267.75
7 | 5.2.2 | Reinforced cement concrete work in walls (any thickness), including attached pilasters, buttresses, plinth and string courses, fillets, columns, pillars, piers, abutments, posts and struts etc. above plinth level up to floor five level, excluding cost of centering, shuttering, finishing and reinforcement :1:1.5:3 (1 cement : 1.5 coarse sand(zone-III) : 3 graded stone aggregate 20 mm nominal size) | Cum | 148 | 10852.95 | 1606236.6
8 | 5.9.1 | Centering and shuttering including strutting, propping etc. and removal of form for :Foundations, footings, bases of columns, etc. for mass concrete | SqM | 437 | 392.15 | 171369.55
9 | 5.9.2 | Centering and shuttering including strutting, propping etc. and removal of form for :Walls (any thickness) including attached pilasters, butteresses, plinth and string courses etc. | SqM | 900 | 842.5 | 758250
10 | 5.22.6 or 5.22A.6 | Steel reinforcement for R.C.C. work including straightening, cutting, bending, placing in position and binding all complete at all level.Thermo-Mechanically Treated bars of grade Fe-500D or more. | Kg | 23600 | 107.85 | 2545260
Total | [5 empty] | 6818483
NON Schedule Items
11 | NS | Providing and laying of filter media (53mm to 22.4mm size stone aggregate) along retaining wall. | cum | 86 | 2200 | 189200 | For rate justification quotation Attached
12 | NS | Providing and fixing of uPVC Single socketed pipe of approved make of 110mm outer dia of class 3 (Working pressure 6 Kg/ Sq.Cm.) conforming to IS - 13592 at all levels for all types of masonry work(as weep holes) complete in all respect | meter | 25.8 | 1200 | 30960
Total for NS items | [5 empty] | 220160
Total for NS items Including GST @ 18% | [5 empty] | 259789
Grand Total Estimated cost | [5 empty] | 7078272

## 363 Cost Estimate (hidden)
Cost Estimate- RCC Retaining wall: Tower no.363 of 765kV Drg. Ref No.:
S.N. | Ref of DSR 2023 Item No. | Particulars of Items | Unit | Nos | Length | Width | Height | Qty | Rate in Rs. | Amount (Rs.)
1 | 2.6.1 | Earth work in excavation by mechanical means (Hydraulic excavator)/manual means over areas (exceeding 30 cm in depth, 1.5 m in width as well as 10 sqm on plan) including getting out and disposal of excavated earth lead upto 50 m and lift upto 1.5 m, as directed by Engineer-in-charge. All kinds of soil | Cum
|  | For Wall below footing wall height 4m |  | 1 | 64.2 | 1.15 | 0.5 | 36.915
|  | For footing wall height 4m |  | 1 | 64.2 | 3.15 | 1.275 | 257.8432
|  | For Wall below footing Wall height 3m |  | 1 | 64.2 | 1.05 | 0.5 | 33.705
|  | For footing Wall height 3m |  | 1 | 64.2 | 2.45 | 0.975 | 153.3578
481.821
|  | Total Quantity | Cum |  |  |  | Say | 485 | 177.5 | 86087.5
2 | 2.26.1 | Extra for every additional lift of 1.5 m or part thereof in excavation / banking excavated or stacked materials. All kind of soil.
|  | extra for excavation below 1.5m for wall height 4m |  | 1 | 64.2 | 1.15 | 0.275 | 20.3033
|  | Total Quantity | Cum |  |  |  | Say | 21 | 126.8 | 2662.8
3 | 2.25 | Filling available excavated earth (excluding rock) in trenches, plinth, sides of foundations etc. in layers not exceeding 20cm in depth, consolidating each deposited layer by ramming and watering, lead up to 50 m and lift upto 1.5 m.
|  | Total Excavation Lum Sum | [5 empty] | 485
|  | Total Quantity | cum |  |  |  | Say | 485 | 196 | 95060
4 | 2.25 (a) | Excavating, supplying and filling of local earth (including royalty) by mechanical transport upto a lead of 5km also including ramming and watering of the earth in layers not exceeding 20 cm in trenches, plinth, sides of foundation etc. complete.
|  | Filling inside of wall Lum sum |  | 1 | 128.4 | 0.5 | 3.5 | 224.7
|  | Total Quantity | cum |  |  |  | Say | 225 | 700.5 | 157612.5
5 | 4.1.8 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering - All work up to plinth level :1:4:8 (1 Cement : 4 coarse sand (zone-III) : 8 graded stone aggregate 40 mm nominal size) | Cum
|  | For Wall below footing for wall footing 4m |  | 1 | 64.2 | 0.55 | 0.075 | 2.6482
|  | For footing for wall footing 4m |  | 1 | 64.2 | 2.15 | 0.075 | 10.3523
|  | For Wall below footing for wall footing 3m |  | 1 | 64.2 | 0.45 | 0.075 | 2.1667
|  | For footing for wall footing 3m |  | 1 | 64.2 | 1.55 | 0.075 | 7.4632
22.6305
|  | Total Quantity | Cum |  |  |  |  | 23 | 6812 | 156676
6 | 5.1.2 | Providing and laying in position specified grade of reinforced cement concrete, excluding the cost of centering, shuttering, finishing and reinforcement - All work up to plinth level :1:1.5:3 (1 cement : 1.5 coarse sand (zone-III): 3 graded stone aggregate 20 mm nominal size)
|  | For Wall below footing 4m |  | 1 | 64.4 | 0.4 | 0.5 | 12.88
|  | For footing 4m |  | 1 | 64.4 | 2.4 | 0.3 | 46.368
|  | wall from footing top to GL 4m |  | 1 | 64.4 | 0.4 | 0.9 | 23.184
|  | For Wall below footing 3m |  | 1 | 64.4 | 0.3 | 0.5 | 9.66
|  | For footing 3m |  | 1 | 64.4 | 1.7 | 0.3 | 32.844
|  | wall from footing top to GL 3m |  | 1 | 64.4 | 0.3 | 0.6 | 11.592
136.528
|  | Total Quantity | Cum |  |  |  | Say | 137 | 9045.75 | 1239267.75
7 | 5.2.2 | Reinforced cement concrete work in walls (any thickness), including attached pilasters, buttresses, plinth and string courses, fillets, columns, pillars, piers, abutments, posts and struts etc. above plinth level up to floor five level, excluding cost of centering, shuttering, finishing and reinforcement :1:1.5:3 (1 cement : 1.5 coarse sand(zone-III) : 3 graded stone aggregate 20 mm nominal size)
|  | wall from above GL 4m |  | 1 | 64.2 | 0.35 | 4 | 89.88
|  | wall from above GL 3m |  | 1 | 64.2 | 0.3 | 3 | 57.78 |  |  | 285 | 228
147.66
|  | Total Quantity | Cum |  |  |  | Say | 148 | 10852.95 | 1606236.6
8 | 5.9.1 | Centering and shuttering including strutting, propping etc. and removal of form for :Foundations, footings, bases of columns, etc. for mass concrete
|  | For Wall below footing (PCC) |  | 2 | 128.4 |  | 0.075 | 19.26
|  | For Wall below footing (RCC) |  | 2 | 128.4 |  | 0.5 | 128.4
|  | For footing (PCC) |  | 2 | 128.4 |  | 0.075 | 19.26
|  | For footing (RCC) |  | 2 | 128.4 |  | 0.3 | 77.04
|  | For wall RCC 4m |  | 2 | 64.2 |  | 0.9 | 115.56
|  | For wall RCC 3m |  | 2 | 64.2 |  | 0.6 | 77.04
436.56
|  | Total Quantity | SqM |  |  |  | Say | 437 | 392.15 | 171369.55
9 | 5.9.2 | Centering and shuttering including strutting, propping etc. and removal of form for :Walls (any thickness) including attached pilasters, butteresses, plinth and string courses etc.
|  | Wall from footing to top |  | 2 | 64.2 |  | 4 | 513.6
|  | Wall from footing to top |  | 2 | 64.2 |  | 3 | 385.2
898.8
|  | Total Quantity | SqM |  |  |  | Say | 900 | 842.5 | 758250
10 | 5.22.6 or 5.22A.6 | Steel reinforcement for R.C.C. work including straightening, cutting, bending, placing in position and binding all complete at all level.Thermo-Mechanically Treated bars of grade Fe-500D or more. |  |  |  | Wt/mtr
|  | Raft Top & Bottom main Bar 16mm@200c/c |  | 644 | 2.6 | 1.58 |  | 2645.552
|  | Raft Top & Bottom Binder 16mm @ 200c/c |  | 26 | 64.2 | 1.58 |  | 2637.336
|  | Over Lap(authorised) |  | 156 | 0.8 | 1.58 |  | 197.184
|  | Wall verticle main bar 16mm@150c/c (Inner Side & Outside) |  | 858 | 4.1 | 1.58 |  | 5558.124
|  | Wall verticle main bar 16mm@150c/c (Inner Side & Outside) |  | 430 | 1.6 | 1.58 |  | 1087.04
|  | Wall Binder 12mm@ 150C/C (inner side & Outer) |  | 76 | 64.2 | 0.889 |  | 4337.6088
|  | Over Lap(authorised) |  | 456 | 0.6 | 0.889 |  | 243.2304
|  | Raft Top & Bottom main Bar 10mm@200c/c |  | 644 | 1.9 | 0.617 |  | 754.9612
|  | Raft Top & Bottom Binder 10mm @ 200c/c |  | 18 | 64.2 | 0.617 |  | 713.0052
|  | Over Lap(authorised) |  | 108 | 0.5 | 0.617 |  | 33.318
|  | Wall verticle main bar 12mm@150c/c (Inner Side & Outside) |  | 858 | 4.5 | 0.889 |  | 3432.429
|  | Wall Binder 10mm@ 200C/C (inner side & Outer) |  | 46 | 64.2 | 0.617 |  | 1822.1244
|  | Over Lap(authorised) |  | 276 | 0.5 | 0.617 |  | 85.146
23547.059
|  | Total Quantity | Kg |  |  |  | Say | 23600 | 107.85 | 2545260 |  |  | 86
11 | NS | Providing and laying of filter media (53mm to 22.4mm size stone aggregate) along retaining wall.
|  |  |  | 1 | 86
|  | Total Quantity | cum |  |  |  | Say | 86 | 2200 | 189200
12 | NS | Providing and fixing of uPVC Single socketed pipe of approved make of 110mm outer dia of class 3 (Working pressure 6 Kg/ Sq.Cm.) conforming to IS - 13592 at all levels for all types of masonry work(as weep holes) complete in all respect
|  | Total Qty. | meter | 86 | 0.3 |  |  | 25.8 | 1200 | 30960
|  | Total Estimated cost as per DSR'2023 | [7 empty] | 7038642.7
|  | GST @18 % on NS Items | [7 empty] | 39628.8
|  | Grand Total Estimated cost | [7 empty] | 7078271.5

## Protection Plan of L363 (hidden)
Details of SCHEME FOR PROTECTION OF FOUNDATION OF TOWERS FROM SOIL CUTTING
| Name of Transmission Line :- | Tower no.363 of 765 kV Drg. Ref No.:
Drg. Ref No.:
[5 empty] | Calculation of Revetment wall length | L(mm) | L(mm)
Tower No-363,Tower Type-C+3 ,RCC Wall -4 side
[5 empty] | M =Distance between outer of adjecent pit | 20800 | 20800
[5 empty] | 2X = length of both side of Frustam | 0 | 0
[5 empty] | 2 EL = Distance between existing outer frustam and RCC wall | 11000 | 11000
[5 empty] | W=Width of RCC wall | 300 | 300
[5 empty] | Z =One side protection wall length=(M+2X+W) | 32100 | 32100
[5 empty] | No of wall for revetment=sides | 2 | 2
[5 empty] | Total length of revetment RCC WALL | 64200 | 64200 | 128400
[5 empty] | Height of RCC Wall above NGL | 4 | 3
|  |  | W | W=300 mm

## Abstract of L98 (hidden)
Cost Estimate- RCC Retaining wall: Tower no. 98 of 400 kV
BOQ Ref. Drg.:
Sl. No. | Ref of DSR 2021 Item No. | Particulars of Items | Unit | Qty | Rate in Rs. | Amount (Rs.)
1 | 2.6.1 | Earth work in excavation by mechanical means (Hydraulic excavator)/manual means over areas (exceeding 30 cm in depth, 1.5 m in width as well as 10 sqm on plan) including getting out and disposal of excavated earth lead upto 50 m and lift upto 1.5 m, as directed by Engineer-in-charge. All kinds of soil | Cum | 110 | 177.5 | 19525
2 | 2.25 | Filling available excavated earth (excluding rock) in trenches, plinth, sides of foundations etc. in layers not exceeding 20cm in depth, consolidating each deposited layer by ramming and watering, lead up to 50 m and lift upto 1.5 m. | cum | 110 | 196 | 21560
3 | 2.25 (a) | Excavating, supplying and filling of local earth (including royalty) by mechanical transport upto a lead of 5km also including ramming and watering of the earth in layers not exceeding 20 cm in trenches, plinth, sides of foundation etc. complete. | cum | 135 | 700.5 | 94567.5
4 | 4.1.8 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering - All work up to plinth level :1:4:8 (1 Cement : 4 coarse sand (zone-III) : 8 graded stone aggregate 40 mm nominal size) | Cum | 6 | 6812 | 40872
5 | 5.1.2 | Providing and laying in position specified grade of reinforced cement concrete, excluding the cost of centering, shuttering, finishing and reinforcement - All work up to plinth level :1:1.5:3 (1 cement : 1.5 coarse sand (zone-III): 3 graded stone aggregate 20 mm nominal size) | Cum | 31 | 9045.75 | 280418.25
6 | 5.2.2 | Reinforced cement concrete work in walls (any thickness), including attached pilasters, buttresses, plinth and string courses, fillets, columns, pillars, piers, abutments, posts and struts etc. above plinth level up to floor five level, excluding cost of centering, shuttering, finishing and reinforcement :1:1.5:3 (1 cement : 1.5 coarse sand(zone-III) : 3 graded stone aggregate 20 mm nominal size) | Cum | 15 | 10852.95 | 162794.25
7 | 5.9.1 | Centering and shuttering including strutting, propping etc. and removal of form for :Foundations, footings, bases of columns, etc. for mass concrete | SqM | 85 | 392.15 | 33332.75
8 | 5.9.2 | Centering and shuttering including strutting, propping etc. and removal of form for :Walls (any thickness) including attached pilasters, butteresses, plinth and string courses etc. | SqM | 150 | 842.5 | 126375
9 | 5.22.6 or 5.22A.6 | Steel reinforcement for R.C.C. work including straightening, cutting, bending, placing in position and binding all complete at all level.Thermo-Mechanically Treated bars of grade Fe-500D or more. | Kg | 2650 | 107.85 | 285802.5
Total | [5 empty] | 1065247
NON Schedule Items
10 | NS | Providing and laying of filter media (53mm to 22.4mm size stone aggregate) along retaining wall. | cum | 30 | 2200 | 66000 | For rate justification quotation attached
11 | NS | Providing and fixing of uPVC Single socketed pipe of approved make of 110mm outer dia of class 3 (Working pressure 6 Kg/ Sq.Cm.) conforming to IS - 13592 at all levels for all types of masonry work(as weep holes) complete in all respect | metre | 9 | 1200 | 10800
Total for NS items | [5 empty] | 76800
Total for NS items Including GST @ 18% | [5 empty] | 90624
Grand Total Estimated cost | [5 empty] | 1155871

## L 98 Cost Estimate (hidden)
Cost Estimate- RCC Retaining wall: Tower no.98 of 400 kV
For 43.8 mtr Length and 1.1m Height above NGL
S.N. | Ref of DSR 2023 Item No. | Particulars of Items | Unit | Nos | Length | Width | Height | Qty | Rate in Rs. | Amount (Rs.)
1 | 2.6.1 | Earth work in excavation by mechanical means (Hydraulic excavator)/manual means over areas (exceeding 30 cm in depth, 1.5 m in width as well as 10 sqm on plan) including getting out and disposal of excavated earth lead upto 50 m and lift upto 1.5 m, as directed by Engineer-in-charge. All kinds of soil | Cum
|  | For Wall below footing |  | 1 | 43.8 | 1.05 | 0.5 | 22.995
|  | For footing |  | 1 | 43.8 | 1.95 | 0.975 | 83.2747
106.2697
|  | Total Quantity | Cum |  |  |  | Say | 110 | 177.5 | 19525
2 | 2.25 | Filling available excavated earth (excluding rock) in trenches, plinth, sides of foundations etc. in layers not exceeding 20cm in depth, consolidating each deposited layer by ramming and watering, lead up to 50 m and lift upto 1.5 m.
|  | Total Excavation Lum Sum | [5 empty] | 106.2697
|  | Total Quantity | cum |  |  |  | Say | 110 | 196 | 21560
3 | 2.25 (a) | Excavating, supplying and filling of local earth (including royalty) by mechanical transport upto a lead of 5km also including ramming and watering of the earth in layers not exceeding 20 cm in trenches, plinth, sides of foundation etc. complete.
|  | Filling inside |  | 1 | 10.95 | 10.95 | 1.1 | 131.8928
|  | Total Quantity | cum |  |  |  | Say | 135 | 700.5 | 94567.5
4 | 4.1.8 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering - All work up to plinth level :1:4:8 (1 Cement : 4 coarse sand (zone-III) : 8 graded stone aggregate 40 mm nominal size) | Cum
|  | For Wall below footing |  | 1 | 43.8 | 0.45 | 0.075 | 1.4783
|  | For footing |  | 1 | 43.8 | 1.35 | 0.075 | 4.4347
5.913
|  | Total Quantity | Cum |  |  |  |  | 6 | 6812 | 40872
5 | 5.1.2 | Providing and laying in position specified grade of reinforced cement concrete, excluding the cost of centering, shuttering, finishing and reinforcement - All work up to plinth level :1:1.5:3 (1 cement : 1.5 coarse sand (zone-III): 3 graded stone aggregate 20 mm nominal size)
|  | For Wall below footing |  | 1 | 43.8 | 0.3 | 0.5 | 6.57
|  | For footing |  | 1 | 43.8 | 1.2 | 0.3 | 15.768
|  | wall from footing top to GL |  | 1 | 43.8 | 0.3 | 0.6 | 7.884
30.222
|  | Total Quantity | Cum |  |  |  | Say | 31 | 9045.75 | 280418.25
6 | 5.2.2 | Reinforced cement concrete work in walls (any thickness), including attached pilasters, buttresses, plinth and string courses, fillets, columns, pillars, piers, abutments, posts and struts etc. above plinth level up to floor five level, excluding cost of centering, shuttering, finishing and reinforcement :1:1.5:3 (1 cement : 1.5 coarse sand(zone-III) : 3 graded stone aggregate 20 mm nominal size)
|  | wall from Plinth level to top |  | 1 | 43.8 | 0.3 | 1.1 | 14.454
|  | Total Quantity | Cum |  |  |  | Say | 15 | 10852.95 | 162794.25
7 | 5.9.1 | Centering and shuttering including strutting, propping etc. and removal of form for :Foundations, footings, bases of columns, etc. for mass concrete
|  | For Wall below footing (PCC) |  | 2 | 43.8 |  | 0.075 | 6.57
|  | For Wall below footing (RCC) |  | 2 | 43.8 |  | 0.5 | 43.8
|  | For footing (PCC) |  | 2 | 43.8 |  | 0.075 | 6.57
|  | For footing (RCC) |  | 2 | 43.8 |  | 0.3 | 26.28
83.22
|  | Total Quantity | SqM |  |  |  | Say | 85 | 392.15 | 33332.75
8 | 5.9.2 | Centering and shuttering including strutting, propping etc. and removal of form for :Walls (any thickness) including attached pilasters, butteresses, plinth and string courses etc.
|  | Wall from footing to GL |  | 2 | 43.8 |  | 0.6 | 52.56
|  | Wall from GL to Top |  | 2 | 43.8 |  | 1.1 | 96.36
148.92
|  | Total Quantity | SqM |  |  |  | Say | 150 | 842.5 | 126375
9 | 5.22.6 or 5.22A.6 | Steel reinforcement for R.C.C. work including straightening, cutting, bending, placing in position and binding all complete at all level.Thermo-Mechanically Treated bars of grade Fe-500D or more. |  |  |  | Wt/mtr
|  | Raft Top & Bottom main Bar 10mm@200c/c |  | 742 | 1.3 | 0.617 |  | 595.1582
|  | Raft Top & Bottom Binder 10mm @ 200c/c |  | 14 | 43.8 | 0.617 |  | 378.3444
|  | Over Lap(authorised) |  | 56 | 0.5 | 0.617 |  | 17.276
|  | Wall verticle main bar 10mm@150c/c (Inner Side & outer) |  | 586 | 2.6 | 0.617 |  | 940.0612
|  | Wall Binder 10mm@ 200C/C (inner side & outer side) |  | 24 | 43.8 | 0.617 |  | 648.5904
|  | Over Lap(authorised) |  | 96 | 0.5 | 0.617 |  | 29.616
2609.0462
|  | Total Quantity | Kg |  |  |  | Say | 2650 | 107.85 | 285802.5
10 | NS | Providing and laying of filter media (53mm to 22.4mm size stone aggregate) along retaining wall.
|  | Total Qty. | cum | 1 | 43.8 | 0.5 | 1.1 | 30 | 2200 | 66000 | 29.2
11 | NS | Providing and fixing of uPVC Single socketed pipe of approved make of 110mm outer dia of class 3 (Working pressure 6 Kg/ Sq.Cm.) conforming to IS - 13592 at all levels for all types of masonry work(as weep holes) complete in all respect
|  | Total Qty. | RM | 30 | 0.3 |  |  | 9 | 1200 | 10800
|  | Total Estimated cost as per DSR'2023 | [7 empty] | 1142047.25
|  | GST @18 % on NS Items | [7 empty] | 13824
|  | Grand Total Estimated cost | [7 empty] | 1155871.25

## L98 Protection Plan (hidden)
Details of SCHEME FOR PROTECTION OF FOUNDATION OF TOWERS FROM SOIL CUTTING
|  | Name of Transmission Line :- | Tower no. 161 of 98 kV
Ref. Drg.:
[6 empty] | Calculation of Revetment wall length | L(mm)
Tower No-98,Tower Type A ,RCC Wall -4 side
[6 empty] | M =Distance between centre of adjecent pit | 7650
2X = length of both side of Frustam
[6 empty] | 2 EL = Distance between existing foundation and RCC wall | 3000
[6 empty] | W=Width of RCC wall | 300
[6 empty] | Z =One side protection wall length=(M+2X+W) | 10950
| 750 |  |  |  |  | No of wall for revetment=sides | 4
[6 empty] | Total length of revetment RCC WALL | 43800
[6 empty] | Height of RCC Wall above NGL | 1.1
|  |  |  | W | W=300 mm

## Abtract of L 161 (hidden)
Cost Estimate- RCC Retaining wall: Tower no. 161 of 400 kV
BOQ Ref. Drg.:
Sl. No. | Ref of DSR 2021 Item No. | Particulars of Items | Unit | Qty | Rate in Rs. | Amount (Rs.)
1 | 2.6.1 | Earth work in excavation by mechanical means (Hydraulic excavator)/manual means over areas (exceeding 30 cm in depth, 1.5 m in width as well as 10 sqm on plan) including getting out and disposal of excavated earth lead upto 50 m and lift upto 1.5 m, as directed by Engineer-in-charge. All kinds of soil | Cum | 185 | 177.5 | 32837.5
2 | 2.25 | Filling available excavated earth (excluding rock) in trenches, plinth, sides of foundations etc. in layers not exceeding 20cm in depth, consolidating each deposited layer by ramming and watering, lead up to 50 m and lift upto 1.5 m. | cum | 185 | 196 | 36260
3 | 2.25 (a) | Excavating, supplying and filling of local earth (including royalty) by mechanical transport upto a lead of 5km also including ramming and watering of the earth in layers not exceeding 20 cm in trenches, plinth, sides of foundation etc. complete. | cum | 60 | 700.5 | 42030
4 | 4.1.8 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering - All work up to plinth level :1:4:8 (1 Cement : 4 coarse sand (zone-III) : 8 graded stone aggregate 40 mm nominal size) | Cum | 10 | 6812 | 68120
5 | 5.1.2 | Providing and laying in position specified grade of reinforced cement concrete, excluding the cost of centering, shuttering, finishing and reinforcement - All work up to plinth level :1:1.5:3 (1 cement : 1.5 coarse sand (zone-III): 3 graded stone aggregate 20 mm nominal size) | Cum | 52 | 9045.75 | 470379
6 | 5.2.2 | Reinforced cement concrete work in walls (any thickness), including attached pilasters, buttresses, plinth and string courses, fillets, columns, pillars, piers, abutments, posts and struts etc. above plinth level up to floor five level, excluding cost of centering, shuttering, finishing and reinforcement :1:1.5:3 (1 cement : 1.5 coarse sand(zone-III) : 3 graded stone aggregate 20 mm nominal size) | Cum | 34 | 10852.95 | 369000.3
7 | 5.9.1 | Centering and shuttering including strutting, propping etc. and removal of form for :Foundations, footings, bases of columns, etc. for mass concrete | SqM | 145 | 392.15 | 56861.75
8 | 5.9.2 | Centering and shuttering including strutting, propping etc. and removal of form for :Walls (any thickness) including attached pilasters, butteresses, plinth and string courses etc. | SqM | 315 | 842.5 | 265387.5
9 | 5.22.6 or 5.22A.6 | Steel reinforcement for R.C.C. work including straightening, cutting, bending, placing in position and binding all complete at all level.Thermo-Mechanically Treated bars of grade Fe-500D or more. | Kg | 4500 | 107.85 | 485325
Total | [5 empty] | 1826201
NON Schedule Items
10 | NS | Providing and laying of filter media (53mm to 22.4mm size stone aggregate) along retaining wall. | cum | 50 | 2200 | 110000 | For rate justification quotation attached
11 | NS | Providing and fixing of uPVC Single socketed pipe of approved make of 110mm outer dia of class 3 (Working pressure 6 Kg/ Sq.Cm.) conforming to IS - 13592 at all levels for all types of masonry work(as weep holes) complete in all respect | metre | 15 | 1200 | 18000
Total for NS items | [5 empty] | 128000
Total for NS items Including GST @ 18% | [5 empty] | 151040
Grand Total Estimated cost | [5 empty] | 1977241

## L 161 Cost Estimate (hidden)
Cost Estimate- RCC Retaining wall: Tower no.161 of 400 kV
For 74 mtr Length and 1.5m Height above NGL
S.N. | Ref of DSR 2023 Item No. | Particulars of Items | Unit | Nos | Length | Width | Height | Qty | Rate in Rs. | Amount (Rs.)
1 | 2.6.1 | Earth work in excavation by mechanical means (Hydraulic excavator)/manual means over areas (exceeding 30 cm in depth, 1.5 m in width as well as 10 sqm on plan) including getting out and disposal of excavated earth lead upto 50 m and lift upto 1.5 m, as directed by Engineer-in-charge. All kinds of soil | Cum
|  | For Wall below footing |  | 1 | 74 | 1.05 | 0.5 | 38.85
|  | For footing |  | 1 | 74 | 1.95 | 0.975 | 140.6925
179.5425
|  | Total Quantity | Cum |  |  |  | Say | 185 | 177.5 | 32837.5
2 | 2.25 | Filling available excavated earth (excluding rock) in trenches, plinth, sides of foundations etc. in layers not exceeding 20cm in depth, consolidating each deposited layer by ramming and watering, lead up to 50 m and lift upto 1.5 m.
|  | Total Excavation Lum Sum | [5 empty] | 179.5425
|  | Total Quantity | cum |  |  |  | Say | 185 | 196 | 36260
3 | 2.25 (a) | Excavating, supplying and filling of local earth (including royalty) by mechanical transport upto a lead of 5km also including ramming and watering of the earth in layers not exceeding 20 cm in trenches, plinth, sides of foundation etc. complete.
|  | Filling inside of wall Lum sum |  | 1 | 74 | 0.5 | 1.5 | 55.5
|  | Total Quantity | cum |  |  |  | Say | 60 | 700.5 | 42030
4 | 4.1.8 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering - All work up to plinth level :1:4:8 (1 Cement : 4 coarse sand (zone-III) : 8 graded stone aggregate 40 mm nominal size) | Cum
|  | For Wall below footing |  | 1 | 74 | 0.45 | 0.075 | 2.4975
|  | For footing |  | 1 | 74 | 1.35 | 0.075 | 7.4925
9.99
|  | Total Quantity | Cum |  |  |  |  | 10 | 6812 | 68120
5 | 5.1.2 | Providing and laying in position specified grade of reinforced cement concrete, excluding the cost of centering, shuttering, finishing and reinforcement - All work up to plinth level :1:1.5:3 (1 cement : 1.5 coarse sand (zone-III): 3 graded stone aggregate 20 mm nominal size)
|  | For Wall below footing |  | 1 | 74 | 0.3 | 0.5 | 11.1
|  | For footing |  | 1 | 74 | 1.2 | 0.3 | 26.64 |  |  |  | 1.2+.6
|  | wall from footing top to GL |  | 1 | 74 | 0.3 | 0.6 | 13.32
51.06
|  | Total Quantity | Cum |  |  |  | Say | 52 | 9045.75 | 470379
6 | 5.2.2 | Reinforced cement concrete work in walls (any thickness), including attached pilasters, buttresses, plinth and string courses, fillets, columns, pillars, piers, abutments, posts and struts etc. above plinth level up to floor five level, excluding cost of centering, shuttering, finishing and reinforcement :1:1.5:3 (1 cement : 1.5 coarse sand(zone-III) : 3 graded stone aggregate 20 mm nominal size)
|  | wall from Plinth level to top |  | 1 | 74 | 0.3 | 1.5 | 33.3 |  |  |  | 6880
|  | Total Quantity | Cum |  |  |  | Say | 34 | 10852.95 | 369000.3
7 | 5.9.1 | Centering and shuttering including strutting, propping etc. and removal of form for :Foundations, footings, bases of columns, etc. for mass concrete
|  | For Wall below footing (PCC) |  | 2 | 74 |  | 0.075 | 11.1
|  | For Wall below footing (RCC) |  | 2 | 74 |  | 0.5 | 74
|  | For footing (PCC) |  | 2 | 74 |  | 0.075 | 11.1
|  | For footing (RCC) |  | 2 | 74 |  | 0.3 | 44.4
140.6
|  | Total Quantity | SqM |  |  |  | Say | 145 | 392.15 | 56861.75
8 | 5.9.2 | Centering and shuttering including strutting, propping etc. and removal of form for :Walls (any thickness) including attached pilasters, butteresses, plinth and string courses etc.
|  | Wall from footing to GL |  | 2 | 74 |  | 0.6 | 88.8
|  | Wall from GL to Top |  | 2 | 74 |  | 1.5 | 222
310.8
|  | Total Quantity | SqM |  |  |  | Say | 315 | 842.5 | 265387.5
9 | 5.22.6 or 5.22A.6 | Steel reinforcement for R.C.C. work including straightening, cutting, bending, placing in position and binding all complete at all level.Thermo-Mechanically Treated bars of grade Fe-500D or more. |  |  |  | Wt/mtr
|  | Raft Top & Bottom main Bar 10mm@200c/c |  | 742 | 1.3 | 0.617 |  | 595.1582
|  | Raft Top & Bottom Binder 10mm @ 200c/c |  | 14 | 74 | 0.617 |  | 639.212
|  | Over Lap(authorised) |  | 98 | 0.5 | 0.617 |  | 30.233
|  | Wall verticle main bar 10mm@150c/c (Inner Side & outer) |  | 988 | 3 | 0.617 |  | 1828.788
|  | Wall Binder 10mm@ 200C/C (inner side & outer side) |  | 28 | 74 | 0.617 |  | 1278.424
|  | Over Lap(authorised) |  | 196 | 0.5 | 0.617 |  | 60.466
4432.2812
|  | Total Quantity | Kg |  |  |  | Say | 4500 | 107.85 | 485325
10 | NS | Providing and laying of filter media (53mm to 22.4mm size stone aggregate) along retaining wall.
|  | Total Qty. | cum | 1 | 74 | 0.5 | 1.5 | 50 | 2200 | 110000 | 49.3333
11 | NS | Providing and fixing of uPVC Single socketed pipe of approved make of 110mm outer dia of class 3 (Working pressure 6 Kg/ Sq.Cm.) conforming to IS - 13592 at all levels for all types of masonry work(as weep holes) complete in all respect
|  | Total Qty. | RM | 50 | 0.3 |  |  | 15 | 1200 | 18000
|  | Total Estimated cost as per DSR'2023 | [7 empty] | 1954201.05
|  | GST @18 % on NS Items | [7 empty] | 23040
|  | Grand Total Estimated cost | [7 empty] | 1977241.05

## L 161 Protection Plan (hidden)
Details of SCHEME FOR PROTECTION OF FOUNDATION OF TOWERS FROM SOIL CUTTING
|  | Name of Transmission Line :- | Tower no. 161 of 400 kV
Ref. Drg.:
[6 empty] | Calculation of Revetment wall length | L(mm)
Tower No-161, DA+25 Tower Type- ,RCC Wall -4 side
[6 empty] | M =Distance between centre of adjecent pit | 15200
2X = length of both side of Frustam
[6 empty] | 2 EL = Distance between existing foundation and RCC wall | 3000
[6 empty] | W=Width of RCC wall | 300
[6 empty] | Z =One side protection wall length=(M+2X+W) | 18500
| 750 |  |  |  |  | No of wall for revetment=sides | 4
[6 empty] | Total length of revetment RCC WALL | 74000
[6 empty] | Height of RCC Wall above NGL | 1500
|  |  |  | W | W=300 mm

## Abstract of L 82 (hidden)
Cost Estimate- RCC Retaining wall: 400 kV Meerut-Mandola ckt-I & II , L-82
Sl. No. | Ref of DSR 2023 Item No. | Particulars of Items | Unit | Nos | Length | Width | Height | Qty | Rate in Rs. | Amount (Rs.)
1 | 2.1.1 | Earth work in surface excavation not exceeding 30 cm in depth but exceeding 1.5 m in width as well as 10 sqm on plan including getting out and disposal of excavated earth upto 50 m and lift upto 1.5 m, as directed by Engineer-in- Charge: All kinds of soil | sqm | 1 | 12.5 | 12.5 |  | 156.25 | 129.85 | 20289.0625
2 | 2.6.1 | Earth work in excavation by mechanical means (Hydraulic excavator)/manual means over areas (exceeding 30 cm in depth, 1.5 m in width as well as 10 sqm on plan) including getting out and disposal of excavated earth lead upto 50 m and lift upto 1.5 m, as directed by Engineer-in-charge. All kinds of soil | Cum |  |  |  |  | 116.325 | 177.5 | 20647.6875
3 | 2.25 | Filling available excavated earth (excluding rock) in trenches, plinth, sides of foundations etc. in layers not exceeding 20cm in depth, consolidating each deposited layer by ramming and watering, lead up to 50 m and lift upto 1.5 m. | Cum |  |  |  |  | 116.325 | 196 | 22799.7
4 | 2.25 (a) | Excavating, supplying and filling of local earth (including royalty) by mechanical transport upto a lead of 5km also including ramming and watering of the earth in layers not exceeding 20 cm in trenches, plinth, sides of foundation etc. complete. | Cum |  |  |  |  | 0 | 700.5 | 0
5 | 4.1.8 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering - All work up to plinth level :1:4:8 (1 Cement : 4 coarse sand (zone-III) : 8 graded stone aggregate 40 mm nominal size) | Cum |  |  |  |  | 7.425 | 6812 | 50579.1
6 | 5.1.2 | Providing and laying in position specified grade of reinforced cement concrete, excluding the cost of centering, shuttering, finishing and reinforcement - All work up to plinth level :1:1.5:3 (1 cement : 1.5 coarse sand (zone-III): 3 graded stone aggregate 20 mm nominal size) | [5 empty] | 53.46 | 9045.75 | 483585.795
7 | 5.2.2 | Reinforced cement concrete work in walls (any thickness), including attached pilasters, buttresses, plinth and string courses, fillets, columns, pillars, piers, abutments, posts and struts etc. above plinth level up to floor five level, excluding cost of centering, shuttering, finishing and reinforcement :1:1.5:3 (1 cement : 1.5 coarse sand(zone-III) : 3 graded stone aggregate 20 mm nominal size) | [5 empty] | 31.68 | 10852.95 | 343821.456
8 | 5.9.1 | Centering and shuttering including strutting, propping etc. and removal of form for :Foundations, footings, bases of columns, etc. for mass concrete | [5 empty] | 125.4 | 392.15 | 49175.61
9 | 5.9.2 | Centering and shuttering including strutting, propping etc. and removal of form for :Walls (any thickness) including attached pilasters, butteresses, plinth and string courses etc. | [5 empty] | 343.2 | 842.5 | 289146
10 | 5.22.6 or 5.22A.6 | Steel reinforcement for R.C.C. work including straightening, cutting, bending, placing in position and binding all complete at all level.Thermo-Mechanically Treated bars of grade Fe-500D or more. | [5 empty] | 4680 | 107.85 | 504738
|  | Total | [7 empty] | 1784782.411
11 | NS | Providing and laying of filter media (53mm to 22.4mm size stone aggregate) confined in GI(hot dip galvanised- galvanizing/ zinc coating not less than 270g/Sq.m.) welded wire mesh (of average width of aperture 15mm and nominal dia of wire 1.6mm conforming to IS:4948(Latest)) of approximately 500 mm size cuboid(typical) with edges(at junction of two faces) of cuboid strengthened with MS flat 25x3mm or Angle section 25x25x3 (size of cuboid 300 mm each face) including labours, materials at all levels complete in all respect. (Unit in Each) | Each | 58.6667 |  |  |  | 44 | 2200 | 129800
12 | NS | Providing and fixing of uPVC Single socketed pipe of approved make of 110mm outer dia of class 3 (Working pressure 6 Kg/ Sq.Cm.) conforming to IS - 13592 at all levels for all types of masonry work(as weep holes) complete in all respect | RM |  | 0.3 |  |  | 14 | 1200 | 21240
Total of NS Items | [9 empty] | 151040
GST@18% on NS Item | [9 empty] | 27187.2
Grand Total Estimated cost | [9 empty] | 1963009.611

## L 82 Cost Estimate (hidden)
Cost Estimate- RCC Retaining wall: 400 kV Meerut-Mandola ckt-I & II , L-82
For (12.5+2+2)x4=66 mtr Length and 2 Mtr Height
Sl. No. | Ref of DSR 2023 Item No. | Particulars of Items | Unit | Nos | Length | Width | Height | Qty | Rate in Rs. | Amount (Rs.)
1 | 2.1.1 | Earth work in surface excavation not exceeding 30 cm in depth but exceeding 1.5 m in width as well as 10 sqm on plan including getting out and disposal of excavated earth upto 50 m and lift upto 1.5 m, as directed by Engineer-in- Charge: All kinds of soil
|  | Total area | sqm | 1 | 10 | 10 |  | 100 | 129.85 | 12985
2 | 2.6.1 | Earth work in excavation by mechanical means (Hydraulic excavator)/manual means over areas (exceeding 30 cm in depth, 1.5 m in width as well as 10 sqm on plan) including getting out and disposal of excavated earth lead upto 50 m and lift upto 1.5 m, as directed by Engineer-in-charge. All kinds of soil | Cum
|  | For Wall below footing |  | 1 | 66 | 0.6 | 0.5 | 19.8
|  | For footing |  | 1 | 66 | 1.5 | 0.975 | 96.525
|  | Total Qty. | Cum |  |  |  |  | 116.325 | 177.5 | 20647.6875
3 | 2.25 | Filling available excavated earth (excluding rock) in trenches, plinth, sides of foundations etc. in layers not exceeding 20cm in depth, consolidating each deposited layer by ramming and watering, lead up to 50 m and lift upto 1.5 m.
|  | Total Excavation | [5 empty] | 116.325
|  | Total Qty. | cum |  |  |  |  | 116.325 | 196 | 22799.7
4 | 2.25 (a) | Excavating, supplying and filling of local earth (including royalty) by mechanical transport upto a lead of 5km also including ramming and watering of the earth in layers not exceeding 20 cm in trenches, plinth, sides of foundation etc. complete.
|  | Filling inside of wall |  | 0 | 0 | 0 | 0 | 0
|  | Total Qty. | cum |  |  |  |  | 0 | 700.5 | 0
5 | 4.1.8 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering - All work up to plinth level :1:4:8 (1 Cement : 4 coarse sand (zone-III) : 8 graded stone aggregate 40 mm nominal size) | Cum
|  | For Wall below footing |  | 1 | 66 | 0.45 | 0.075 | 2.2275
|  | For footing |  | 1 | 66 | 1.05 | 0.075 | 5.1975
|  | Total Qty. | Cum |  |  |  |  | 7.425 | 6812 | 50579.1
6 | 5.1.2 | Providing and laying in position specified grade of reinforced cement concrete, excluding the cost of centering, shuttering, finishing and reinforcement - All work up to plinth level :1:1.5:3 (1 cement : 1.5 coarse sand (zone-III): 3 graded stone aggregate 20 mm nominal size)
|  | For Wall below footing |  | 1 | 66 | 0.3 | 0.5 | 9.9
|  | For footing |  | 1 | 66 | 1.2 | 0.3 | 23.76
|  | wall from footing top to GL |  | 1 | 66 | 0.3 | 0.6 | 11.88
|  | wall from GL to Plinth lvl |  | 1 | 66 | 0.3 | 0.4 | 7.92
|  | Total Qty. | Cum |  |  |  |  | 53.46 | 9045.75 | 483585.795
7 | 5.2.2 | Reinforced cement concrete work in walls (any thickness), including attached pilasters, buttresses, plinth and string courses, fillets, columns, pillars, piers, abutments, posts and struts etc. above plinth level up to floor five level, excluding cost of centering, shuttering, finishing and reinforcement :1:1.5:3 (1 cement : 1.5 coarse sand(zone-III) : 3 graded stone aggregate 20 mm nominal size)
|  | wall from Plinth level to top |  | 1 | 66 | 0.3 | 1.6 | 31.68
|  | Total Qty. | Cum |  |  |  |  | 31.68 | 10852.95 | 343821.456
8 | 5.9.1 | Centering and shuttering including strutting, propping etc. and removal of form for :Foundations, footings, bases of columns, etc. for mass concrete
|  | For Wall below footing (PCC) |  | 2 | 66 |  | 0.075 | 9.9
|  | For Wall below footing (RCC) |  | 2 | 66 |  | 0.5 | 66
|  | For footing (PCC) |  | 2 | 66 |  | 0.075 | 9.9
|  | For footing (RCC) |  | 2 | 66 |  | 0.3 | 39.6
|  | Total Qty. | SqM |  |  |  |  | 125.4 | 392.15 | 49175.61
9 | 5.9.2 | Centering and shuttering including strutting, propping etc. and removal of form for :Walls (any thickness) including attached pilasters, butteresses, plinth and string courses etc.
|  | Wall from footing to GL |  | 2 | 66 |  | 0.6 | 79.2
|  | Wall from GL to Top |  | 2 | 66 |  | 2 | 264
|  | Total Qty. | SqM |  |  |  |  | 343.2 | 842.5 | 289146
10 | 5.22.6 or 5.22A.6 | Steel reinforcement for R.C.C. work including straightening, cutting, bending, placing in position and binding all complete at all level.Thermo-Mechanically Treated bars of grade Fe-500D or more.
|  | As per BBS. | Kg |  |  |  |  | 4680 | 107.85 | 504738
11 | NS | Providing and laying of filter media (53mm to 22.4mm size stone aggregate) confined in GI(hot dip galvanised- galvanizing/ zinc coating not less than 270g/Sq.m.) welded wire mesh (of average width of aperture 15mm and nominal dia of wire 1.6mm conforming to IS:4948(Latest)) of approximately 500 mm size cuboid(typical) with edges(at junction of two faces) of cuboid strengthened with MS flat 25x3mm or Angle section 25x25x3 (size of cuboid 300 mm each face) including labours, materials at all levels complete in all respect. (Unit in Each) | [8 empty] | 44
|  | Total Qty. | Each | 44 |  |  |  | 44 | 2200 | 96800
12 | NS | Providing and fixing of uPVC Single socketed pipe of approved make of 110mm outer dia of class 3 (Working pressure 6 Kg/ Sq.Cm.) conforming to IS - 13592 at all levels for all types of masonry work(as weep holes) complete in all respect
|  | Total Qty. | RM |  | 0.3 |  |  | 14 | 1200 | 16800
Total Estimated cost as per DSR'2023 | [9 empty] | 1891078.3485
GST@18% on NS Item | [9 empty] | 20448
Grand Total Estimated cost | [9 empty] | 1911526.3485

## Bar Bending Schedule of L 82 (hidden)
POWER GRID CORPORATION OF INDIA LTD.
BAR BENDING SCHEDULE
Drawing No. :- C/ENGG/NR1/BW/RETAING WALL/BW-01
Line Name & Location :- 400 Kv Meerut - Mandola , Loc-82 (66 mtr) : 2.0 meter height
Item Name :- Retaining Wall
SR NO. | Description | Bar dia | No of Footings | Spacing | No. of bar | Total No of Bars | Shape of Bar. | Length (M) |  |  | Length (M) | Total Length (in M) | Unit weight (kg per mtr) |  |  |  | Remarks
[8 empty] | a | b | c |  |  | 8 | 10 | 12 | 16
[13 empty] | 0.395 | 0.617 | 0.888 | 1.58
1 | Raft
1 | Bottom Bar (Short Bar) | 10 | 1 | 200 | 331 | 331 |  | 0.1 | 1.1 | 0.1 | 1.3 | 430.3 | 0 | 265.4951 | 0 | .
2 | Top Bar (Short Bar) | 10 | 1 | 200 | 331 | 331 |  | 0.1 | 1.1 | 0.1 | 1.3 | 430.3 | 0 | 265.4951 | 0 | .
3 | Bottom Bar (Long bar) | 10 | 1 | 200 | 6.5 | 7 |  | … | 66 | .. | 66 | 462 |  | 285.054 |  | . | Avg. Length
4 | Top Bar (Long bar) | 10 | 1 | 200 | 6.5 | 7 |  | …. | 66 | .. | 66 | 462 |  | 285.054 |  | . | Avg. Length
Wall
5 | Vertcal Bar (Inner side) | 10 | 1 | 150 | 441 | 441 |  | 0.1 | 3.52 | 0.1 | 3.72 | 1640.52 | 0 | 1012.2008 |  | .
6 | Vertcal Bar (Outer side) | 10 | 1 | 150 | 441 | 441 |  | 0.1 | 3.52 | 0.1 | 3.72 | 1640.52 | 0 | 1012.2008 |  | .
7 | Horizontal bar (Inner side) | 10 | 1 | 200 | 17.5 | 18 |  | .. | 66 | .. | 66 | 1188 | . | 732.996 | .. | .
8 | Horizontal bar (Outer side) | 10 | 1 | 200 | 17.5 | 18 |  | .. | 66 | .. | 66 | 1188 |  | 732.996 | .. | .
9 | Over Lap | 10 | 1 | .. | 286.9565 |  |  | .. | 0.5 | . | 0.5 | 143.4783 |  | 88.5261 |  |  | Eff. Length 11.5
[13 empty] | 0 | 4680.018 | 0 | 0 | 4680.018
Note : this measurement is tantative . Billing process is to be made as per actual value.