| Sr. No. | Clause No. & Reference | Tender Description |  | Bidders Query | POWERGRID Reply |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | Bid Data Sheet (BDS) Introduction | POWERGRID Energy Services ltd (PESL), a wholly owned subsidiary of Power Grid Corporation of India Ltd (POWERGRID) a company incorporated under the companies act, 2013 having its registered office plot no-2 sector - 29, Gurugram, Haryana – 122001, has been appointed as Project Implementing Agency (PIA) (Hereinafter referred to as employer/utility) Form-6 & Form 21 |  | Please refer to the Bid forms and kindly specify whether the name of Employer or the name of the utility is to be filled | Against form 6 and 21, the documents need to be submitted in the name of POWERGRID only. Refer amendment-2 in this regard. |  |
|  | Bid Data Sheet (BDS) Introduction | POWERGRID Energy Services ltd (PESL), a wholly owned subsidiary of Power Grid Corporation of India Ltd (POWERGRID) a company incorporated under the companies act, 2013 having its registered office plot no-2 sector - 29, Gurugram, Haryana – 122001, has been appointed as Project Implementing Agency (PIA) (Hereinafter referred to as employer/utility) Form-15, Form-18 & Form - 20 |  | Please refer to the Bid forms and kindly specify whether the name of Employer or the name of the utility is to be filled | Against form 15, 18 and 20, the documents need to be submitted in the name of POWERGRID only as per the provisions of the Bidding Documents. |  |
|  | Bid Data Sheet (BDS) Introduction | POWERGRID Energy Services ltd (PESL), a wholly owned subsidiary of Power Grid Corporation of India Ltd (POWERGRID) a company incorporated under the companies act, 2013 having its registered office plot no-2 sector - 29, Gurugram, Haryana – 122001, has been appointed as Project Implementing Agency (PIA) (Hereinafter referred to as employer/utility) Form-1,Form-5, Form-6, Form-9,Form-10,Form-12 to 20 & Form-4A,4B |  | Please refer to the Bid forms and kindly specify whether the name and address of Employer is to be filled | Against form 1,5,6,9,10,12,20,4A & 4B, the documents need to be submitted in the name of POWERGRID only as per the provisions of the Bidding Documents. |  |
|  | Section-4: Bidding Forms-Technical Part of the Bid | Net worth in last three years - Financial Year 2020-21 - Financial Year 2021-22 - Financial Year 2022-23 Form 9 |  | As the balance sheet of the Financial Year 2022-23 is not yet finalized, you are requested to amend the clause. Net worth in last three years - Financial Year 2019-20 - Financial Year 2020-21 - Financial Year 2021-22 Minimum Average Annual turnover (MAAT) - Financial Year 2017-18 - Financial Year 2018-19 - Financial Year 2019-20 Financial Year 2019-20 - Financial Year 2020-21 - Financial Year 2021-22 | Please refer Amendment No.2 in this regard. |  |
|  |  | Minimum Average Annual turnover (MAAT) - Financial Year 2018-19 - Financial Year 2019-20 Financial Year 2019-20 - Financial Year 2020-21 - Financial Year 2021-22 - Financial Year 2022-23 Form 9 |  |  |  |  |
|  | BOQ and SBD Part-2 Technical Specification | Price schedule 1.1 KV, 1 CORE 70 MM2, FRLS, PVC CABLE 1.1 KV, 1 CORE 95 MM2, FRLS, PVC CABLE AS TS 1.1 KV, 1 CORE 185 MM2, FRLS, PVC CABLE AS PER TS The Specification of LT cable |  | As per BOQ the LT cable of 1.1 kV, 1Core 70 mm2 , 1.1 kV, 1Core 95 mm2 & 1.1 kV, 1Core 185 mm2 is mentioned as PVC insulated but as per TS the same cable mentioned as XLPE Insulated . Please clarify the cable is XLPE insulated or PVC insulated. If PVC insulated then please provide the TS of PVC insulated LT cable | The referred LT cable is PVC insulated. For technical specification of PVC LT Cable refer Clause 3.3 of Section Project of Bidding documents which is reproduced below: In case specification of any equipment /material is not included in this volume, the same shall be supplied as per relevant standards. Latest REC specification & Construction Standards may also be referred to. |  |
|  | SBD Part-2 Technical Specification | Technical Specification of Insulation Piercing Connectors Page 696 – The contact plates should be made of tinned copper / aluminum alloy. |  | Please define which material should be considered for the contact plate. | Both type of contact plate as per TS shall be acceptable. |  |
|  | Tender Document | BOCW / Labour Cess |  | Please clarify that the BOCW taxes will be applicable on total contract value (Supply+ Erection) or only erection price. The GST of BOCW is also applicable or not. | The provisions of the Bidding Documents are amply clear. |  |
|  | Price schedule /Scope of Work | 11 KV 3CX120+1X95 MM2, AB CABLE AS TS |  | As per our previous work experience usage of HT AB Cable is not successful due to frequently fault occurs in cable and there are frequently maintenance /replacement require. Presently maximum power utilities are avoiding usage of HT AB Cable, even KPDCL also avoided usage of HT AB Cable. in our previously executed project. Hence in place of HT AB Cable we propose to use bare Conductor or Covered Conductor. | HT AB Cable shall be used as per Price Schedule BOQ. |  |
|  | Price_schedule_Pulwama_Awantipora | SL No. - 7 under Awantipura LT DISTRIBUTION BOX, WITH MCCB FOR INCOMER & SWITCH FUSE UNITS FOROUTGOING CIRCUITS, SUITABLE FOR 63 KVA DT AS PER TS Quantity- 253 SL No. - 16 under Awantipura LT DISTRIBUTION BOX SUITABLE FOR 63 KVA DT AS PER TS Quantity- 253 |  | There is a discrepancy in the quantity of Distribution box for 63 KVA Transformer under Awantipura's BOQ. According to our understanding, one component should be a 63 KVA transformer and the other should be an LTDB. Please clarify the same and modify the BOQ accordingly. | Price schedule’s description has been modified. Refer Errata-1 |  |
|  | Price_schedule_Pulwama_Awantipora | Mismatch the Supply VS Erection Quantity of Steel Tubular Pole (STP) |  | Total Quantity of STP in Sch-1(Supply) is 17537 No. but total quantity of STP in Sch-2 (Erection) is 16464 No. Please confirm the exact quantity and accordingly modify the BOQ. | Quantity in Price schedule has been modified. Refer Errata-1 |  |
|  | Price_schedule_Pulwama_Awantipora | Mismatch the Supply VS Erection Quantity of HT AB Cable |  | Total Qiuantity of HT AB Cable in Sch-1(Supply) is 452 Km. but total quantity of STP in Sch-2 (Erection) is 162 Km. Please confirm the exact quantity and accordingly modify the BOQ. | Quantity in Price schedule has been modified. Refer Errata-1 |  |
|  | Price_schedule_Pulwama_Awantipora | Mismatch the Supply VS Erection Quantity of Steel Tubular Pole (STP) |  | Total Quantity of STP in Sch-1(Supply) is 20452 No. but total quantity of STP in Sch-2 (Erection) is 20914 No. Please confirm the exact quantity and accordingly modify the BOQ. | Quantity in Price schedule has been modified. Refer Errata-1 |  |
|  |  | GI FLAT FOR NEUTRAL EARTHING OF DT |  | 50x6mm GI Flat is mentioned for earth mat and risers in Scope of work (pg-100), but the given price schedule Quantity/weight of GI flat is not sufficient for DTR Earthing and also 8SWG GI wire for earthing is not given in Price schedule. Please clarify. | DT shall be earthed as per REC construction standard. Further, DT neutral shall be earthed using MS flat while other equipment shall be earthed using 8 SWG GI wire. Different rating DTs shall be earthed by different size of MS Flat and detail quantity shall be finalized during detail engineering. 8 SWG GI wire is available in the price schedule. |  |
|  |  | 200kVA ,11/0.433kV, 3ph LT Transformer |  | As per Section Project pg-7, 2.9.2,Super enamel/DPC Aluminium conductor has been considered for HV and LV winding of DTR, Please confirm whether the same is to be considered for higher rating DTR’s like 250KVA,400KVA,630KVA. | DT winding shall be shall be as per cl no 2.9.2.1 of Section Project. Further, in this project higher rating DTR’s like 250KVA,400KVA,630KVA is not in the scope. |  |
|  |  | ‘63 KVA DTR’ Schedule |  | 11kV Stay set are not given in Price Schedule, please confirm whether to consider stay set | 11kV Stay set are not considered for 63kVA,100kVA and 200kVA DTRs. if there is any requirement of Stay Set for DTRs erection, the same may be used from described BOQ of other items. Same shall be paid accordingly. |  |
|  |  | ‘100 KVA DTR’ Schedule |  |  |  |  |
|  |  | ‘200 KVA DTR’ Schedule |  |  |  |  |
|  |  | Danger Board |  | Danger board for LT and 11kV Lines are not given in price schedule, please confirm whether to consider. | Same has been included in Line stringing. |  |
|  |  |  |  | Please refer Awantipora supply schedule Item No. 7, LT Distribution Box (quantity 253 Nos.), as per our understanding this item should be 63 KVA Distribution transformers. | Price schedule’s description has been modified. Refer Errata-1 |  |
|  |  |  |  | Survey quantity of LT AB Cable line is missing in erection schedule. | For replacement / reconductoring work survey has not been considered. Assessment for replacement of pole/structure / Insulator /clamps (wherever applicable) etc. is in the scope of replacement / reconductoring work. |  |
|  |  |  |  | In supply schedule, Pole quantity and stringing of LT AB Cable is not matching. As per our understanding per KMs Pole quantity should be 40 Nos. but as per supply schedule given by you pole quantity is much lower than required quantity, please clear our understanding. | For replacement / reconductoring works, pole quantity has been worked out considering existing pole. The BOQ quantity is in order. |  |
|  | SECTION PROJECT 2.2.13. Reconnection of consumer after reconductoring. |  | DB shall be made of CRCA sheet of thickness not less than 2.5mm and shall have aluminium bus bar…… | Due to our Vendor’s Concern, 2.5 mm CRCA sheets is rarely used in distribution system and manufacturing lead time is more which will affect project completion schedule. So kindly accept sheet thickness 20 S.W.G instead of 2.5 mm. | Refer Amendment-3 to the Bidding Documents. |