| Sr. No. | Clause No. & Reference | Tender Description | Bidders Query | POWERGRID Reply |
| --- | --- | --- | --- | --- |
|  | BDS/ITB 11.3 | The bidders are required to submit hard copy of the documents listed below, in original, along with the Technical Part of their Bid: (i) DD or Online Payment Acknowledgement towards Bidding Document fee of the amount as specified in the in accordance with clause 18 of ITB (ii) Bid Security (in Original), in separate envelope in accordance with clause 18 of ITB, Section-3. (iii) Integrity Pact (in Original) in accordance with provisions of ITB clause (iv) Power of Attorney (v) In case of Bid from Joint Venture, the Joint Venture Agreement & Power of Attorney of Joint Venture Agreement, both in original (vi) Bidders shall also submit Joint Deed of Undertaking by the collaborator along with the bidder/manufacturer, duly signed and stamped on each page in original, if applicable as per Annexure- A (BDS); and (vii) Any other document further specified in the BDS duly signed and stamped on each page. Bidder shall note that no document is required to be submitted as part of Second envelope in Hard Copy. | We understand that only following documents shall be submitted in Originals hard copy within 2 working days after the last date of the bid submission.; (i) DD or Online Payment Acknowledgement towards Bid document (ii) Bid Security (iii) Integrity Pact (in Original) (iv) Power of Attorney (v) In case of Bid from Joint Venture, the Joint Venture Agreement & Power of Attorney of Joint Venture Agreement, both in original (vi) Bidders shall also submit Joint Deed of Undertaking by the collaborator along with the bidder/manufacturer, duly signed and stamped on each page in original, if applicable as per Annexure- A (BDS); and Please confirm. Further we understand that there is no need of submitting completed technical bid in Hard copy except above mentioned. Please Confirm. | As part of hard copy part of bids, bidders are required to submit the documents listed as per ITB/BDS 11.3 |
|  | BDS/ITB 18.1 | A Bid Security shall be required. The amount of the Bid Security shall be as specified in Table A of Section-I (RFB) of the respective package. | Please provide the Bank account details for SFMS; i) Bank Name: ii) Account number: iii) IFSC Code: | Please refer Amendment-2 to the Bidding Documents |
|  | Part 1 - Bidding Procedures and Requirements | 18 (Eighteen) Months from the Effective Date of the Contract | We understand that as per standard SBD of the REC the Contract Time Schedule is 24 Months from the effective date of Contract. Please amend the time schedule to 24 Months instead 18 months based on the above reference. Further the terrain, where the work to executed is very tough and challenging, thus 18 months completion period is insufficient. | The provision of bidding document shall prevail |
|  | Appendix-2, Payment Terms | i. Under the Supply of Plant Contract (Contract Part I), initial interest bearing adjustable Advance of 15% of Contract Price for Contract Part I shall be released in 2 (two)installments each of 7.5% of the Contract Price for Contract Part I. | The clauses are found contradictory. Please clarify whether advance shall be paid on Ex-Work Price component or Contract price (Contract -I). The Contract price is sum of Ex-Works+GST. So please clarify the 15% advance shall be paid including GST or Excluding GST. | The provision of bidding document shall prevail |
|  |  | The bidder must utilize first advance installment of 7.5% of ex-works supply component before requesting for second advance installment. Second installment of 7.5% shall be released on submission of Contractor’s invoice. |  |  |
|  | Appendix-2, Payment Terms | 3. Progressive payments (Erection): 3.1. First Installment (90%) : Ninety percent (90%) payments against Erection contracts shall be paid on erection, testing and commissioning of works and on submission of relevant documents indicated herein under: | There is no clarity about payment of GST@18% while making this payment. Please clarify whether 100% GST is paid while making of 90% Progressive payments (Erection). | The provision of bidding document shall prevail |
|  |  | 8M STP 410 MPA SP 15 | 1) As per "Section project" all structural items shall be Hot-dip galvanized. Whereas, requirement of galvanization of STP is not mentioned anywhere in the TS. Hence please clarify, galvanization for STP poles is required or not. 2) As per "Section project" document-2.9.5.5, it is mentioned thet 25x3mm flat should be used for STP earthing. Please clarify whether 25x3mm flat or GI wire is to be used for STP pole to Spike earthing connection. | 1) As per Clause 2.9.5 of Section -Project of Bidding documents: STP shall be aluminium painted. 2) Earthing of STP shall be done by 25x3 mm flat. Further clause no 2.9.5.3 & 2.9.5.5 of Section Project may also be referred for same. |
|  |  | 9M STP 410 MPA SP 33 |  |  |
|  |  | 11 M STP 410 MPA SP 56 |  |  |
|  |  | SUSPENSION CLAMP SUITABLE FOR LT AB CABLE (3CX120+1CX16+1CX70 SQ.MM) as TS | Kindly clarify the suspension and Tension clamps required for LTAB cable are suitable for Insulated messenger wire type or Bare massenger wire type. As there is ambiguity in the Technical specifications of LTAB cable and accessories respectively. | Refer cl no 2.9.3.1 of section Project. The messenger wire of LT AB cable is bare. Accordingly, the suspension and Tension clamps shall be suitable for bare messenger wire. |
|  |  | TENSION CLAMP SUITABLE FOR LT AB CABLE (3CX120+1X16+1CX70 SQ.MM) as TS |  |  |
|  |  | 20 MM DIA 2500 MM LONG GI ROD TOGETHER WITH FIXING ARRANGEMENT(EXCLUDING GI WIRE REQUIRED FOR EARTHING) AS PER APPROVED DRAWING. | 1) Please classify the earthing is of Treated or Un-treated type. 2. Please clarify whether 25x3mm flat is to be considered along with STP pole in the BoQ/Price schedule. | 1) Earthing of pole, done by 20 mm dia 2500 mm long GI rod, shall be untreated type 2) Refer cl no 2.9.5.5 which specifies that 25x3 mm flat shall be used for earthing of the pole. Cost of same shall be paid as per the quoted price of structure |
|  |  | HARDWARE FITTINGS (1 SET CONSISTS OF ANCHOR PLATE - 1 NO., ANCHOR ROD-1 NO., TURNBUCKLE -1 NO., THIMBLES -2 NOS., GUY GRIPS - 4 NOS.,FASTNERS TO ATTATCH ANCHOR PLATE TO ANCHOR ROD) TO COMPLETE STAY SET TS | We presume that 16mm rod is used for LT Stay set. Please confirm. | Refer the technical specification of GS Stay set attached in the SBD-Part-2 technical specification. As per the same anchor rod shall be 16 mm dia. |
|  |  | 11kV Stay set complete including Hardware as per TS | We presume that 16mm rod is used for 11kV Stay set. Please confirm. Further please specify the size of stay wire. | Refer the technical specification of GS Stay set attached in the SBD-Part-2 technical specification. As per the same anchor rod shall be 16 mm dia. 7/10 SWG wire shall be used as stay wire. |
|  |  | DISC INSULATOR HARDWARE & ACCESSORIES SUITABLE TO 11 KV B&S TYPE, 45KN POLYMER INSULATORS AS PER TS | As per price schedule the insulator hardware is of "B&S type" whereas, in TS it is "T&C type". Please clarify. | The type of insulator hardware shall be as per the price schedule. |
|  |  | Tender Drawings | Please provide Erection arrangement drawings for reference purpose to enable us to verify the BOQ/any additional materials requirements suitable for completion of work. | Bidder shall develop the tender drawing as per the site requirement and technical specification. BOQ for various scope has been specified in the price schedule. Bidder may refer REC construction drawing for reference purpose also. |
|  |  | 8M STP 410 MPA SP 15 | Kindly provide the Technical Specification | As per Clause 2.9.5 of Section -Project of Bidding documents: STP shall be of SP 410 grade as per IS 2713 Part-I. Other constructional part shall be as per the attached technical Specification. |
|  |  | 20 MM DIA 2500 MM LONG GI ROD TOGETHER WITH FIXINGARRANGEMENT(EXCLUDING GI WIRE REQUIRED FOR EARTHING) AS PER APPROVEDDRAWING. | Kindly provide the Technical Specification | For technical specification of 20 MM DIA 2500 MM LONG GI ROD refer Clause 3.3 of Section -Project of Bidding documents which is reproduced below: In case specification of any equipment /material is not included in this volume, the same shall be supplied as per relevant standards. Latest REC specification & Construction Standards may also be referred to. |
|  |  | 1.1 KV, 4 CORE 35 MM2, XLPE CABLE SUITABLE FOR LT AB CABLE(3CX120+1CX16+1CX70 SQ.MM) AS PER TS | Kindly provide Technical Specification of 1.1 KV, 4 CORE 35 MM2, XLPE CABLE | SBD Part-2 Technical Specification may be referred for TS of LT XLPE cable. |
|  |  | 1.1 KV, 1 CORE 25 MM2, XLPE CABLE SUITABLE FOR LT AB CABLE(3CX120+1CX16+1CX70 SQ.MM) AS PER TS | Kindly provide Technical Specification for 1.1 KV, 1 CORE 25 MM2, XLPE CABLE | SBD Part-2 Technical Specification may be referred for TS of LT XLPE cable. |
|  |  | 1.1 KV, 1 CORE 70 MM2, FRLS, PVC CABLE AS TS | Kindly provide Technical Specification | For technical specification of 1.1 kv, 1 core 70 mm2, FRLS, pvc cable refer Clause 3.3 of Section -Project of Bidding documents which is reproduced below: In case specification of any equipment /material is not included in this volume, the same shall be supplied as per relevant standards. Latest REC specification & Construction Standards may also be referred to. |
|  |  | 1.1 KV, 1 CORE 120 MM2, FRLS, PVC CABLE AS TS | Kindly provide Technical Specification | For technical specification of 1.1 kv, 1 core 120 mm2, FRLS, pvc cable refer Clause 3.3 of Section -Project of Bidding documents which is reproduced below: In case specification of any equipment /material is not included in this volume, the same shall be supplied as per relevant standards. Latest REC specification & Construction Standards may also be referred to. |
|  |  | 1.1 KV, 1 CORE 185 MM2, FRLS, PVC CABLE AS TS | Kindly provide Technical Specification | For technical specification of 1.1 kv, 1 core 185 mm2, FRLS, pvc cable refer Clause 3.3 of Section -Project of Bidding documents which is reproduced below: In case specification of any equipment /material is not included in this volume, the same shall be supplied as per relevant standards. Latest REC specification & Construction Standards may also be referred to. |
|  |  | 11KV HG FUSE INCLUDING ALL ACCESSORIES | Kindly provide Technical Specification | For technical specification of 11KV HG FUSE INCLUDING ALL ACCESSORIES refer Clause 3.3 of Section -Project of Bidding documents which is reproduced below: In case specification of any equipment /material is not included in this volume, the same shall be supplied as per relevant standards. Latest REC specification & Construction Standards may also be referred to. |
|  |  | 11 KV 3CX120+1X95 MM2, AB CABLE AS TS | Kindly provide detailed Technical Specification | SBD Part-2 Technical Specification may be referred for TS of HT AB Cable. Further, details are also provided in Clause 2.9.4 of Section -Project of Bidding documents. |
|  |  | HEAT SHRINKABLE OUTDOOR CABLE TERMINATION KIT SUITABLE FOR 11KV 3CX120+1X95 MM2, AB CABLE AS TS | Kindly provide Technical Specification | For technical specification of Heat shrinkable outdoor cable termination kit refer Clause 3.3 of Section -Project of Bidding documents which is reproduced below: In case specification of any equipment /material is not included in this volume, the same shall be supplied as per relevant standards. Latest REC specification & Construction Standards may also be referred to. |
|  |  | MID SPAN STRAIGHT THROUGH JOINTING KIT SUITABLE FOR 11 KV 3CX120+1X95MM2, AB CABLE AS TS | Kindly provide Technical Specification | For technical specification of mid span straight through refer Clause 3.3 of Section -Project of Bidding documents which is reproduced below: In case specification of any equipment /material is not included in this volume, the same shall be supplied as per relevant standards. Latest REC specification & Construction Standards may also be referred to. |
|  |  | SUSPENSION CLAMP SUITABLE FOR 11 KV 3CX9120+1X95 MM2, AB CABLE AS TS | Kindly provide Technical Specification | Our understanding is that bidder is refereeing to suspension clamp of 11KV 3CX120+1X95 MM2 cable. Accordingly technical specification of suspension refer Clause 3.3 of Section -Project of Bidding documents which is reproduced below: In case specification of any equipment /material is not included in this volume, the same shall be supplied as per relevant standards. Latest REC specification & Construction Standards may also be referred to. |
|  |  | TENSION CLAMP SUITABLE FOR 11KV 3CX12+1X95 MM2, AB CABLE AS TS | Kindly provide Technical Specification | Our understanding is that bidder is refereeing to tension clamp of 11KV 3CX120+1X95 MM2 cable. Accordingly, technical specification of tension clamp refer Clause 3.3 of Section -Project of Bidding documents which is reproduced below: In case specification of any equipment /material is not included in this volume, the same shall be supplied as per relevant standards. Latest REC specification & Construction Standards may also be referred to. |
|  | Annexure - A (BDS) | General | Annexure - A (BDS) is not available in TENDER DOCUMENTS Tender ID No. 22766, 22767, 22768. Please provide the same. | Please refer Amendment-1 to the Bidding Documents |
|  |  |  | J&K Power Distribution approved vendors all to RDSS work. Can we consider J&K power distribution approve material for project ? | Bidder shall procure material from POWERGRID’s approved vendors. New vendors shall be approved subject to meeting the technical and other manufacturing requirements. |
|  | Employer Requirement Part - 2 . S.No.13 . 12 | SBD-Section 6 | Drawing for underground cable trench for HT & LT Cables ? Please provide cross section detailed drawing for underground cable trenching work. | Refer cl no 2.2.12.2 of section-project, which specifies the width of the trench. Further, the depth shall be as per IS 1255. |
|  | Employer Requirement Part - 2 . S.No.13 . 2 Page Nos. - 51 , Paragrah 2. | SBD-Section 6 | We need clarity that on tubular pole / RSJ Pole / Rail pole . What is coating method with materail to be considered . As complete section ( 13.2 , Support - Pole ) is not clear | Refer clarification sl no 6 for coating of STP. The coating method shall be finalized during engineering stage |
|  | Employer Requirement Part - 2 . S.No.13 . 2 | Page Nos. - 51 , Paragraph 2 The minimum coating of the Zinc on steel tubular poles or wide parallel Beam supports shall comply with IS:2629 and IS:2633 (with latest amendments). Galvanising shall be checked and tested in accordance with IS:2633 | What type of anti corrosion coating needed on Tubular pole, Galvanization / HDG / Zinc Coating ? etc. | Refer clarification sl no 6 for coating of STP. |
|  | General |  | What is percentage & quantum of subcontractor allowed post award of contract to bidder. ? | The provisions of the Bidding Documents are amply clear. Kindly refer Part-3, Section -7 (Conditions of Contract), Sr. No. 19 (subcontracting) in this regard |
|  | General |  | Can bidder submit BG against EMD with joint name of subcontactor ? Or Can 3rd party BG option available ? | Bidder needs to submit the EMD in the form of BG in the complete name of Bidder. Refer Part-1, Section-3, Sr. No. 18 (Bid Security) in this regard. EMD BG format is given in Form - 3B |
|  | BOQ Line item nos. 132, 211, 238, 382 & 461 | Price schedule Pulwama_Awantipora | 11 KV 3CX120+1X95 MM2, AB CABLE. Is 11kV mentioned in line items are correct? Whether it is 11kV or 1.1 KV? Please clarify? | The referred BOQ is for 11 kV. |
|  | Part – 1 Form 21 , Format of integrity Pact . | Bidding procedures & Requirements | What would be name of utility to be mentioned in format? KPDCL or POWERGRID Energy Services Limited (PESL). Please clarify ? | Revised format of Integrity Pact is given in Amendment-2 to the Bidding Documents. |
|  | SBD Part 2 – SOW, TS Clause No. 11.2 Page nos. 97 | As per clause, The losses in Distribution Transformer should be as per Energy Efficiency Level 1 as specified in IS 1180 (Part-1):2014 and amendment 1,2,3 &4 for all kVA ratings of distribution . | Kindly confirm the required losses as per IS:1180 (Part-1) 2014, latest Amendment No. 4 dtd. 4-Mar-21. Please confirm. | - Refer clause no 2.9.2.5 of section project. Total loss of DTs shall be as per Energy Efficiency Level-1 specified in IS 1180 (Part-1):2021. |
|  | SBD Part 2 - Techncial Specification, TS Clause No. 23 , Page Nos. 109. | As per per clause asking for ‘Not required Cable Box below 200 kVA’ but as per general practice of Jammu & Kashmir state, they required ‘Empty Cable Box’ for all ratings. Please clarify. | As per general practice of Jammu & Kashmir state, they required ‘Empty Cable Box’ for all ratings. Please clarify. | - Refer clause no 2.9.2.6 of section project. LV Cable box shall be provided in transformer above 200 kVA. |
|  | BID DATA SHEET Page no.-57 | SBD Part-1 | In bidding form 4 & form-11, employer name/Utility Name is mentioned Power Grid Corporation of India Ltd . But in Bid Data Sheet it is given Powergrid Energy Service Limited. Please clarify which one is to be used as employer name in bidding form as well as Bank Guarantee. | The procurement related activities in respect of subject package has been entrusted to PESL on the behalf of KPDCL on deposit work basis. POWERGRID Energy Services Limited (PESL) is a wholly owned subsidiary of Power Grid Corporation of India Ltd (POWERGRID). The subject tender has been invited by POWERGRID. As such, all the bid(s) and relevant documents needs to be submitted to POWERGRID in the name of POWERGRID CORPORATION OF INDIA LIMITED, Saudamini, Plot No. 2, Sector - 29, Gurgaon. |
|  | Section-1 | SBD Part-1 | Please clarify in whose favour the EMD BG will be prepared, as "In favour of" is not mentioned in the tender document. And also detailed address ris required. | EMD BG format is given in Form - 3B. It should be in favour of POWERGRID CORPORATION OF INDIA LIMITED, Saudamini, Plot No. 2, Sector - 29, Gurgaon |
|  | Section-4 Page No.-134 | SBD Part-1 | In form-21 (Integrity Pact) stamp duty is not provided. Please provide the same. Also please confirm the stamp duty amount of form-4, form-6 & form-11. | Non-judicial stamp paper of minimum Rupees One Hundred Only (INR 100/-) shall be used for Form -4, Form -6, Form-11 and Form -21. |
|  | Section-4 Page No.-100 | SBD Part-1 | In form-9 Net worth required for FY 20-21 to FY 22-23& MAAT required for FY 18-19 to FY 22-23. FY 22-23 is closed recently and updation of financial report for FY 22-23 is under process. So we can submit the supporing documents for Net worth and MAAT for previous five year i.e. FY 17-18 to FY 21-22. Please allow and confirm the same. | Please refer the revised format of Form -9 attached with Amendment -2 to the Bidding Documents. |
|  |  | Price Schedule | In Powergrid portal, it is found that in item overview, The Total Buy Back Amount (Sl.No. 0008) & Total GST on Buy Back (Sl.No. 0009) is given. But in price schedule BOQ, the same is not provided. Please clarify the same. | Please refer Amendment-2 to the Bidding Documents |
|  |  | Price Schedule | In price schedule it is mentioned that 8M STP 410 MPA SP 15; 9M STP 410 MPA SP 33 & 11 M STP 410 MPA SP 56 poles is required where as in Technical Specification same steel pole designation mentioned 540 SP 28, 540 SP 52, but technical specification for 410MPA designation is not mentioned. Kindly provide technical specification along with GA drawing. | As per Clause 2.9.5 of Section -Project of Bidding documents: STP shall be of SP 410 grade as per IS 2713 Part-I. Other constructional aspect shall be as per the attached technical Specification. GA drawing shall be developed by the contractor during post award stage. |
|  | Technical Specification |  | Kindly provide the technical specification of 11KV HG FUSE INCLUDING ALL ACCESSORIES. | For technical specification of 11KV HG FUSE INCLUDING ALL ACCESSORIES refer Clause 3.3 of Section -Project of Bidding documents which is reproduced below: In case specification of any equipment /material is not included in this volume, the same shall be supplied as per relevant standards. Latest REC specification & Construction Standards may also be referred to. |
|  | Technical Specification |  | Technical Specification of pipe earthing of 40 mm dia, 2.5m long gi pipe (medium grade) for treated earthing is not available. Please provide the same. | For technical specification of 40 mm dia, 2.5m long GI pipe (medium grade) refer Clause 3.3 of Section -Project of Bidding documents which is reproduced below: In case specification of any equipment /material is not included in this volume, the same shall be supplied as per relevant standards. Latest REC specification & Construction Standards may also be referred to. |
|  | Technical Specification |  | Kindly provide the detailed Technical Specification of 11 kv 3cx120+1x95 mm2, ab cable & heat shrinkable outdoor cable termination kit. | Refer clarification sl no 24 & 25. |
|  | Technical Specification |  | Kindly provide the technical specification of 11KV AB cable accessories i.e supention & dead end clamp, eye hook & mid span straight through jointing kit etc. | For technical specification of 11KV AB cable accessories i.e suspension & dead end clamp, eye hook & mid span straight through jointing kit etc refer Clause 3.3 of Section -Project of Bidding documents which is reproduced below: In case specification of any equipment /material is not included in this volume, the same shall be supplied as per relevant standards. Latest REC specification & Construction Standards may also be referred to. |
|  | Technical Specification |  | Kindly Provide the techinical specification of 1.1 kv, 1 core 70 mm2, 95mm2 & 185mm2 FRLS, pvc cable. | Refer clarification sl no 20 for specification of PVC cable. |
|  | Technical Specification |  | Technical Specification of 1.1 kv, 4 core 35 mm2 & 1 CORE 25 MM2 xlpe cable suitable for lt ab cable service main box. | Refer clarification sl no 18 and 19. |
|  | Price Schedule | Sl.No.-49,66,83,100 | As per supply price schedule we understood that LT ab cable work to be executed by using GI clamp along with hook, But practically it is observed that GI clamp along with eyehook is not fixed properly in exiting pole. In this situation AB cable is being fixed with suspention & dead end clamp assembly. Kindly consider suspention & deadend assembly instead of eyehook along with GI clamp in price schedule. | As per Clause 2.2.3 of Section -Project of Bidding documents. The A B Cable shall be strung using suspension/tension clamp, eye hook and structure etc. BOQ are also prepared in line of same. This arrangement is in line of DISCOM’s practice and bidders are requested to use this arrangement only. |
|  |  | Letter Ref.: BEL/EPC-PD/23-24/PGCIL/T-03/01 of Bajaj Electricals | duration for completion of the work vide above tenders is 18 Months. As per our assessment duration is insufficient since this period will have two cycles of extreme weather conditions (of 3months each), considering the initial mobilization and procurement period of approximately 3months, the favourable working period available for erections works will be only 9 months. Considering the quantum of work and working condition it is requested that duration of work should be 30 Months from date of award. | The provision of bidding document shall prevail |
|  | Awantipora_1.1.1(Price Schedule sch-1, Sl.No.7) | Price Schedule_Pulwama_Awantipora | In Supply Price Shedule the item given at Sl.No. 7 is "LT DISTRIBUTION BOX , WITH MCCB FOR INCOMER & SWITCH FUSE UNITS FOR OUTGOING CIRCUITS, SUITABLE FOR 63 KVA DT AS PER TS" the same item is mentioned in Sl.No. 16 also. We understand the given item on Sl.No. 7 is "63KVA, 11/.433KV, 3PH STATION TRANSFORMER WITH CRGO CORE AL WINDING WITH ALL ACCESSORIES". Please clarify our understanding and make correction in BOQ. | Refer Errata-I(Pulwama). Bidder understanding is in order. Further, 63 KVA DT has been referred as STATION TRANSFORMER in BOQ. Bidder understanding is in order. |
|  | Schedule sch-2 | Price Schedule | The erection schedule does not have erection of MSDB for single phase and three phase. Please incorporate the same. | The scope of installation of MSDB i.e. Service distribution box is to be included in scope of installation of LT AB cable. |
|  | Clause no. 2.9.5.5 & Page no. 7 | SBD Part-2_Volume-1 of 2 (Section project-JPDCL/KPDCL) | As per referred clause the earthing of steel tubular pole is done by 25x3 mm flat whereas in price schedule the mention BOQ is given as "20 MM DIA 2500 MM LONG GI ROD TOGETHER WITH FIXING ARRANGEMENT (EXCLUDING GI WIRE REQUIRED FOR EARTHING) AS PER APPROVED DRAWING." which shows the earthing will be done by GI wire. We understand, the earthing is done by GI wire. Please confirm our understanding. | Earthing of STP shall be done by 25x3 mm flat. Further clause no 2.9.5.3 & 2.9.5.5 of Section Project may also be referred for same. |
|  | Clause no. 4.2 & Page no. 7 | SBD Part-2_Volume-1 of 2 (Section project-JPDCL/KPDCL) | As per referred clause, No extra consumption shall be considered for payment for ACSR conductor and Aerial Bunched Cable for construction of lines on account of sag, jumpering, damage, loss, wastage etc. over the measured length of lines. Whereas as per quantity provided in price schedule of supply & erection margin for sag & jumpering is incorporated. We understand that the price schedule will prevail over given SBD clauses. Please confirm the same. | Clause no 4.2 of section project shall prevail over quantity mention in the BOQ regarding extra consumption. |
|  | Clause no. 2.3 & Page no. 4 | SBD Part-2_Volume-1 of 2 (Section project-JPDCL/KPDCL) | In given clause, the dismantled conductor shall be wound in drum (to be provided / arranged by contractor) and other material shall also be properly packed. The drum of supplied conductor/cable may also be used for this purpose. This is practically not possible hence kindly remove this part of clasue which mentioned the contractor need to wound the dismantled conductor in drum. | Provision of Technical specification is in order. |
|  | Clause no. 2.2.8 & Page no. 4 | SBD Part-2_Volume-1 of 2 (Section project-JPDCL/KPDCL) | As per given clause, no concreting will be done for installation of RDSS board. Please clarify our understanding | The RDSS board shall be installed as per specification using concreting. |
|  | Schedule sch-1 | Price Schedule | In LT AB cabling work, the GI wire for earthing is not given in supply Schedule. Please incorporate the same. | LT pole shall be Earthed by 25x3 mm flat. GI wire has been provided in other scope of work i.e DT. Wherever it will be required same shall be used from that scope and shall be paid accordingly. |
|  |  | Technical Specification | Technical Specification of PG Clamp is not available. Please provide the same. | For technical specification of PG Clamp refer Clause 3.3 of Section -Project of Bidding documents which is reproduced below: In case specification of any equipment /material is not included in this volume, the same shall be supplied as per relevant standards. Latest REC specification & Construction Standards may also be referred to |
|  |  | Technical Specification | Technical Specification of 20 MM Dia 2500 MM Long GI Rod is not available. Please provide the same. | For technical specification of 20 MM Dia 2500 MM Long GI Rod refer Clause 3.3 of Section -Project of Bidding documents which is reproduced below: In case specification of any equipment /material is not included in this volume, the same shall be supplied as per relevant standards. Latest REC specification & Construction Standards may also be referred to. |
|  |  |  | Kindly extend the completion period from 18 months to 24 months as due to extreme weather conditions there completion schedule of 18 months is less. hence kindly extend the work completion | The provision of bidding document shall prevail |
|  |  |  | -kindly provide contact details of the concerned person who can give brief details regarding site visit. | ##### Following executive may be contacted for site visit for the project ##### Sh S K Chowan, , Sr GM (Mobile No – 9419156687) may be contacted for JPDCL projects. ##### Md Shafat Ahmad Wani, Sr GM (Mobile No – 9797550099) may be contacted for KPDCL Projects. |
|  |  |  | Technical specification of following items are no given with bid documents, a) 8 M STP 410 MPA AP 15 b) 9 M STP 410 MPA AP 33 c) 11 M STP 410 MPA AP 5 | Refer clarification sl no 16 for specification of STP. |
|  | Location Details | SBD | Proposed Locations of work to be executed, details not available in the SBD Kindly Provide for the same to understand the exact requirement. | Bidder are advised to visit the site. Further, Refer clarification sl no 64 for detail of concerned executive. |
|  | Bid Capacity | BDS | As per the REC SBD it is mentioned as N: Years prescribed for work completion under tender (but in order to standardize the same, a value of [3] may be taken). REC corrigendum No: Version-02 Dated: 11.07.2022 Enclosed. As per Present SBD it is mentioned that, N: Years prescribed for work completion under tender i.e. 1.5 years. Request you to modify as per REC SBD i.e. N=3 Years. | Please refer Amendment-2 to the Bidding Documents. |
|  | Erection BOQ Item No. 12 & 13 | BOO | As per the Erection Schedule Stringing of ACSR Weasel conductor Unit of Measurement mentioned in KM. please confirm whether it is a Km or CKM. | Erection of 11 kV line on ACSR conductor has been envisaged for single circuit 3-phase 3 wire system. So km of line and CKM shall be same. |
|  | DTR | BOQ | Technical specifications for 250 KVA,400 KVA & 630 KVA DTR's not available in bid documents kindly provide the same. | Refer clause no 2.9.1 of section – project for specific detail. other section may be referred from the attached technical specification |
|  | LT Distribution Box. | BOQ | Technical specifications for 400 KVA & 630 KVA LT Distribution Box not available in bid document kindly provide the same. | Refer clause no 2.9.1 of section – project for specific detail. other constructional detail may be referred from the attached technical specification |
|  | Polymer Insulators | BOO | Technical specifications for Polymer Pin & Disc insulator not available in bid document kindly provide the same. | Chapter 11 kV/22 kV/33 kV Composite Insulators of SBD Part-2 Technical Specification may be referred for TS of polymer pin and disc insulator. |
|  |  | GTP, Type test & MAL | Manufacturer authorization letters, GTP Drawings and Type test reports shall submit along with technical tender or not? Please confirm. | The provisions of the Bidding Documents are amply clear. Documents to be submitted along with soft copy part of the bid/ hard copy part of the bid are clearly stated. |
|  |  | Time completion | Request you to Amendment the Time for Completion of the works is:24(Twenty four) Months from the Effective Date of the Contract. | The provision of bidding document shall prevail. |
|  | clause | Project closure | We understand PESL/PGCIL will take over the completed portion of the work immediate after the charging of the same please confirm. | The completed work shall be handed over to owner (JPDCL/KPDCL) . |
|  |  | General | If any bidder is quoting more than one project, please clarify that technical and financial qualification criteria will be evaluated individually or cumulatively. | Qualification Requirements(QR) of a particular package are clearly stated. The bidder should meet the QR of the subject package in order to be eligible for the subject package. |
|  |  | General | We presume that all the required Statutory Approval & charges/ Fee like road restoration, railway crossing clearance etc. are at your scope or Reimbursement to the contractor please confirm. | Refer cl no 2.2.12.3 of section project for restoration changes. As per the same the Road restoration charges shall be borne by the contractor and shall be included in total bid price Refer cl no 2.9.1.2 for State Electrical Inspectorate’s inspection charge. As per the same the cost is to be included in the bid cost Other charges, if any shall be paid/reimbursed as per the provision of the contract. |
|  |  | General | Requested to release EMD BG's after finalization of price Bid without linking it with the issue of LOA to L1 bidder. | The provisions of the Bidding Documents shall remain unchanged. Please refer Part-1, Section-3, Sr. No. 18 (Bid Security) in this regard. |
|  |  | General | we presume that the required ROW, Forrest clearance and its statutory payment will be born by the PESL /PGCIL please confirm. | These charges shall be born by contractor as per the provision of the SBD. |
|  |  | General | We assumed that after completion of project the left over/ balance material will be taken over by the PESL /PGCIL please confirm. | Regarding balance material refer cl no 5.4 of section project which is reproduced below: “Any item supplied by the contractor but not erected shall be taken back by the contractor and payment made by Employer, if any, shall be recovered at LOA rate.” |
|  |  |  | Devaluation of Materials where to hand over, whether it is nearest Department store or location of store details of PESL /PGCIL please provide. | Refer section project. The designated stores shall be finalized after discussion with DISCOM and site in charge. |
|  |  |  | Line Clearance, shutdown schedules will be provided well in advance for mobilization of MEN and material as per the schedule and to minimize the Ideal manpower and machinery, please confirm minimum shut down time available per day and per week. | This shall be finalised during execution in consultation with the contractor and the DISCOM in line of L-2 schedule/level of gang mobilization. |
|  |  |  | We presume that, if additional material is required for completion of work, which are not covered in the Price schedule/ BOQ will be paid extra as on additional item please confirm. | We do not envisage any additional material presently. If any additional material required during execution which is not specified in the Price schedule/ BOQ same shall be paid extra. |
|  | 1TB 18.1BDS | A Bid Security shall be required. The amount of the Bid Security shall be. Package; Amount. Loss Reduction work under RDSS in Pulwama District; 3,13,50,000. Loss Reduction work under ROSS in Anantnag District; 4,35,02,000. Loss Reduction work under ROSS in Shopian and Kulgam District; 3,53,02,000. | Kindly confirm the Bank Guarantee (BG) mode of EMD submission is acceptable or not? As per RBI guidelines, BG Should be transmitting through the SFMS platform after issuance of BG in original. Hence, it is requested to provide the Bank details for the preparation of EMD in Bank Guarantee mode. Kindly confirm the BG Favour of whom? Please provide us the value of Non-Judicial Stamp Paper of Bank Guarantee to be issued | Please refer Amendment-2 to the Bidding Documents. |
|  | Section• 1: Request for Bids Notice/Notice Inviting Tender, Cost of documents/ tender fee | The non-refundable fee towards the cost of Bidding Documents shall be Rs.25,000/· [Note: The non-refundable Tender fee is towards the cost of bidding documents, the cost is common for all the packages under a single Bidding Documents and bidders are not required to pay the amount package wise. Bidders, on their own discretion, may choose to participate in any and all packages covered under Bidding Documents] | 1. Please clarify that the tender document fee will be paid through online mode or DD mode, | Please refer Amendment-2 to the Bidding Documents. |
|  | 1TB 11.3 BDS | The bidders are required to submit hard copy of the documents listed below, in original, along with the Technical Part of their Bid: (i) DD or Online Payment Acknowledgement towards Bidding Document fee of the amount as specified in the in accordance with clause 18 of 1TB | 2. Please also provide the details of beneficiary name for favouring of bank Demand Draft | Please refer Amendment-2 to the Bidding Documents |
|  | Section • 1: Request for Bids Notice/Notice Inviting Tender, Cost of documents/ tender fee | The Time for Completion of the works is: 18 (Eighteen) Months from the Effective Date of the Contract | As per our previous project work experience in Kashmir, the completion period of the works execution of this works i.e. 18 months is very short, in view of Geographical and Climatic condition of Kashmir, hence you are requested to amend the work completion clause from 18 months to 30 months for the smooth execution of the project. | The provision of bidding document shall prevail. |
|  | Bidding Forms Section 4 & ITB-11 of BDS | Form-1: Bidder shall fill this form 1 in the MS Excel Format namely 'First Envelope and Bid Forms' Attached herewith | Please provide us 'First Envelope and Bid Forms' in MS EXCEL Format | Please refer Amendment-2 to the Bidding Documents |
|  | Technical Specification | 12. Terms of Payment 12.5 <The Employer shall be eligible for 1.50% of rebate of invoice value (excluding GST) in the event it makes payment to the Contractor within 10 days of receipt of invoices complete in all respect.> | Please clarify that, the 1.5% of rebate of invoice value (excluding GST) will be applicable value i.e. 60% of payable value or 100% bill value of Invoice. We understand that 1.5% (excluding GST) should be applicable on payable value only, because we are not getting payment balance 40% amount on that time | The provision of bidding document shall prevail |
|  | GCC 27.8, SBD - Part- 3: Conditions and Contract Forms | The extension of Defect Liability in aggregate, shall not exceed 24 months | Please clarify Performance Bank Guarantee is require for extended defect liability period or not. | The provisions of the Bidding Documents are amply clear |
|  | 12 Cable length of AB Cable TS under Part 3 | The cable shall be supplied in continuous lengths of 500m with 5% tolerance. | Reputed manufacturer is overloaded due to ongoing RDSS projects and for this reason there are space constraints in their factory and delay in avaibality of wood. Hence our request to finalise the standard length of drum will be 1000 Meter+/- 5% | Other standard length shall be finalised during detail engineering. |