| Sr. No | Clause No. | Existing Specification | Clarification / Change in Specification requested | Remarks / Reason | Clarification |
| --- | --- | --- | --- | --- | --- |
| 1 | Volume II, Section VII B, Annexure A, clause 17 | Bending Test on Composite Core (as Type Test) Bending test on composite core before stranding shall be performed as per ASTM B987/B987M-17 on composite core samples taken from composite core at conductor manufacturing unit before stranding of conductor. Alternatively, supplier may carry out bending test on composite core before stranding on the samples taken at the core manufacturing unit, from the same reel being supplied to conductor manufacturer subject to proper traceability of the same at the conductor manufacturers works. Bending test on composite core shall also be performed as per ASTM B987/ B987M-17 on composite core samples taken from stranded conductor. For test after stranding the diameter of cylindrical mandrel shall be as following: For high strength grade composite core: 60 times the diameter of composite core. For Extra high strength grade composite core: 70 times the diameter of composite core. | Please add following, Bending test on composite core before stranding shall be performed as per ASTM B987/B987M-20 on composite core samples taken from composite core at conductor manufacturing unit before stranding of conductor. Alternatively, supplier may carry out bending test on composite core before stranding on the samples taken at the core manufacturing unit, from the same reel being supplied to conductor manufacturer subject to proper traceability of the same at the conductor manufacturers works. Or Bending test on composite core shall also be performed as per ASTM B987/ B987M-17 on composite core samples taken from stranded conductor. For test after stranding the diameter of cylindrical mandrel shall be as following: For high strength grade composite core: 60 times the diameter of composite core. For Extra high strength grade composite core: 70 times the diameter of composite core. | Please add latest amendment of ASTM B987. Also add or so that either bidder can perform tests before stranding or after stranding. Current procedure is written in such a way that bidder needs to perform bending test before and after stranding. | Bidder to follow technical Specification. |
| 2 | Price schedule Schedule – 3 | Service BOQ is not available in price schedule |  | Please amend the service BOQ | Kindly refer Amendment - I |
| 3 | Supply BOQ Schedule – 1&2 | Also confirmation required on below line item as line is 132KV but hardware of 220KV is mentioned in sr.no.5 5; Supply of Hardwa fittings (Excl. clamp); DTS -220KV W/O TEN CLMP SINGLE PANTHER; SET; 12. |  | Also, confirmation required on below line item as line is 132KV but hardware of 220KV is mentioned in sr.no.5 | Kindly refer Amendment - I |
| 4 | BPS | -- | We are unable to find out GTP's for HTLS Conductor, Hardware Fittings & Accessories and other items in the Tender documents. | We are unable to find out GTP's for HTLS Conductor, Hardware Fittings & Accessories and other items in the Tender documents. | Kindly refer Section-VII B, Section-VI A and Section-VI B of Technical Specification for Technical Requirement for HTLS conductor, hardware fittings & accessories. Further, for formats for furnishing GTP of conductor, HW and accessories kindly refer amendment-I |