Bhadla-II & Fatehgarh-II S/S

| SN | Clause reference | Provision in Specification | Bidder’s Query | POWERGRID Reply |
| --- | --- | --- | --- | --- |
|  | "Vol – II Section: STATCOM Stations" General | Number of switching for MSC & MSR is not defined. | Number of switching events of the MSC/MSR is not defined within any document. Hence, Switching stresses may be calculated as per IEC 60871-Part1. | Noted. However, It should be possible for the user to set the same in setting parameterisation. |
|  | "Vol – II Section: STATCOM Stations" Chapter 6.1.8, page 16 | STATCOM station response shall be such that the change in measured system voltage to small disturbance should reach 90% of the desired total change within 30ms of the initiating a 5% step change of voltage reference. | "Bidder clarifies that these response times are achievable/applicable only to the STATCOM branches. | Confirmed, the response corresponds to the control of STATCOM branches during dynamic support. |
|  | Section: STATCOM Stations Rev 02 "Chapter 8.6, page 41 and Chapter 8.5, page 41" | "The MSC Components shall be designed with the aim to achieve operation according to the overall performance requirements of the STATCOM Station. And The MSR Components shall be designed with the aim to achieve operation according to the overall performance requirements of the STATCOM Station." | "The bidder clarifies that the dynamic performance requirements of the STATCOM station shall be met using STATCOM Branches only whereas steady state performances shall be met using MSCs & MSRs. In this way the overall performance requirements of the STATCOM STATION are met. Kindly confirm this understanding. Alternatively please elaborate ""Overall performance Requirements"" with respect to individual elements (e.g. MSCs. MSRs & STATCOM)." | Confirmed, Overall performance requirement of MSC and MSR are amply clarified in the Technical specification. |
|  | "Vol ll Section Project" Cl. 12 "Association and Training of Employer personals Cl. 12.1 Scope " | "The Contractor shall submit ............................ Wherever the Employer intends to have Employers personnel stationed at the Contractor's office/works, the association / training of these engineers shall constitute 1 man months and at Employers office/site shall constitute 2 man months for which price shall be quoted in the BPS. The broad break up of man months for Training shall be as follows: a) System engineering design and equipment Specification: 2 man months b) Operation and maintenance: 2 man months c) Operation and maintenance hands on Training at site:2 man months (1 man month = 20 man days) " | "As per 3rd paragraph of referred CL. number, training is required for 3 man months (1 man month in Contractor’s office/works + 2 man months in Employer’s office/site), however as per next para where breakup is specified, training is required for 6 man months as mentioned in the next clause (4 man months in Contractor’s office/works + 2 man months in Employer’s site). Please clarify duration of trainings to be considered by bidder under subject project." | The mentioned clause 12.1 has no reference to training for 4 man months. It specifies total training duration of 6 man months only. Bidder to quote as per requirement of Bidding document. |
|  | "Vol ll Section Project" Cl. 12 Association and Training of Employer personals | General | "Bidder understand that that the training requirements mentioned at various sections / clauses in tender documents e.g. Section-Project (Annexure-II, sr. 30), Section-SAS Rev04 (Cl. 12.0), etc. are deemed to be included in the total number of man months mentioned under Cl. 12.1 of Section-Project." | Confirmed. |
|  | "Vol ll Section Project" Annexure – III Annexure-IV Details of System Studies to be performed | "1. GENERAL ….......................... The Contractor may note that the following list is only indicative and if any other studies, calculations etc. are required the same shall have to be done by contractor without any extra charges to the employer. " | "Predefined studies in tender documents cover a large spectrum of cases according to the needs of the customer. In case other extra studies are needed by the customer they should be discussed separately. If additional studies other that what is envisaged in the Technical Specification are required at project stage the same shall be discussed with the successful bidder. The time schedule and commercial terms shall be mutually agreed. Please Confirm." | The provisions of the Technical Specification are amply clear and bidder shall follow the same. |
|  | "Vol II Section STATCOM" Cl. 8.1.5.t STATCOM Valve Cooling system | Replacement of certain cooling equipment (e.g., pumps, fans, cooler unit etc.), if defective, should be possible while the cooling system still operates. | "Bidder clarifies that replacement of cooler unit (Cooler Bank / cooler module) shall not be possible while STATCOM is in service at full load, as only 10% redundancy in cooler modules (Fan units) has been specified. However replacement of cooler units shall be possible at reduced load. Please clarify requirement." | Bidder to follow the requirements of technical specification. It basically envisages that it should be possible to replace certain cooling equipment without the outage of complete cooling system. |
|  | "Section-STATCOM Station, Rev02 8.9.1 (o) last paragraph (page 47 of 62) General Requirements & S. No. 1 of Amendment-III Amendment-II" | In addition to above, Model Technical Specification “Technical Specification: Section-Transformer (Up to 400kV Class)” shall be referred for the Coupling Transformer. | "The clause 8.9 of Section-STATCOM Station, Rev02 specifies ""The Coupling Transformer shall be designed based on the design of similar type of Transformer which has been tested successfully for dynamic short circuit type test."". However; as per S. No. 88 of SPECIFIC REQUIREMENT’S (Section- Project) C/ENGG/SPEC/SEC-PROJECT/SPECIFIC REQUIREMENT REV NO 02 and as per clause 3.13.1 of Technical Specification: Section -Transformer (Up to 400kV Class), the bidder shall have carried out short circuit test for 315 MVA auto transformer. Kindly clarify if a short circuit test on a similar transformer (2-winding transformer) as defined in IEC is acceptable or the short circuit test on a 315 MVA (or higher MVA rating) auto transformer is acceptable." | The requirement of dynamic Short circuit type test on coupling transformer shall be as per Section STATCOM Station Rev-02. Short circuit tests on similar type 2 -winding transformer shall be acceptable as per IEC. Requirement mentioned at S. No. 88 of SPECIFIC REQUIREMENT (Section- Project) C/ENGG/SPEC/ SEC-PROJECT/SPECIFIC REQUIREMENT REV NO 02 and at clause 3.13.1 of Technical Specification: Section -Transformer (Up to 400kV Class) is applicable for 315MVA or above rating auto transformer which is not envisaged in the present scope, hence shall not be referred. |
|  | "Vol II Section STATCOM Project" Annexure-X Cl. 24.24.c Other STATCOM Station MV Equipments | Cooling System | "It is understood that cooling system manufacturer has to select the sub vendors for major subcomponents e.g. pumps, outdoor coolers etc. based on the condition that they should be in successful operation of at least 2 years for similar applications (FACTS or HVDC). Please confirm." | Technical requirement for cooling system has been specified in the specification. Regarding sub component, bidder’s understanding is acceptable however, these shall be finalized during detail engineering. |
|  | "Vol II Section STATCOM" "Cl. 8.1.2 Cl. 2.1" "Semiconductor Switches Relevant Standard" | "Cl. 8.1.2 - The semiconductor switch shall meet the requirements of IEC 60747 except where otherwise specified herein. Cl. 2.1 - 1) Voltage sourced converter (VSC) valves for STATCOM - Standard IEC 60747" | IEC 60747 is generally not applicable for the proposed multi-level configuration. However, some definitions used by the OEMs of the semiconductor switch are based on IEC 60747. Kindly confirm this understanding. | Bidder’s understanding is generally in order. |
|  | "Vol II Section STATCOM" Cl. 6.1 (i) STATCOM Station Ratings | The bidder shall assume the negative sequence voltage of 1% at rated short circuit level and provide control to reduce this unbalance. | "Bidder understands that the specified negative sequence is only valid for the STATCOM because a single phase operation of MSRs and MSCs is not possible (only three phase operation). Kindly confirm this understanding." | Bidder’s understanding is generally in order. |
|  | "Vol II Section Project" Cl. 7.0.(II) Availability Spares | The Contractor shall supply the spare parts required to meet the specified guaranteed availability and shall include such spare parts in the scope of supply. The detailed lists of spare parts to meet the guaranteed reliability & availability requirements shall be part of the contract documents. | "The bidder doesn't envisage supply of any separate availability spares because the guaranteed availability is being met considering the mandatory spares specified in TS. As per specification, the availability period will start six months after trial operation. The mandatory spares will be delivered at site before scheduled completion date (i.e. final commissioning). During the availability monitoring period, in the event of failure of any component leading to forced outage (complete or partial); the failed component will be replaced from the stock of mandatory spares available at site. At the same time, a new spare will be ordered and delivered to site by Contractor in order to replenish the stock of mandatory spares. Hence, there shall be no need to keep any additional availability spares at site. Kindly confirm your acceptance." | Noted. However, any outage during availability & reliability guarantee period due to unavailability of spares shall be attributable to the contractors account. |
|  | Clarification No. - I (Technical) dated 01/06/2020 Sr. No. 58 | "With reference clarification Employer confirmed that All the necessary Clearance for site land ,land acquisition, forest clearances, Right of way for the substation location as well as approach road from the nearest State Highway or Village Road etc shall be in PGCIL s' scope of work. Our scope of work is restricted for construction of STATCOM station boundary fencing & all works within the said boundary only." | "Bidder further wants to clarify that : 1. Handing over of encumbrance free levelled land within one month of Notice of award (NoA). 2. Approach road shall be provided with in one month of Notice of award (NoA). 3. Here approach road means road suitable for general transport of construction material and STATCOM STATION Equipments. Please confirm." | 1. Noted. Levelled land for STATCOM Stations already exists at site. 2 & 3. Noted. Approach road upto Site main entrance already exist at site. Laying of Road inside site for present scope shall be finalized during detailed engineering. |
|  | "Vol II Section Project" "General" FACILITIES TO BE PROVIDED BY THE EMPLOYER | "I - Employer shall make available the auxiliary power…............................" | "Bidder understands that :- 1. ""Single point in Sub-Station"" refers to ""Single Point in STATCOM Sub Station"". 2. Employer shall provide auxiliary power with in one month of Notice of award (NOA). Please confirm." | 1. Single point in Sub-station refers to point in Switchyard as per availability. 2. Noted. |
|  | "Vol II Section Project" FACILITIES TO BE PROVIDED BY THE EMPLOYER | Employer shall make available the auxiliary power supplies on chargeable basis at a single point in the Sub-station. The prevailing energy rates of the state shall be applicable. All further distribution from the same for construction and permanent auxiliary supply shall be made by the contractor. However, in case of failure of power due to any unavoidable circumstances, the contractor shall make his own necessary arrangements like diesel generator sets etc. at his own cost so that progress of work is not affected and Employer shall in no case be responsible for any delay in works because of non-availability of power. | "1) Employer is requested to confirm the voltage level of the auxiliary power source e.g. 33kV / 11kV or 415V, 3-phase, 50 Hz along with the maximum variation in voltage and frequency. 2) In order to ensure fair and equitable costing consideration between all Bidders, it is requested that Employer confirms the energy rates at which the auxiliary power will be charged (in case Bidder opts to take Employer's auxiliary power connection)." | 1. Auxiliary voltage available at site for construction shall be as per Cl. 15.1 of Section: GTR. 2. The prevailing energy rates of the state utility at the time of execution of work shall be applicable. Bidder shall quote accordingly. |
|  | "Vol II Section Project" Annexure-III, Sr. no. 9 Capacitance, Inductance & Resistance Meter | The equipment should be Table top and should be able to carry out measurement of R, L &C of valve components. | The specified meter is not part of the Bidder's standard tools for convertor because as the OEM we do not recommend/require measurement of R, L, C of our valve components for O&M as the same is not necessary. Nevertheless, the bidder will supply the Capacitance Inductance and resistance meter as per specification and it can be used by Employer for their own application other than the converter. | Noted. Bidder to Quote as per Bidding document. |
|  | "Vol II Section STATCOM" Cl. 6.8.11 Guaranteed of Failure Rate - AC Power Capacitor | "Till the expiry of guarantee period, all replacement for failed units shall be supplied by the Contractor free of cost." | "Bidder understands that till the expiry of Defect Liability Period, all replacement for failed units shall be supplied by the Contractor free of cost in accordance with the terms & conditions mentioned in General Conditions of Contract (GCC). Please confirm." | Confirmed. |
|  | "Vol II Section Project" 2.8 System Engineering and Studies | "The contractor .................................................. The Employer shall have right to observe and participate in the studies performed as a part of the Contract and shall have access to all data necessary for complete understanding of the purpose of such studies as well as the validity of the results. The Contractor shall give the Employer at least thirty days prior notice before commencement of the above studies. " | "The participation is understood to mean review & verification of design results only; and will be done after the studies have been completed by the Contractor. There will be trainings about the Contractor STATCOM technology, the software packages and the models provided by Contractor for the customer to get a complete understanding. Therefore, please note that the Employer's study team will only be involved in the discussion on the study and cannot participate in the studies during project execution as the design and engineering process remains the intellectual property of Contractor. Please confirm." | It is clarified that the requirement is envisaged to provide access, if required, to employer for complete understanding of the studies and the validity of the results. |
|  | "Vol II Section Project" Annexure-IV Details of System Studies to be performed | 1. GENERAL….......................... The Contractor may note that the following list is only indicative and if any other studies, calculations etc. are required the same shall have to be done by contractor without any extra charges to the employer. | "Predefined studies in tender documents cover a large spectrum of cases according to the needs of the customer. In case other extra studies are needed by the customer they should be discussed separately. If additional studies other that what is envisaged in the Technical Specification are required at project stage the same shall be discussed with the successful bidder. The time schedule and commercial terms shall be mutually agreed. Please Confirm." | The provisions of the Technical Specification are amply clear and bidder shall follow the same. |
|  | "Vol II Section STATCOM" Cl 8.1 STATCOM Unit / Branch | In general the STATCOM units shall equally share the load however under contingency condition it should be possible to run the units with unequal load. | "Unequal loading is not foreseen during operation. Load will be shared symmetrically between active STATCOM branches by the control system. However, uneven load sharing can be controlled manually through HMI, if required for testing purpose. Please confirm bidder’s understanding is correct." | Bidder’s understanding is generally in order. |
|  | "Vol II Section STATCOM" Cl. 6.1.4 (d) Over Voltage Strategy | The contractor shall demonstrate to the satisfaction of the Employer that STATCOM Station will not excite ferro-resonance and sub-synchronous oscillation in the AC system. | "Contractor will demonstrate through simulation with available data that STATCOM station will not excite ferro resonance and sub synchronous oscillation in the AC system. No site testing is foreseen. Kindly confirm this understanding. " | Confirmed. |