## 205 BCU
220kV ICT incomer
Sr. No. | Voltage Level | Feeder Name | NAME ( BAY-205 ICT )
|  |  | SIGNAL DESCRIPTION | Information type | Telegram address | Position | EVENT | ALARM
BINARY INPUT (Double Point)
1 | 200KV | 400kV ICT | CB B-PH POSITION | DP | B205_BCUCB_1P_POSITION$RSLEDGAPC1$ST$DPS2 | stVal | √
2 |  |  | CB R-PH POSITION | DP | B205_BCUCB_1P_POSITION$RSLEDGAPC1$ST$DPS | stVal | √
3 |  |  | CB Y-PH POSITION | DP | B205_BCUCB_1P_POSITION$RSLEDGAPC1$ST$DPS1 | stVal | √
4 |  |  | CB POSITION | DP | B205_BCUCB$CSWI1$ST$Pos:2 | stVal | √
5 |  |  | 89A POSITION | DP | B205_BCU89A$CSWI1$ST$Pos:2 | stVal | √
6 |  |  | 89AE POSITION | DP | B205_BCU89AE$CSWI1$ST$Pos:2 | stVal | √
7 |  |  | 89B POSITION | DP | B205_BCU89B$CSWI1$ST$Pos:2 | stVal | √
8 |  |  | 89C POSITION | DP | B205_BCU89C$CSWI1$ST$Pos:2 | stVal | √
9 |  |  | 89T POSITION | DP | B205_BCU89T$CSWI1$ST$Pos:2 | stVal | √
10 |  |  | 89TE1 POSITION | DP | B205_BCU89TE1$CSWI1$ST$Pos:2 | stVal | √
11 |  |  | 89TE2 POSITION | DP | B205_BCU89TE2$CSWI1$ST$Pos:2 | stVal | √
12
13 |  |  | BINARY INPUT (Single Point)
14
15 |  |  | LED RESET | SP | B205_BCUApplication$LLN0$ST$LEDRs:2 | stVal | √
16 |  |  | BCU MODE | SP | B205_BCUApplication$LLN0$ST$LocKey | stVal | √
17 |  |  | 86A TRIP RELAY RESET | SP | B205_BCUUD1$RSLEDGAPC1$ST$SPC:2 | stVal | √ | √
18 |  |  | 86A TRIP RELAY FAULTY | SP | B205_BCUUD1$RSLEDGAPC1$ST$SPS12 | stVal | √ | √
19 |  |  | 86A TRIP RELAY OPTD | SP | B205_BCUUD1$RSLEDGAPC1$ST$SPS11 | stVal | √ | √
20 |  |  | 86B TRIP RELAY RESET | SP | B205_BCUUD1$RSLEDGAPC1$ST$SPC1:2 | stVal | √ | √
21 |  |  | 86B TRIP RELAY FAULTY | SP | B205_BCUUD1$RSLEDGAPC1$ST$SPS24 | stVal | √ | √
22 |  |  | 86B TRIP RELAY OPTD | SP | B205_BCUUD1$RSLEDGAPC1$ST$SPS23 | stVal | √ | √
23 |  |  | 87B RELAY FAULTY | SP | B205_BCUUD1$RSLEDGAPC1$ST$SPS14 | stVal | √ | √
24 |  |  | AC KIOSK HEAT FIRE DETECTION | SP | B205_BCUUD1$RSLEDGAPC1$ST$SPS19 | stVal | √ | √
25 |  |  | AC KIOSK SMOKE DETECTION | SP | B205_BCUUD1$RSLEDGAPC1$ST$SPS18 | stVal | √ | √
26 |  |  | CB AC SUPPLY FAIL | SP | B205_BCUUD1$RSLEDGAPC1$ST$SPS9 | stVal | √ | √
27 |  |  | AC-1 ON | SP | B205_BCUUD1$RSLEDGAPC1$ST$SPS20 | stVal | √
28 |  |  | AC-1/2 POWER FAIL | SP | B205_BCUUD1$RSLEDGAPC1$ST$SPS22 | stVal | √ | √
29 |  |  | AC-2 ON | SP | B205_BCUUD1$RSLEDGAPC1$ST$SPS21 | stVal | √
30 |  |  | BAY IN NORMAL MODE | SP | B205_BCUUD1$RSLEDGAPC1$ST$SPS26 | stVal | √
31 |  |  | BAY IN TRANSFER MODE | SP | B205_BCUUD1$RSLEDGAPC1$ST$SPS25 | stVal | √
32 |  |  | BUS-1 VT DESELECTED | SP | B205_BCUUD1$RSLEDGAPC1$ST$SPS35 | stVal | √
33 |  |  | BUS-1 VT SELECTED | SP | B205_BCUUD1$RSLEDGAPC1$ST$SPS34 | stVal | √
34 |  |  | BUS-2 VT DESELECTED | SP | B205_BCUUD1$RSLEDGAPC1$ST$SPS28 | stVal | √
35 |  |  | BUS-2 VT SELECTED | SP | B205_BCUUD1$RSLEDGAPC1$ST$SPS27 | stVal | √
36 |  |  | CB DC-1 SUPPLY FAIL | SP | B205_BCUUD1$RSLEDGAPC1$ST$SPS5 | stVal | √
37 |  |  | CB DC-2 SUPPLY FAIL | SP | B205_BCUUD1$RSLEDGAPC1$ST$SPS6 | stVal | √
38 |  |  | CB IN LOCAL MODE | SP | B205_BCUUD1$RSLEDGAPC1$ST$SPS7 | stVal | √
39 |  |  | EMERGENCY/MANUAL CB CLOSE | SP | B205_BCUUD1$RSLEDGAPC1$ST$SPS16 | stVal | √ | √
40 |  |  | EMERGENCY/MANUAL CB TRIP | SP | B205_BCUUD1$RSLEDGAPC1$ST$SPS15 | stVal | √ | √
41 |  |  | CB POLE DISCREPANCY OPTD | SP | B205_BCUUD1$RSLEDGAPC1$ST$SPS1 | stVal | √ | √
42 |  |  | CB REMOTE POSITION SELECTED | SP | B205_BCUUD1$RSLEDGAPC1$ST$SPS8 | stVal | √ | √
43 |  |  | CB SF6 LOCKOUT | SP | B205_BCUUD1$RSLEDGAPC1$ST$SPS3 | stVal | √ | √
44 |  |  | CB SF6 GAS PRESSURE REFILL LOW ALARM | SP | B205_BCUUD1$RSLEDGAPC1$ST$SPS2 | stVal | √ | √
45 |  |  | CB SPRING CHARGED | SP | B205_BCUUD1$RSLEDGAPC1$ST$SPS | stVal | √ | √
46 |  |  | DC SUPPLY-1 FAIL | SP | B205_BCUUD1$RSLEDGAPC1$ST$SPS13 | stVal | √ | √
47 |  |  | CB TC-1 R-PHASE FAULTY |  |  |  | √ | √
48 |  |  | CB TC-1 Y-PHASE FAULTY |  |  |  | √ | √
49 |  |  | CB TC-1 B-PHASE FAULTY | SP |  | stVal | √ | √
50 |  |  | CB TC-2 R-PHASE FAULTY | SP |  | stVal | √ | √
51 |  |  | CB TC-2 Y-PHASE FAULTY | SP |  | stVal | √ | √
52 |  |  | CB TC-2 B-PHASE FAULTY | SP |  | stVal | √ | √
53 |  |  | NORMAL MODE | SP | B205_BCUUD1$RSLEDGAPC1$ST$SPS33 | stVal | √
54 |  |  | TRANSFER MODE | SP | B205_BCUUD1$RSLEDGAPC1$ST$SPS32 | stVal | √
55 |  |  | GOOSE RECEIPT FAIL/TROUBLE | SP | B205_BCUUD1$RSLEDGAPC1$ST$SPS35 | stVal | √ | √
56 |  |  | TIME SYNCHRONISATION ERROR | SP | B205_BCUApplication$LMTS0$ST$TmSynErr | stVal | √ | √
57
58 |  |  | MEASUREMENT
59
60 |  |  | POWER FACTOR | ME_FL | B205_BCUVI3p1_OperationalValues$PPRE_MMXU1$MX$TotPF:1 | mag$f
61 |  |  | FREQUENCY | ME_FL | B205_BCUVI3p1_OperationalValues$PPRE_MMXU1$MX$Hz:1 | mag$f
62 |  |  | ACTIVE POWER | ME_FL | B205_BCUVI3p1_OperationalValues$PPRE_MMXU1$MX$TotW:1 | mag$f
63 |  |  | REACTIVE POWER | ME_FL | B205_BCUVI3p1_OperationalValues$PPRE_MMXU1$MX$TotVAr:1 | mag$f
64 |  |  | APPARENT POWER | ME_FL | B205_BCUVI3p1_OperationalValues$PPRE_MMXU1$MX$TotVA:1 | mag$f
65 |  |  | I-R-PH CURRENT | ME_FL | B205_BCUVI3p1_OperationalValues$RPRE_MMXU1$MX$A:1 | phsA$cVal$mag$f
66 |  |  | I-Y-PH CURRENT | ME_FL | B205_BCUVI3p1_OperationalValues$RPRE_MMXU1$MX$A:1 | phsB$cVal$mag$f
67 |  |  | I-B-PH CURRENT | ME_FL | B205_BCUVI3p1_OperationalValues$RPRE_MMXU1$MX$A:1 | phsC$cVal$mag$f
68 |  |  | R-Y VOLTAGE | ME_FL | B205_BCUVI3p1_OperationalValues$RPRE_MMXU1$MX$PPV:1 | phsAB$cVal$mag$f
69 |  |  | Y-B VOLTAGE | ME_FL | B205_BCUVI3p1_OperationalValues$RPRE_MMXU1$MX$PPV:1 | phsBC$cVal$mag$f
70 |  |  | B-R VOLYAGE | ME_FL | B205_BCUVI3p1_OperationalValues$RPRE_MMXU1$MX$PPV:1 | phsCA$cVal$mag$f
71
72 |  |  | CB B-PH COUNTER | ME_I | B205_BCUUD3$RSLEDGAPC1$ST$INS2 | stVal
73 |  |  | CB R-PH COUNTER | ME_I | B205_BCUUD3$RSLEDGAPC1$ST$INS | stVal
74 |  |  | CB Y-PH COUNTER | ME_I | B205_BCUUD3$RSLEDGAPC1$ST$INS1 | stVal
75
76 |  |  | COMMANDS
77
78 |  |  | 89A CONTROL | DC | B205_BCU89A$CSWI1$CO$Pos:8 | Oper$ctlVal | √
79 |  |  | 89AE CONTROL | DC | B205_BCU89AE$CSWI1$CO$Pos:8 | Oper$ctlVal | √
80 |  |  | 89B CONTROL | DC | B205_BCU89B$CSWI1$CO$Pos:8 | Oper$ctlVal | √
81 |  |  | 89C CONTROL | DC | B205_BCU89C$CSWI1$CO$Pos:8 | Oper$ctlVal | √
82 |  |  | 89T CONTROL | DC | B205_BCU89T$CSWI1$CO$Pos:8 | Oper$ctlVal | √
83 |  |  | 89TE1 CONTROL | DC | B205_BCU89TE1$CSWI1$CO$Pos:8 | Oper$ctlVal | √
84 |  |  | 89TE2 CONTROL | DC | B205_BCU89TE2$CSWI1$CO$Pos:8 | Oper$ctlVal | √
85 |  |  | CB CONTROL | DC | B205_BCUCB$CSWI1$CO$Pos:8 | Oper$ctlVal | √
86 |  |  | TRANSFER/NORMALCONTROL | DC | B205_BCUDc8$CSWI1$CO$Pos:8 | Oper$ctlVal | √
87 |  |  | 86A TRIP RELAY RESET COMMAND | SC | B205_BCUUD1$RSLEDGAPC1$CO$SPC:8 | Oper$ctlVal | √
88 |  |  | 86B TRIP RELAY RESET COMMAND | SC | B205_BCUUD1$RSLEDGAPC1$CO$SPC1:8 | Oper$ctlVal | √
89 |  |  | CB MANUAL TRIP
90 |  |  | CB MANUAL CLOSE
91 |  |  | BUSBAR OPERATED
92 |  |  | BCU IN LOCAL/REMOTE
93 |  |  | SETTINGS CHANGED |  |  |  |  | √
94 |  |  | RELAY IN TEST MODE |  |  |  |  | √
Note: 1. Additional signal for CB Trouble, etc as per scheme & As per standard DR signal requirement the input not considered in HMI signal list 2. 5 Nos of GGIO signal need to be configured as SPARE till the SCADA Database 3. The Logical Device LD is for reference only and vendors may use the same as per their own stndardized way, however the logical nodes used are to be used only as specified. 4. If the logical nodes have been made more specific under the same logical node class by adding prefixes, same can be used as per the application. For example, PDIFF has been specified for all types of differential functions, but if some vendor, under the same logical node class, made the function more specific by adding prefix HZD1PDIFF for 1 phase High Impedance Differential function & T3WPDIFF for 3 winding Low Impedance differential protection, same may be used.