## LEGEND
Sheet Ref. | IED MODEL | IED SYMBOLIC NAME(TYPICAL) | APPLICATION | IED NAME IN SCD | Additional Remarks
1 | 6MD66 | BCU | BCU FOR BUS REACTOR | STNM4XXBCU | BCU is for each bay so 4XX refers to Bay
2 | 7SA522 | BR 21R | BACKUP IMPEDANCE RELAY FOR BUS REACTOR | STNM4XXBRBU | Bay No. 4XX will be always the main bay number for the BUS REACTOR feeder. BR for BUS REACTOR and LR for LINE REACTOR.
3 | 7SJ80 | BR 64.2R | REF RELAY FOR BUS REACTOR | STNM4XXBRREF | Bay No. 4XX will be always the main bay number for the BUS REACTOR feeder. BR for BUS REACTOR and LR for LINE REACTOR.
4 | 7UT | BR 87R | DIFFERENTIAL RELAY FOR BUS REACTOR | STNM4XXBRDIF | Bay No. 4XX will be always the main bay number for the BUS REACTOR feeder. BR for BUS REACTOR and LR for LINE REACTOR.
NOTE 1: The characters "STNM" stand for Substation Name with maximum 4 characters, this code will be given by POWERGRID for each project.
NOTE 2: The characters "4XX" stand for Bay name, example if the bay no 401 then same has to be implemented like STNM401BCU

## BCU
400kV BUS REACTOR (BCU)
Sr. No. | Voltage Level | Feeder Name | Source | NAME ( BAY-403 BUS REACTOR )
|  |  |  | Signal Decription | INFORMATION TYPE | Telegram Address | POSITION | Event | Alarm
BINARY INPUT (Double Point)
1 | 400kV | 400kV BUS REACTOR | BCU | CB R-PH POSITION | DP | B403_BCUCBB$XCBR1$ST$Pos:2 | stVal | √
2 |  |  |  | CB Y-PH POSITION | DP | B403_BCUCBR$XCBR1$ST$Pos:2 | stVal | √
3 |  |  |  | CB B-PH POSITION | DP | B403_BCUCBY$XCBR1$ST$Pos:2 | stVal | √
4 |  |  |  | CB POSITION | DP | B403_BCUCB$CSWI1$ST$Pos:2 | stVal | √
5 |  |  |  | 89AE POSITION | DP | B403_BCU89AE$CSWI3$ST$Pos:2 | stVal | √
6 |  |  |  | 89AE2 POSITION | DP | B403_BCU89AE2$CSWI6$ST$Pos:2 | stVal | √
7 |  |  |  | 89BE1 POSITION | DP | B403_BCU89BE1$CSWI5$ST$Pos:2 | stVal | √
8 |  |  |  | 89BE POSITION | DP | B403_BCU89BE$CSWI7$ST$Pos:2 | stVal | √
9 |  |  |  | 89RE-B POSITION | DP | B403_BCU89REB$CSWI9$ST$Pos:2 | stVal | √
10 |  |  |  | 89RE POSITION | DP | B403_BCU89RE$CSWI9$ST$Pos:2 | stVal | √
11 |  |  |  | 89RE-Y POSITION | DP | B403_BCU89REY$CSWI9$ST$Pos:2 | stVal | √
12 |  |  |  | 89A POSITION | DP | B403_BCU89A$CSWI2$ST$Pos:2 | stVal | √
13 |  |  |  | 89B POSITION | DP | B403_BCU89B$CSWI4$ST$Pos:2 | stVal | √
14 |  |  |  | 89R-B POSITION | DP | B403_BCU89RB$CSWI8$ST$Pos:2 | stVal | √
15 |  |  |  | 89R POSITION | DP | B403_BCU89R$CSWI8$ST$Pos:2 | stVal | √
16 |  |  |  | 89R-Y POSITION | DP | B403_BCU89RY$CSWI8$ST$Pos:2 | stVal | √
17
18
19 |  |  |  | BINARY INPUT (Single Point)
20
21 |  |  |  | AUX POWER FAIL | SP | B403_BCUApplication$LPHD0$ST$AuxPwrFail | stVal | √ | √
22 |  |  |  | TIME SYNCHRONISATION ERROR | SP | B403_BCUApplication$LMTS0$ST$TmSynErr | stVal | √ | √
23 |  |  |  | BCU MODE | SP | B403_BCUApplication$LLN0$ST$LocKey | stVal | √ | √
24 |  |  |  | CB SF6 GAS PRESSURE REFILL LOW ALARM | SP | B403_BCUApplication$USER1$ST$SPS | stVal | √ | √
25 |  |  |  | CB SF6 GAS PRESSURE LOCKOUT | SP | B403_BCUApplication$USER1$ST$SPS1 | stVal | √ | √
26 |  |  |  | 89A POLE DESCREPENCY | SP | B403_BCUApplication$USER3$ST$SPS3 | stVal | √ | √
27 |  |  |  | 89B POLE DESCREPENCY | SP | B403_BCUApplication$USER3$ST$SPS4 | stVal | √ | √
28 |  |  |  | CB DC SUPPLY-1/2 FAIL | SP | B403_BCUApplication$USER3$ST$SPS1 | stVal | √
29 |  |  |  | CB SPRING CHARGED | SP | B403_BCUApplication$USER3$ST$SPS2 | stVal | √
30 |  |  |  | CB SF6 GAS PRESSURE LOCKOUT | SP | B403_BCUApplication$USER3$ST$SPS | stVal | √ | √
31 |  |  |  | EMERGENCY/MANUAL CB TRIP | SP | B403_BCUApplication$USER6$ST$SPS | stVal | √ | √
32 |  |  |  | PSD DEVICE HEALTHY | SP | B403_BCUApplication$USER6$ST$SPS19 | stVal | √
33 |  |  |  | PSD DEVICE IN SERVICE | SP | B403_BCUApplication$USER6$ST$SPS20 | stVal | √
34 |  |  |  | WTI ALARM | SP | B403_BCUApplication$USER6$ST$SPS23 | stVal | √ | √
35 |  |  |  | OTI ALARM | SP | B403_BCUApplication$USER6$ST$SPS24 | stVal | √ | √
36 |  |  |  | PSD ALARM | SP | B403_BCUApplication$USER6$ST$SPS21 | stVal | √ | √
37 |  |  |  | PSD SYNCH DATA ERROR | SP | B403_BCUApplication$USER6$ST$SPS22 | stVal | √ | √
38 |  |  |  | SURGE ARRESTER B-PH | SP | B403_BCUApplication$USER6$ST$SPS18 | stVal | √
39 |  |  |  | SURGE ARRESTER R-PH | SP | B403_BCUApplication$USER6$ST$SPS16 | stVal | √
40 |  |  |  | SURGE ARRESTER Y-PH | SP | B403_BCUApplication$USER6$ST$SPS17 | stVal | √
41 |  |  |  | 86A TRIP RELAY SUPERVISION | SP | B403_BCUApplication$USER5$ST$SPS2 | stVal | √ | √
42 |  |  |  | 86A TRIP RELAY OPERATED | SP | B403_BCUApplication$USER5$ST$SPS1 | stVal | √ | √
43 |  |  |  | 86B TRIP RELAY SUPERVISION | SP | B403_BCUApplication$USER5$ST$SPS5 | stVal | √ | √
44 |  |  |  | 86B TRIP RELAY OPERATED | SP | B403_BCUApplication$USER5$ST$SPS4 | stVal | √ | √
45 |  |  |  | CB TC-1 FAULTY | SP | B403_BCUApplication$USER5$ST$SPS | stVal | √ | √
46 |  |  |  | CB TC-2 FAULTY | SP | B403_BCUApplication$USER5$ST$SPS3 | stVal | √ | √
47 |  |  |  | CB POLE DISCREPANCY | SP | B403_BCUApplication$USER2$ST$SPS1 | stVal | √ | √
48 |  |  |  | CB SF6 GAS PRESSURE REFILL LOW ALARM | SP | B403_BCUApplication$USER2$ST$SPS | stVal | √ | √
49 |  |  |  | BUS-1 VT RESET | SP | B403_BCUApplication$USER7$ST$SPS1 | stVal | √
50 |  |  |  | BUS-2 VT RESET | SP | B403_BCUApplication$USER7$ST$SPS3 | stVal | √
51 |  |  |  | LINE VT RESET | SP | B403_BCUApplication$USER7$ST$SPS5 | stVal | √
52 |  |  |  | BUS-1 VT SELECTED | SP | B403_BCUApplication$USER7$ST$SPS | stVal | √
53 |  |  |  | BUS-2 VT SELECTED | SP | B403_BCUApplication$USER7$ST$SPS2 | stVal | √
54 |  |  |  | ICT LV VT SELECTED | SP | B403_BCUApplication$USER7$ST$SPS4 | stVal | √
55 |  |  |  | CB READY | SP | B403_BCUCB$XCBR1$ST$Rdy | stVal | √
56 |  |  |  | CB POSITION NO SYNC | SP | B403_BCUCB$CSWI1$ST$Pos | noSync | √
57 |  |  |  | GAS PRESSURE LOW ALARM-1 GC401-1 Y-PH | SP | B403_BCUApplication$USER5$ST$SPS10 | stVal | √ | √
58 |  |  |  | GAS PRESSURE LOW ALARM -1 GC401-1 B-PH | SP | B403_BCUApplication$USER5$ST$SPS11 | stVal | √ | √
59 |  |  |  | GAS PRESSURE LOW ALARM-1 GC401-2 R-PH | SP | B403_BCUApplication$USER5$ST$SPS12 | stVal | √ | √
60 |  |  |  | GAS PRESSURE LOW ALARM -1 GC401-2 Y-PH | SP | B403_BCUApplication$USER5$ST$SPS13 | stVal | √ | √
61 | 400kV | 400kV BUS REACTOR | BCU | GAS PRESSURE LOW ALARM-1 GC401-2 B-PH | SP | B403_BCUApplication$USER5$ST$SPS14 | stVal | √ | √
62 |  |  |  | GAS PRESSURE LOW ALARM-1 GC401-3 R-PH | SP | B403_BCUApplication$USER5$ST$SPS15 | stVal | √ | √
63 |  |  |  | GAS PRESSURE LOW ALARM -1 GC401-3 Y-PH | SP | B403_BCUApplication$USER5$ST$SPS16 | stVal | √ | √
64 |  |  |  | GAS PRESSURE LOW ALARM-1 GC401-3 B-PH | SP | B403_BCUApplication$USER5$ST$SPS17 | stVal | √ | √
65 |  |  |  | GAS PRESSURE LOW ALARM-1 GC401-4 R-PH | SP | B403_BCUApplication$USER5$ST$SPS18 | stVal | √ | √
66 |  |  |  | GAS PRESSURE LOW ALARM -1 GC401-4 Y-PH | SP | B403_BCUApplication$USER5$ST$SPS19 | stVal | √ | √
67 |  |  |  | GAS PRESSURE LOW ALARM-1 GC401-4 B-PH | SP | B403_BCUApplication$USER5$ST$SPS20 | stVal | √ | √
68 |  |  |  | GAS PRESSURE LOW ALARM-1 GC401-5 R-PH | SP | B403_BCUApplication$USER5$ST$SPS21 | stVal | √ | √
69 |  |  |  | GAS PRESSURE LOW ALARM -1 GC401-5 Y-PH | SP | B403_BCUApplication$USER5$ST$SPS22 | stVal | √ | √
70 |  |  |  | GAS PRESSURE LOW ALARM-1 GC401-5 B-PH | SP | B403_BCUApplication$USER5$ST$SPS23 | stVal | √ | √
71 |  |  |  | GAS PRESSURE LOW ALARM-1 GC401-6 R-PH | SP | B403_BCUApplication$USER5$ST$SPS24 | stVal | √ | √
72 |  |  |  | GAS PRESSURE LOW ALARM -1 GC401-6 Y-PH | SP | B403_BCUApplication$USER5$ST$SPS25 | stVal | √ | √
73 |  |  |  | GAS PRESSURE LOW ALARM-1 GC401-6 B-PH | SP | B403_BCUApplication$USER5$ST$SPS26 | stVal | √ | √
74 |  |  |  | GAS PRESSURE LOW ALARM-1 GC401-7 R-PH | SP | B403_BCUApplication$USER5$ST$SPS27 | stVal | √ | √
75 |  |  |  | GAS PRESSURE LOW ALARM -1 GC401-7 Y-PH | SP | B403_BCUApplication$USER5$ST$SPS28 | stVal | √ | √
76 |  |  |  | GAS PRESSURE LOW ALARM-1 GC401-7 B-PH | SP | B403_BCUApplication$USER5$ST$SPS29 | stVal | √ | √
77 |  |  |  | GAS PRESSURE LOW ALARM-2 GC401-1 | SP | B403_BCUApplication$USER5$ST$SPS30 | stVal | √ | √
78 |  |  |  | GAS PRESSURE LOW ALARM-2 GC401-2 | SP | B403_BCUApplication$USER5$ST$SPS31 | stVal | √ | √
79 |  |  |  | GAS PRESSURE LOW ALARM-2 GC401-3 | SP | B403_BCUApplication$USER5$ST$SPS32 | stVal | √ | √
80 |  |  |  | GAS PRESSURE LOW ALARM-2 GC401-4 | SP | B403_BCUApplication$USER5$ST$SPS33 | stVal | √ | √
81 |  |  |  | GAS PRESSURE LOW ALARM-2 GC401-5 | SP | B403_BCUApplication$USER5$ST$SPS34 | stVal | √ | √
82 |  |  |  | GAS PRESSURE LOW ALARM-2 GC401-6 | SP | B403_BCUApplication$USER5$ST$SPS35 | stVal | √ | √
83 |  |  |  | GAS PRESSURE LOW ALARM-2 GC401-7 | SP | B403_BCUApplication$USER5$ST$SPS36 | stVal | √ | √
84 |  |  |  | GAS COMPARTMENT ZONE TRIP GC401-52 | SP | B403_BCUApplication$USER5$ST$SPS37 | stVal | √ | √
85 |  |  |  | GAS COMPARTMENT ZONE TRIP GC401-1 | SP | B403_BCUApplication$USER5$ST$SPS38 | stVal | √ | √
86 |  |  |  | GAS COMPARTMENT ZONE TRIP GC401-2 | SP | B403_BCUApplication$USER5$ST$SPS39 | stVal | √ | √
87 |  |  |  | GAS COMPARTMENT ZONE TRIP GC401-3 | SP | B403_BCUApplication$USER5$ST$SPS40 | stVal | √ | √
88 |  |  |  | GAS COMPARTMENT ZONE TRIP GC401-4 | SP | B403_BCUApplication$USER5$ST$SPS41 | stVal | √ | √
89 |  |  |  | GAS COMPARTMENT ZONE TRIP GC401-5 | SP | B403_BCUApplication$USER5$ST$SPS42 | stVal | √ | √
90 |  |  |  | GAS COMPARTMENT ZONE TRIP GC401-6 | SP | B403_BCUApplication$USER5$ST$SPS43 | stVal | √ | √
91 |  |  |  | GAS COMPARTMENT ZONE TRIP GC401-7 | SP | B403_BCUApplication$USER5$ST$SPS44 | stVal | √ | √
92 |  |  |  | GAS PRESSURE LOW ALARM-1 GC401-8 R-PH | SP | B403_BCUApplication$USER7$ST$SPS26 | stVal | √ | √
93 |  |  |  | GAS PRESSURE LOW ALARM -1 GC401-8 Y-PH | SP | B403_BCUApplication$USER7$ST$SPS27 | stVal | √ | √
94 |  |  |  | GAS PRESSURE LOW ALARM-1 GC401-8 B-PH | SP | B403_BCUApplication$USER7$ST$SPS28 | stVal | √ | √
95 |  |  |  | GAS PRESSURE LOW ALARM-2 GC401-8 | SP | B403_BCUApplication$USER7$ST$SPS29 | stVal | √ | √
96 |  |  |  | DEVICE HEALTHY | SP | B403_BCUApplication$LPHD0$ST$PhyHealth:0 | stVal:1 | √
97 |  |  |  | GOOSE RECEIPT FAIL/TROUBLE | SP | B403_BCUApplication$USER7$ST$SPS30 | stVal | √ | √
98 |  |  |  | CB CLOSE INTERLOCK | SP | B403_BCUCB$CILO1$ST$EnaCls | stVal | √
99 |  |  |  | 89AE OPEN INTERLOCK | SP | B403_BCU89AE$CILO3$ST$EnaOpn | stVal | √
100 |  |  |  | 89AE2 OPEN INTERLOCK | SP | B403_BCU89AE2$CILO6$ST$EnaOpn | stVal | √
101 |  |  |  | 89BE OPEN INTERLOCK | SP | B403_BCU89BE$CILO5$ST$EnaOpn | stVal | √
102 |  |  |  | 89BE2 OPEN INTERLOCK | SP | B403_BCU89BE2$CILO7$ST$EnaOpn | stVal | √
103 |  |  |  | 89BRE OPEN INTERLOCK | SP | B403_BCU89RE$CILO9$ST$EnaOpn | stVal | √
104 |  |  |  | 89RE-R-PH OPEN INTERLOCK | SP | B403_BCU89RER$CILO9$ST$EnaOpn | stVal | √
105 |  |  |  | 89RE-Y-PH OPEN INTERLOCK | SP | B403_BCU89REY$CILO9$ST$EnaOpn | stVal | √
106 |  |  |  | 89A OPEN INTERLOCK | SP | B403_BCU89A$CILO2$ST$EnaOpn | stVal | √
107 |  |  |  | 89B OPEN INTERLOCK | SP | B403_BCU89B$CILO4$ST$EnaOpn | stVal | √
108 |  |  |  | 89BR OPEN INTERLOCK | SP | B403_BCU89R$CILO8$ST$EnaOpn | stVal | √
109 |  |  |  | 89R-R-PH OPEN INTERLOCK | SP | B403_BCU89RR$CILO8$ST$EnaOpn | stVal | √
110 |  |  |  | 89R-Y-PH OPEN INTERLOCK | SP | B403_BCU89RY$CILO8$ST$EnaOpn | stVal | √
111 |  |  |  | DC -1/2 SUPPLY HEALTHY
112 |  |  |  | 89BR POLE DISCREPANCY ALARM
113 |  |  |  | CT SF6 ALARM
114 |  |  |  | CT SF6 LOCKOUT
115 |  |  |  | PSD IN POSITION
116 |  |  |  | PSD OUT POSITION
117 |  |  |  | PSD OPENING PROBLEM
118 |  |  |  | PSD CLOSING PROBLEM
119
120
121 |  |  |  | MEASUREMENT
122
123 |  |  |  | POWER FACTOR | ME_FL | B403_BCUVI3p1_OperationalValues$PPRE_MMXU1$MX$TotPF:1 | mag$f
124 |  |  |  | FREQUENCY | ME_FL | B403_BCUVI3p1_OperationalValues$PPRE_MMXU1$MX$Hz:1 | mag$f
125 |  |  |  | ACTIVE POWER | ME_FL | B403_BCUVI3p1_OperationalValues$PPRE_MMXU1$MX$TotW:1 | mag$f
126 |  |  |  | REACTIVE POWER | ME_FL | B403_BCUVI3p1_OperationalValues$PPRE_MMXU1$MX$TotVAr:1 | mag$f
127 |  |  |  | APPARENT POWER | ME_FL | B403_BCUVI3p1_OperationalValues$PPRE_MMXU1$MX$TotVA:1 | mag$f
128 |  |  |  | I-R-PH CURRENT | ME_FL | B403_BCUVI3p1_OperationalValues$RPRE_MMXU1$MX$A:1 | phsA$cVal$mag$f
129 |  |  |  | I-Y-PH CURRENT | ME_FL | B403_BCUVI3p1_OperationalValues$RPRE_MMXU1$MX$A:1 | phsB$cVal$mag$f
130 |  |  |  | I-B-PH CURRENT | ME_FL | B403_BCUVI3p1_OperationalValues$RPRE_MMXU1$MX$A:1 | phsC$cVal$mag$f
131 |  |  |  | R-Y VOLTAGE | ME_FL | B403_BCUVI3p1_OperationalValues$RPRE_MMXU1$MX$PPV:1 | phsAB$cVal$mag$f
132 |  |  |  | Y-B VOLTAGE | ME_FL | B403_BCUVI3p1_OperationalValues$RPRE_MMXU1$MX$PPV:1 | phsBC$cVal$mag$f
133 |  |  |  | B-R VOLYAGE | ME_FL | B403_BCUVI3p1_OperationalValues$RPRE_MMXU1$MX$PPV:1 | phsCA$cVal$mag$f
134
135 |  |  |  | CB-B-PH COUNTER | ME_I | B403_BCUCBB$XCBR1$ST$OpCnt | stVal
136 |  |  |  | CB-R-PH COUNTER | ME_I | B403_BCUCBR$XCBR1$ST$OpCnt | stVal
137 |  |  |  | CB-Y-PH COUNTER | ME_I | B403_BCUCBY$XCBR1$ST$OpCnt | stVal
138
139 |  |  |  | COMMANDS
140
141 |  |  |  | 89BR CONTROL | DC | B403_BCU89BR$CSWI8$CO$Pos:8 | Oper$ctlVal | √
142 |  |  |  | 89B CONTROL | DC | B403_BCU89B$CSWI4$CO$Pos:8 | Oper$ctlVal | √
143 |  |  |  | 89A CONTROL | DC | B403_BCU89A$CSWI2$CO$Pos:8 | Oper$ctlVal | √
144 |  |  |  | 89BRE CONTROL | DC | B403_BCU89RE$CSWI9$CO$Pos:8 | Oper$ctlVal | √
145 |  |  |  | 89BE CONTROL | DC | B403_BCU89BE$CSWI7$CO$Pos:8 | Oper$ctlVal | √
146 |  |  |  | 89AE CONTROL | DC | B403_BCU89AE$CSWI3$CO$Pos:8 | Oper$ctlVal | √
147 |  |  |  | CB CONTROL | DC | B403_BCUCB$CSWI1$CO$Pos:8 | Oper$ctlVal | √
148 |  |  |  | CB CONTROL NO SYNC | SC | B403_BCUCB$CSWI1$CO$Pos | Oper$noSync | √
149 |  |  |  | 86B TRIP RELAY RESET COMMAND | SC | B403_BCUApplication$USER2$CO$SPC1:8 | Oper$ctlVal | √
150 |  |  |  | 86A TRIP RELAY RESET COMMAND | SC | B403_BCUApplication$USER2$CO$SPC:8 | Oper$ctlVal | √
151 |  |  |  | PSD SWITCH IN CONTROL | SC
152 |  |  |  | PSD SWITCH OUT CONTROL | SC
153 |  |  | SETTINGS CHANGED |  |  |  | √ | √
154 |  |  | RELAY IN TEST MODE |  |  |  | √ | √
Note: 1. Additional signal for CB Trouble, etc as per scheme & As per standard DR signal requirement the input not considered in HMI signal list 2. 5 Nos of GGIO signal need to be configured as SPARE till the SCADA Database 3. The Logical Device LD is for reference only and vendors may use the same as per their own stndardized way, however the logical nodes used are to be used only as specified. 4. If the logical nodes have been made more specific under the same logical node class by adding prefixes, same can be used as per the application. For example, PDIFF has been specified for all types of differential functions, but if some vendor, under the same logical node class, made the function more specific by adding prefix HZD1PDIFF for 1 phase High Impedance Differential function & T3WPDIFF for 3 winding Low Impedance differential protection, same may be used.

## 403 BR 64.2R
400kV BR
Sr. No. | Voltage Level | Feeder Name | NAME ( BAY-403 BUS REACTOR )
|  |  | Signal Decription | INFORMATION TYPE | Telegram Address | POSITION | Event | Alarm
BINARY INPUT (Single Point)
1 | 400kV | 400kV BR | RESET LED | SP | B403_64RCTRL$LLN0$ST$LEDRs:2 | stVal | √
2 |  |  | BCU UNHEALTHY | SP | B403_64RCTRL$GGIO1$ST$SPCSO1:0 | stVal | √ | √
3 |  |  | GOOSE RECEIPT FAIL/TROUBLE | SP | B403_64RCTRL$GGIO1$ST$SPCSO2:0 | stVal | √ | √
4 |  |  | DC SUPPLY-1 FAIL | SP | B403_64RCTRL$GGIO1$ST$SPCSO3:0 | stVal | √ | √
5 |  |  | PRV-1 TRIP | SP | B403_64RCTRL$GGIO1$ST$SPCSO4:0 | stVal | √ | √
6 |  |  | TIME SYNCHRONISATION ERROR | SP | B403_64REXT$pdGGIO2$ST$SPCSO4:0 | stVal | √ | √
7 |  |  | REF STAGE 1 TRIP | SP | B403_64RPROT$PTOC16$ST$Op | general | √ | √
8 |  |  | REF STAGE 1 PICKUP | SP | B403_64RPROT$PTOC16$ST$Str | general | √
9 |  |  | REF STAGE 2 TRIP | SP | B403_64RPROT$PTOC17$ST$Op | general | √ | √
10 |  |  | REF STAGE 2 PICKUP | SP | B403_64RPROT$PTOC17$ST$Str | general | √
11 |  |  | GENERAL TRIP | SP | B403_64RPROT$PTRC1$ST$Tr | general | √ | √
12 |  |  | GENERAL PICKUP | SP | B403_64RPROT$PTRC1$ST$Str | general | √
13 |  |  | COMMUNICATION STATUS | SP |  | stVal:1 | √ | √
16 |  |  | WTI TRIP | SP | B403_64RCTRL$GGIO1$ST$SPCSO6:0 | stVal | √ | √
17 |  |  | MAIN TANK BUCHHOLZ A TRIP | SP | B403_64RCTRL$GGIO1$ST$SPCSO7:0 | stVal | √ | √
18 |  |  | PNRV ALARM | SP | B403C_64RCTRL$BIBOGGIO1$ST$SPCSO5:0 | stVal | √ | √
19 |  |  | MAIN TANK BUCHHOLZ A ALARM
20 |  |  | WTI ALARM
21 |  |  | OTI TRIP
22 |  |  | SETTINGS CHANGED |  |  |  | √ | √
23 |  |  | RELAY IN TEST MODE |  |  |  | √ | √
Note: 1. Additional signal for CB Trouble, etc as per scheme & As per standard DR signal requirement the input not considered in HMI signal list 2. 5 Nos of GGIO signal need to be configured as SPARE till the SCADA Database 3. The Logical Device LD is for reference only and vendors may use the same as per their own stndardized way, however the logical nodes used are to be used only as specified. 4. If the logical nodes have been made more specific under the same logical node class by adding prefixes, same can be used as per the application. For example, PDIFF has been specified for all types of differential functions, but if some vendor, under the same logical node class, made the function more specific by adding prefix HZD1PDIFF for 1 phase High Impedance Differential function & T3WPDIFF for 3 winding Low Impedance differential protection, same may be used.

## 403 BR 21R
400kV BR
Sr. No. | Voltage Level | Feeder Name | NAME ( BAY-403 BUS REACTOR )
|  |  | Signal Decription | INFORMATION TYPE | Telegram Address | POSITION | Event | Alarm
BINARY INPUT (Single Point)
1 | 400kV | 400kV BR | RESET LED | SP | B403_21RCTRL$LLN0$ST$LEDRs:2 | stVal | √
2 |  |  | 87.1R RELAY UNHEALTHY | SP | B403_21RCTRL$GGIO1$ST$SPCSO1:0 | stVal | √ | √
3 |  |  | 64.2R RELAY UNHEALTHY | SP | B403_21RCTRL$GGIO1$ST$SPCSO2:0 | stVal | √ | √
4 |  |  | GOOSE RECEIPT FAIL/TROUBLE | SP | B403_21RCTRL$GGIO1$ST$SPCSO3:0 | stVal | √ | √
5 |  |  | MOG ALARM | SP | B403_21RCTRL$GGIO1$ST$SPCSO4:0 | stVal | √ | √
6 |  |  | MAIN TANK BUCHHOLZ ALARM | SP | B403_21RCTRL$GGIO1$ST$SPCSO5:0 | stVal | √ | √
7 |  |  | OTI TRIP | SP | B403_21RCTRL$GGIO1$ST$SPCSO6:0 | stVal | √ | √
8 |  |  | TIME SYNCHRONISATION ERROR | SP | B403_21REXT$pdGGIO2$ST$SPCSO4:0 | stVal | √ | √
9 |  |  | VT FUSE FAILURE | SP | B403_21REXT$pdGGIO3$ST$SPCSO41:0 | stVal | √ | √
10 |  |  | BROKEN CONDUCTOR | SP | B403_21REXT$pdGGIO4$ST$SPCSO3:0 | stVal | √ | √
11 |  |  | BACKUP IMPEDENCE ACTIVE | SP | B403_21REXT$pdGGIO58$ST$SPCSO5:0 | stVal | √ | √
12 |  |  | BACKUP IMPEDENCE BLOCKED | SP | B403_21REXT$pdGGIO58$ST$SPCSO4:0 | stVal | √
13 |  |  | BACKUP IMPEDENCE ZONE-1 PICKUP | SP | B403_21RPROT$PDIS1$ST$Str | general | √
14 |  |  | BACKUP IMPEDENCE ZONE-1 TRIP | SP | B403_21RPROT$PDIS1$ST$Op | general | √ | √
15 |  |  | BACKUP IMPEDENCE R-PH TRIP | SP | B403_21RPROT$PDIS1$ST$Op | phsA | √ | √
16 |  |  | BACKUP IMPEDENCE Y-PH TRIP | SP | B403_21RPROT$PDIS1$ST$Op | phsB | √ | √
17 |  |  | BACKUP IMPEDENCE B-PH TRIP | SP | B403_21RPROT$PDIS1$ST$Op | phsC | √ | √
18 |  |  | FAULT DISTANCE | ME_FL | B403_21RPROT$RFLO1$MX$FltDiskm:0 | mag$f
19 |  |  | GENERAL TRIP | SP | B403_21RPROT$PTRC1$ST$Tr | general | √ | √
20 |  |  | GENERAL PICKUP | SP | B403_21RPROT$PTRC1$ST$Str | general | √
21 |  |  | COMMUNICATION STATUS | ORG | _ComFault |  | √ | √
22 |  |  | LOW OIL LEVEL ALARM | SP | B403C_21RCTRL$BIBOGGIO1$ST$SPCSO7:0 | stVal | √ | √
23 |  |  | NON-DIRECTIONAL OVERCURRENT PICKUP | SP | B403C_21RPROT$PTOC2$ST$Str | general | √
24 |  |  | NON-DIRECTIONAL OVERCURRENT TRIP | SP | B403C_21RPROT$PTOC2$ST$Op | general | √ | √
25 |  |  | HIGH OIL LEVEL ALARM
26 |  |  | REACTOR MB AC FAIL
27 |  |  | FLOW SENSITIVE VALVE ALARM
28 |  |  | WTI ALARM
29 |  |  | OTI ALARM
30 |  |  | PRV-1 ALARM
31 |  |  | PRV-2 ALARM
32 |  |  | SETTINGS CHANGED
33 |  |  | RELAY IN TEST MODE
34 |  |  | NON-DIRECTIONAL EARTHFAULT TRIP
35 |  |  | NON-DIRECTIONAL EARTHFAULT START
Note: 1. Additional signal for CB Trouble, etc as per scheme & As per standard DR signal requirement the input not considered in HMI signal list 2. 5 Nos of GGIO signal need to be configured as SPARE till the SCADA Database 3. The Logical Device LD is for reference only and vendors may use the same as per their own stndardized way, however the logical nodes used are to be used only as specified. 4. If the logical nodes have been made more specific under the same logical node class by adding prefixes, same can be used as per the application. For example, PDIFF has been specified for all types of differential functions, but if some vendor, under the same logical node class, made the function more specific by adding prefix HZD1PDIFF for 1 phase High Impedance Differential function & T3WPDIFF for 3 winding Low Impedance differential protection, same may be used.

## 403 BR 87R
400kV BR
Sr. No. | Voltage Level | Feeder Name
|  |  | Signal Decription | INFORMATION TYPE | Telegram Address | POSITION | Event | Alarm
BINARY INPUT (Single Point)
1 | 400kV | 400kV BR | RESET LED | SP | B403R_87RCTRL$LLN0$ST$LEDRs:2 | stVal | √
2 |  |  | GOOSE RECEIPT FAIL/TROUBLE | SP | B403R_87RCTRL$GGIO1$ST$SPCSO5:0 | stVal | √ | √
3 |  |  | REACTOR CB OPEN | SP | B403R_87RCTRL$GGIO1$ST$SPCSO1:0 | stVal | √
4 |  |  | TIME SYNCHRONISATION ERROR | SP | B403R_87REXT$pdGGIO2$ST$SPCSO4:0 | stVal | √ | √
5 |  |  | DIFFERENTIAL PROTECTION ACTIVE | SP | B403R_87REXT$pdGGIO88$ST$SPCSO49:0 | stVal | √ | √
6 |  |  | DIFFERENTIAL PROTECTION BLOCKED | SP | B403R_87REXT$pdGGIO88$ST$SPCSO48:0 | stVal | √
7 |  |  | DIFFERENTIAL TRIP R-PH | SP | B403R_87REXT$pdGGIO89$ST$SPCSO40:0 | stVal | √ | √
8 |  |  | DIFFERENTIAL TRIP Y-PH | SP | B403R_87REXT$pdGGIO89$ST$SPCSO41:0 | stVal | √ | √
9 |  |  | DIFFERENTIAL TRIP B-PH | SP | B403R_87REXT$pdGGIO89$ST$SPCSO42:0 | stVal | √ | √
10 |  |  | DIFFERENTIAL STAGE 1 TRIP | SP | B403R_87RPROT$PDIF1$ST$Op | general | √ | √
11 |  |  | DIFFERENTIAL STAGE 1 PICKUP | SP | B403R_87RPROT$PDIF1$ST$Str | general | √
12 |  |  | DIFFERENTIAL STAGE 2 TRIP | SP | B403R_87RPROT$PDIF2$ST$Op | general | √ | √
13 |  |  | DIFFERENTIAL STAGE 2 PICKUP | SP | B403R_87RPROT$PDIF2$ST$Str | general | √
14 |  |  | GENERAL TRIP | SP | B403R_87RPROT$PTRC1$ST$Tr | general | √ | √
15 |  |  | GENERAL PICKUP | SP | B403R_87RPROT$PTRC1$ST$Str | general | √
16 |  |  | COMMUNICATION STATUS | ORG | _ComFault |  | √ | √
17 |  |  | MAIN CB OPEN | SP | B403C_87RCTRL$BIBOGGIO1$ST$SPCSO3:0 | stVal | √
18 |  |  | TIE CB OPEN | SP | B403C_87RCTRL$BIBOGGIO1$ST$SPCSO4:0 | stVal | √
19 |  |  | 2ND HARMONIC
20 |  |  | 5TH HARMONIC
21 |  |  | SUDDEN PRESSURE RELAY TRIP ALARM
22 |  |  | BUCHHOLZ ALARM-B
23 |  |  | BUCHHOLZ-A TRIP
24 |  |  | PRESSURE RELIEF VALVE-2 OPERATED(TRIP)
25 |  |  | WTI TRIP
26 |  |  | 64R RELAY UNHEALTHY
27 |  |  | 86-A/B TRIP RELAY OPTD
28 |  |  | DC-2 FAIL
29 |  |  | SETTINGS CHANGED |  |  |  |  | √
30 |  |  | RELAY IN TEST MODE |  |  |  |  | √
Note: 1. Additional signal for CB Trouble, etc as per scheme & As per standard DR signal requirement the input not considered in HMI signal list 2. 5 Nos of GGIO signal need to be configured as SPARE till the SCADA Database 3. The Logical Device LD is for reference only and vendors may use the same as per their own stndardized way, however the logical nodes used are to be used only as specified. 4. If the logical nodes have been made more specific under the same logical node class by adding prefixes, same can be used as per the application. For example, PDIFF has been specified for all types of differential functions, but if some vendor, under the same logical node class, made the function more specific by adding prefix HZD1PDIFF for 1 phase High Impedance Differential function & T3WPDIFF for 3 winding Low Impedance differential protection, same may be used.