## LEGEND
SIEMENS SCADA GENERAL SIGNAL LIST FOR VARIOUS PROTECTION & CONTROL SIGNALS - REV03 (INDEX)
Sheet Ref. | IED MODEL | IED SYMBOLIC NAME(TYPICAL) | APPLICATION | IED NAME IN SCD | Additional Remarks
1 | 6MD66 | BCU | ICT BCU | STNM4XXBCU | BCU is for each bay so 4XX refers to Bay
2 | 7SJ80 | 7SJ8_51N | ICT BACKUP EARTHFAULT RELAY (IF GIVEN SEPARATE) | STNM4XXTBU | Bay No. 4XX will be always the main bay number for the ICT feeder
3 | 7SJ80 | 7SJ8_64T.2B | REF RELAY PHASE B FOR ICT | STNM4XXTREFB | Bay No. 4XX will be always the main bay number for the ICT feeder
4 | 7SJ80 | 7SJ8_64T.2R | REF RELAY PHASE R FOR ICT | STNM4XXTREFR | Bay No. 4XX will be always the main bay number for the ICT feeder
5 | 7SJ80 | 7SJ8_64T.2Y | REF RELAY PHASE Y FOR ICT | STNM4XXTREFY | Bay No. 4XX will be always the main bay number for the ICT feeder
6 | 7SJ80 | 7SJ8_67_1 LV | ICT LV BACKUP OVERCURRENT AND EARTHFAULT RELAY | STNM4XXTLVBU | Bay No. 4XX will be always the main bay number for the ICT feeder
7 | 7SJ80 | 7SJ8_67_2HV | ICT HV BACKUP OVERCURRENT AND EARTHFAULT RELAY | STNM4XXTHVBU | Bay No. 4XX will be always the main bay number for the ICT feeder
8 | 7RW | 7RW_99LV | ICT OVERFLUX RELAY | STNM4XXTOF | Bay No. 4XX will be always the main bay number for the ICT feeder
9 | 7UT85 | 7UT85_99HV | ICT DIFFERENTIAL RELAY | STNM4XXTDIF | Bay No. 4XX will be always the main bay number for the ICT feeder
10 | 7SA522 | 7SA522_21R | ICT BACKUP IMPEDANCE RELAY | STNM4XXTBUIMP | Bay No. 4XX will be always the main bay number for the ICT feeder
NOTE 1: The characters "STNM" stand for Substation Name with maximum 4 characters, this code will be given by POWERGRID for each project.
NOTE 2: The characters "4XX" stand for Bay name, example if the bay no 401 then same has to be implemented like STNM401BCU

## BCU
400kV ICT-(BCU)
Sr. No. | Voltage Level | Feeder Name | Source
|  |  |  | Signal Decription | INFORMATION TYPE | Telegram Address | POSITION | EVENT | ALARM
BINARY INPUT (Double Point)
1 | 400kV | 400kV ICT | BCU | CB B-PH POSITION | DP | B701_BCUCBB$XCBR1$ST$Pos:2 | stVal | √
2 |  |  |  | CB R-PH POSITION | DP | B701_BCUCBR$XCBR1$ST$Pos:2 | stVal | √
3 |  |  |  | CB Y-PH POSITION | DP | B701_BCUCBY$XCBR1$ST$Pos:2 | stVal | √
4 |  |  |  | CB POSITION | DP | B701_BCUCB$CSWI1$ST$Pos:2 | stVal | √
S89T-R POSITION
S89T-Y POSITION
5 |  |  |  | S89T-B POSITION | DP | B701_BCUES89AE1$CSWI3$ST$Pos:2 | stVal | √
6 |  |  |  | 89AE POSITION | DP | B701_BCUES89AE2$CSWI10$ST$Pos:2 | stVal | √
7 |  |  |  | 89BE POSITION | DP | B701_BCUES89BE$CSWI5$ST$Pos:2 | stVal | √
8 |  |  |  | 89TE B-PH POSITION | DP | B701_BCUES89TEB$CSWI7$ST$Pos:2 | stVal | √
9 |  |  |  | 89TE R-PH POSITION | DP | B701_BCUES89TER$CSWI7$ST$Pos:2 | stVal | √
10 |  |  |  | 89TE Y-PH POSITION | DP | B701_BCUES89TEY$CSWI7$ST$Pos:2 | stVal | √
11 |  |  |  | 89STE B-PH POSITION | DP | B701_BCUESTSE1B$CSWI9$ST$Pos:2 | stVal | √
12 |  |  |  | 89STE R-PH POSITION | DP | B701_BCUESTSE1R$CSWI9$ST$Pos:2 | stVal | √
13 |  |  |  | 89STE Y-PH POSITION | DP | B701_BCUESTSE1Y$CSWI9$ST$Pos:2 | stVal | √
14 |  |  |  | 89STE POSITION | DP | B701_BCUESTSE2$CSWI11$ST$Pos:2 | stVal | √
15 |  |  |  | 89A POSITION | DP | B701_BCUIS89A$CSWI2$ST$Pos:2 | stVal | √
16 |  |  |  | 89B POSITION | DP | B701_BCUIS89B$CSWI4$ST$Pos:2 | stVal | √
17 |  |  |  | 89T B-PH POSITION | DP | B701_BCUIS89TB$CSWI6$ST$Pos:2 | stVal | √
18 |  |  |  | 89T R-PH POSITION | DP | B701_BCUIS89TR$CSWI6$ST$Pos:2 | stVal | √
19 |  |  |  | 89T Y-PH POSITION | DP | B701_BCUIS89TY$CSWI6$ST$Pos:2 | stVal | √
20 |  |  |  | 89TS1_TS2 B-PH POSITION | DP | B701_BCUIS89TS1_TS2B$CSWI8$ST$Pos:2 | stVal | √
21 |  |  |  | 89TS1_TS2 R-PH POSITION | DP | B701_BCUIS89TS1_TS2R$CSWI8$ST$Pos:2 | stVal | √
22 |  |  |  | 89TS1_TS2 Y-PH POSITION | DP | B701_BCUIS89TS1_TS2Y$CSWI8$ST$Pos:2 | stVal | √
23
24 |  |  |  | BINARY INPUT (Single Point)
25
26 |  |  |  | AUX POWER FAIL | SP | B701_BCUApplication$LPHD0$ST$AuxPwrFail | stVal | √ | √
27 |  |  |  | TIME SYNCHRONISATION ERROR | SP | B701_BCUApplication$LMTS0$ST$TmSynErr | stVal | √ | √
28 |  |  |  | LED RESET | SP | B701_BCUApplication$LLN0$ST$LEDRs:2 | stVal | √
29 |  |  |  | BCU MODE | SP | B701_BCUApplication$LLN0$ST$LocKey | stVal | √
30 |  |  |  | CB SF6 GAS PRESSURE REFILL LOW ALARM | SP | B701_BCUApplication$USER1$ST$SPS | stVal | √ | √
31 |  |  |  | CB SF6 GAS PRESSURE LOCKOUT | SP | B701_BCUApplication$USER1$ST$SPS1 | stVal | √ | √
32 |  |  |  | CB DC SUPPLY-1/2 FAIL | SP | B701_BCUApplication$USER3$ST$SPS3 | stVal | √ | √
33 |  |  |  | CB SF6 GAS PRESSURE LOCKOUT | SP | B701_BCUApplication$USER3$ST$SPS2 | stVal | √ | √
34 |  |  |  | POLE DESCREPENCY | SP | B701_BCUApplication$USER3$ST$SPS1 | stVal | √ | √
35 |  |  |  | CB SPRING CHARGED B-PH | SP | B701_BCUApplication$USER3$ST$SPS6 | stVal | √ | √
36 |  |  |  | CB SPRING CHARGED R-PH | SP | B701_BCUApplication$USER3$ST$SPS4 | stVal | √ | √
37 |  |  |  | CB SPRING CHARGED Y-PH | SP | B701_BCUApplication$USER3$ST$SPS5 | stVal | √ | √
38 |  |  |  | 89A POLE DESCREPENCY | SP | B701_BCUApplication$USER4$ST$SPS | stVal | √ | √
39 |  |  |  | 89B POLE DESCREPENCY | SP | B701_BCUApplication$USER4$ST$SPS1 | stVal | √ | √
40 |  |  |  | 86A TRIP RELAY SUPERVISION | SP | B701_BCUApplication$USER7$ST$SPS2 | stVal | √ | √
41 |  |  |  | 86A TRIP RELAY OPERATED | SP | B701_BCUApplication$USER7$ST$SPS1 | stVal | √ | √
42 |  |  |  | 86B TRIP RELAY SUPERVISION | SP | B701_BCUApplication$USER7$ST$SPS5 | stVal | √ | √
43 |  |  |  | 86B TRIP RELAY OPERATED | SP | B701_BCUApplication$USER7$ST$SPS4 | stVal | √ | √
44 |  |  |  | EMERGENCY/MANUAL TRIP | SP | B701_BCUApplication$USER7$ST$SPS6 | stVal | √ | √
45 |  |  |  | CB TC-1 FAULTY | SP | B701_BCUApplication$USER7$ST$SPS | stVal | √ | √
46 |  |  |  | CB TC-2 FAULTY | SP | B701_BCUApplication$USER7$ST$SPS3 | stVal | √ | √
47 |  |  |  | PSD DEVICE IN SERVICE | SP | B701_BCUApplication$USER8$ST$SPS1 | stVal | √ | √
48 |  |  |  | PSD DEVICE HEALTHY | SP | B701_BCUApplication$USER8$ST$SPS | stVal | √ | √
49 |  |  |  | PSD ALARM | SP | B701_BCUApplication$USER8$ST$SPS2 | stVal | √ | √
50 |  |  |  | PSD SYNCH DATA ERROR | SP | B701_BCUApplication$USER8$ST$SPS3 | stVal | √ | √
51 |  |  |  | PSD SELECTOR SWITCH OUT
52 |  |  |  | PSD SELECTOR SWITCH IN
53 |  |  |  | DGA GAS HIGH ALARM SP-PH | SP | B701_BCUApplication$USER9$ST$SPS31 | stVal | √ | √
54 |  |  |  | DGA GAS HIGH ALARM R_Y_B-PH | SP | B701_BCUApplication$USER9$ST$SPS15 | stVal | √ | √
55 |  |  |  | MOISTER HIGH ALARM R_Y_B-PH | SP | B701_BCUApplication$USER9$ST$SPS16 | stVal | √ | √
56 |  |  |  | MOISTER HIGH ALARM SP-PH | SP | B701_BCUApplication$USER9$ST$SPS32 | stVal | √ | √
57 |  |  |  | OLTC OIL TEMP HIGH B-PH ALARM | SP | B701_BCUApplication$USER9$ST$SPS22 | stVal | √ | √
58 |  |  |  | OLTC OIL TEMP HIGH R-PH ALARM | SP | B701_BCUApplication$USER9$ST$SPS18 | stVal | √ | √
59 |  |  |  | OLTC OIL TEMP HIGH SP-PH ALARM | SP | B701_BCUApplication$USER9$ST$SPS34 | stVal | √ | √
60 |  |  |  | OLTC OIL TEMP HIGH Y-PH ALARM | SP | B701_BCUApplication$USER9$ST$SPS20 | stVal | √ | √
61 |  |  |  | OLTC OIL TEMP LOW B-PH ALARM | SP | B701_BCUApplication$USER9$ST$SPS21 | stVal | √ | √
62 |  |  |  | OLTC OIL TEMP LOW R-PH ALARM | SP | B701_BCUApplication$USER9$ST$SPS17 | stVal | √ | √
63 |  |  |  | OLTC OIL TEMP LOW SP-PH ALARM | SP | B701_BCUApplication$USER9$ST$SPS33 | stVal | √ | √
64 |  |  |  | OLTC OIL TEMP LOW Y-PH ALARM | SP | B701_BCUApplication$USER9$ST$SPS19 | stVal | √ | √
65 |  |  |  | OLTC LOW OIL REFILL B-PH ALARM | SP | B701_BCUApplication$USER9$ST$SPS12 | stVal | √ | √
66 |  |  |  | OLTC LOW OIL REFILL SP-PH ALARM | SP | B701_BCUApplication$USER9$ST$SPS28 | stVal | √ | √
67 |  |  |  | OLTC LOW OIL REFILL R-PH ALARM | SP | B701_BCUApplication$USER9$ST$SPS2 | stVal | √ | √
68 |  |  |  | OLTC LOW OIL REFILL Y-PH ALARM | SP | B701_BCUApplication$USER9$ST$SPS7 | stVal | √ | √
69 |  |  |  | RPH MOG LOW OIL LEVEL ALARM | SP
70 |  |  |  | YPH MOG LOW OIL LEVEL ALARM | SP
71 |  |  |  | BPH MOG LOW OIL LEVEL ALARM | SP
72 |  |  |  | SP-PH MOG LOW OIL LEVEL ALARM | SP
73 |  |  |  | RPH MOG HIGH OIL LEVEL ALARM | SP
74 |  |  |  | YPH MOG HIGH OIL LEVEL ALARM | SP
75 |  |  |  | BPH MOG HIGH OIL LEVEL ALARM | SP
76 |  |  |  | SP-PH MOG HIGH OIL LEVEL ALARM | SP
77 |  |  |  | R-PH OIL FLOW SENSITIVE VALVE ALARM | SP
78 |  |  |  | Y-PH OIL FLOW SENSITIVE VALVE ALARM | SP
79 |  |  |  | B-PH OIL FLOW SENSITIVE VALVE ALARM | SP
80 |  |  |  | SP-PH OIL FLOW SENSITIVE VALVE ALARM | SP
81 |  |  |  | RPH PUMP FAIL - BANK A | SP
82 |  |  |  | RPH PUMP FAIL - BANK B | SP
83 |  |  |  | RPH PUMP FAIL - BANK C | SP
84 |  |  |  | RPH PUMP FAIL - BANK D | SP
85 |  |  |  | YPH PUMP FAIL - BANK A | SP
86 |  |  |  | YPH PUMP FAIL - BANK B | SP
87 |  |  |  | YPH PUMP FAIL - BANK C | SP
88 |  |  |  | YPH PUMP FAIL - BANK D | SP
89 |  |  |  | BPH PUMP FAIL - BANK A | SP
90 |  |  |  | BPH PUMP FAIL - BANK B | SP
91 |  |  |  | BPH PUMP FAIL - BANK C | SP
92 |  |  |  | BPH PUMP FAIL - BANK D | SP
93 |  |  |  | SPH PUMP FAIL - BANK A | SP
94 |  |  |  | SPH PUMP FAIL - BANK B | SP
95 |  |  |  | SPH PUMP FAIL - BANK C | SP
96 |  |  |  | SPH PUMP FAIL - BANK D | SP
97 |  |  |  | RPH THERMAL OVERLOAD TRIP - BANK A | SP
98 |  |  |  | RPH THERMAL OVERLOAD TRIP - BANK B | SP
99 |  |  |  | RPH THERMAL OVERLOAD TRIP - BANK C | SP
100 |  |  |  | RPH THERMAL OVERLOAD TRIP - BANK D | SP
101 |  |  |  | YPH THERMAL OVERLOAD TRIP - BANK A | SP
102 |  |  |  | YPH THERMAL OVERLOAD TRIP - BANK B | SP
103 |  |  |  | YPH THERMAL OVERLOAD TRIP - BANK C | SP
104 |  |  |  | YPH THERMAL OVERLOAD TRIP - BANK D | SP
105 |  |  |  | BPH THERMAL OVERLOAD TRIP - BANK A | SP
106 |  |  |  | BPH THERMAL OVERLOAD TRIP - BANK B | SP
107 |  |  |  | BPH THERMAL OVERLOAD TRIP - BANK C | SP
108 |  |  |  | BPH THERMAL OVERLOAD TRIP - BANK D | SP
109 |  |  |  | SPH THERMAL OVERLOAD TRIP - BANK A | SP
110 |  |  |  | SPH THERMAL OVERLOAD TRIP - BANK B | SP
111 |  |  |  | SPH THERMAL OVERLOAD TRIP - BANK C | SP
112 |  |  |  | SPH THERMAL OVERLOAD TRIP - BANK D | SP
113 |  |  |  | RPH LOW OIL FLOW/REVERSE FLOW - BANK A | SP
114 |  |  |  | RPH LOW OIL FLOW/REVERSE FLOW - BANK B | SP
115 |  |  |  | RPH LOW OIL FLOW/REVERSE FLOW - BANK C | SP
116 |  |  |  | RPH LOW OIL FLOW/REVERSE FLOW - BANK D | SP
117 |  |  |  | YPH LOW OIL FLOW/REVERSE FLOW - BANK A | SP
118 |  |  |  | YPH LOW OIL FLOW/REVERSE FLOW - BANK B | SP
119 |  |  |  | YPH LOW OIL FLOW/REVERSE FLOW - BANK C | SP
120 |  |  |  | YPH LOW OIL FLOW/REVERSE FLOW - BANK D | SP
121 |  |  |  | BPH LOW OIL FLOW/REVERSE FLOW - BANK A | SP
122 |  |  |  | BPH LOW OIL FLOW/REVERSE FLOW - BANK B | SP
123 |  |  |  | BPH LOW OIL FLOW/REVERSE FLOW - BANK C | SP
124 |  |  |  | BPH LOW OIL FLOW/REVERSE FLOW - BANK D | SP
125 |  |  |  | SPH LOW OIL FLOW/REVERSE FLOW - BANK A | SP
126 |  |  |  | SPH LOW OIL FLOW/REVERSE FLOW - BANK B | SP
127 |  |  |  | SPH LOW OIL FLOW/REVERSE FLOW - BANK C | SP
128 |  |  |  | SPH LOW OIL FLOW/REVERSE FLOW - BANK D | SP
129 |  |  |  | RPH COOLER CONTROL SUPPLY FAIL | SP
130 |  |  |  | YPH COOLER CONTROL SUPPLY FAIL | SP
131 |  |  |  | BPH COOLER CONTROL SUPPLY FAIL | SP
132 |  |  |  | SPH COOLER CONTROL SUPPLY FAIL | SP
133 |  |  |  | RPH SUPPLY CHANGE OVER FAIL | SP
134 |  |  |  | YPH SUPPLY CHANGE OVER FAIL | SP
135 |  |  |  | BPH SUPPLY CHANGE OVER FAIL | SP
136 |  |  |  | SPH SUPPLY CHANGE OVER FAIL | SP
137 |  |  |  | RPH SUPPLY - A FAIL | SP
138 |  |  |  | YPH SUPPLY - A FAIL | SP
139 |  |  |  | BPH SUPPLY - A FAIL | SP
140 |  |  |  | SPH SUPPLY - A FAIL | SP
141 |  |  |  | RPH SUPPLY - B FAIL | SP
142 |  |  |  | YPH SUPPLY - B FAIL | SP
143 |  |  |  | BPH SUPPLY - B FAIL | SP
144 |  |  |  | SPH SUPPLY - B FAIL | SP
145 |  |  |  | RPH OLTC MOTOR OVERLOAD | SP
146 |  |  |  | RPH TAP CHANGE IN PROGRESS | SP
147 |  |  |  | RPH TAP CHANGE IN COMPLETE | SP
148 |  |  |  | RPH OLTC IN LOCAL | SP
149 |  |  |  | RPH OLTC IN REMOTE | SP
150 |  |  |  | RPH TAP CHANGE CONTROL SUPPLY FAIL | SP
151 |  |  |  | RPH LOWEST POSITION REACHDED | SP
152 |  |  |  | RPH HIGHESHT POSITION REACHDED | SP
153 |  |  |  | RPH OLTC RAISE COMMAND | CMD
154 |  |  |  | RPH OLTC LOWER COMMAND | CMD
155 |  |  |  | YPH OLTC MOTOR OVERLOAD | SP
156 |  |  |  | YPH TAP CHANGE IN PROGRESS | SP
157 |  |  |  | YPH TAP CHANGE IN COMPLETE | SP
158 |  |  |  | YPH OLTC IN LOCAL | SP
159 |  |  |  | YPH OLTC IN REMOTE | SP
160 |  |  |  | YPH TAP CHANGE CONTROL SUPPLY FAIL | SP
161 |  |  |  | YPH LOWEST POSITION REACHDED | SP
162 |  |  |  | YPH HIGHESHT POSITION REACHDED | SP
163 |  |  |  | YPH OLTC RAISE COMMAND | CMD
164 |  |  |  | YPH OLTC LOWER COMMAND | CMD
165 |  |  |  | BPH OLTC MOTOR OVERLOAD | SP
166 |  |  |  | BPH TAP CHANGE IN PROGRESS | SP
167 |  |  |  | BPH TAP CHANGE IN COMPLETE | SP
168 |  |  |  | BPH OLTC IN LOCAL | SP
169 |  |  |  | BPH OLTC IN REMOTE | SP
170 |  |  |  | BPH TAP CHANGE CONTROL SUPPLY FAIL | SP
171 |  |  |  | BPH LOWEST POSITION REACHDED | SP
172 |  |  |  | BPH HIGHESHT POSITION REACHDED | SP
173 |  |  |  | BPH OLTC RAISE COMMAND | CMD
174 |  |  |  | BPH OLTC LOWER COMMAND | CMD
175 |  |  |  | SPH OLTC MOTOR OVERLOAD | SP
176 |  |  |  | SPH TAP CHANGE IN PROGRESS | SP
177 |  |  |  | SPH TAP CHANGE IN COMPLETE | SP
178 |  |  |  | SPH OLTC IN LOCAL | SP
179 |  |  |  | SPH OLTC IN REMOTE | SP
180 |  |  |  | SPH TAP CHANGE CONTROL SUPPLY FAIL | SP
181 |  |  |  | SPH LOWEST POSITION REACHDED | SP
182 |  |  |  | SPH HIGHESHT POSITION REACHDED | SP
183 |  |  |  | SPH OLTC RAISE COMMAND | CMD
184 |  |  |  | SPH OLTC LOWER COMMAND | CMD
185 |  |  |  | OTI B-PH ALARM | SP | B701_BCUApplication$USER9$ST$SPS14 | stVal | √ | √
186 |  |  |  | OTI R-PH ALARM | SP | B701_BCUApplication$USER9$ST$SPS4 | stVal | √ | √
187 |  |  |  | OTI SP-PH ALARM | SP | B701_BCUApplication$USER9$ST$SPS30 | stVal | √ | √
188 |  |  |  | OTI Y-PH ALARM | SP | B701_BCUApplication$USER9$ST$SPS9 | stVal | √ | √
189 |  |  |  | PUMP FAIL B-PH | SP | B701_BCUApplication$USER9$ST$SPS25 | stVal | √ | √
190 |  |  |  | PUMP FAIL R-PH | SP | B701_BCUApplication$USER9$ST$SPS23 | stVal | √ | √
191 |  |  |  | PUMP FAIL SP-PH | SP | B701_BCUApplication$USER9$ST$SPS35 | stVal | √ | √
192 |  |  |  | PUMP FAIL Y-PH | SP | B701_BCUApplication$USER9$ST$SPS24 | stVal | √ | √
193 |  |  |  | SURGE ARRESTER B-PH | SP | B701_BCUApplication$USER9$ST$SPS38 | stVal | √ | √
194 |  |  |  | SURGE ARRESTER R-PH | SP | B701_BCUApplication$USER9$ST$SPS36 | stVal | √ | √
195 |  |  |  | SURGE ARRESTER Y-PH | SP | B701_BCUApplication$USER9$ST$SPS37 | stVal | √ | √
196 |  |  |  | WTI HV_IV_LV ALARM B-PH | SP | B701_BCUApplication$USER9$ST$SPS13 | stVal | √ | √
197 |  |  |  | WTI HV_IV_LV ALARM R-PH | SP | B701_BCUApplication$USER9$ST$SPS3 | stVal | √ | √
198 |  |  |  | WTI HV_IV_LV ALARM SP-PH | SP | B701_BCUApplication$USER9$ST$SPS29 | stVal | √ | √
199 |  |  |  | WTI HV_IV_LV ALARM Y-PH | SP | B701_BCUApplication$USER9$ST$SPS8 | stVal | √ | √
200 |  |  |  | CB SF6 LOW PRESSURE ALARM B-PH | SP | B701_BCUApplication$USER2$ST$SPS2 | stVal | √ | √
201 |  |  |  | CB SF6 LOW PRESSURE ALARM R-PH | SP | B701_BCUApplication$USER2$ST$SPS | stVal | √ | √
202 |  |  |  | CB SF6 LOW PRESSURE ALARM Y-PH | SP | B701_BCUApplication$USER2$ST$SPS1 | stVal | √ | √
203 |  |  |  | SP ICT B-PH SELECTED | SP | B701_BCUApplication$USER12$ST$SPS2 | stVal | √
204 |  |  |  | SP ICT R-PH SELECTED | SP | B701_BCUApplication$USER12$ST$SPS | stVal | √
205 |  |  |  | SP ICT Y-PH SELECTED | SP | B701_BCUApplication$USER12$ST$SPS1 | stVal | √
206 |  |  |  | BUS-1 VT RESET | SP | B701_BCUApplication$USER10$ST$SPS1 | stVal | √
207 |  |  |  | BUS-2 VT RESET | SP | B701_BCUApplication$USER10$ST$SPS3 | stVal | √
208 |  |  |  | LINE VT RESET | SP | B701_BCUApplication$USER10$ST$SPS5 | stVal | √
209 |  |  |  | BUS-1 VT SELECTED | SP | B701_BCUApplication$USER10$ST$SPS | stVal | √
210 |  |  |  | BUS-2 VT SELECTED | SP | B701_BCUApplication$USER10$ST$SPS2 | stVal | √
211 |  |  |  | LINE VTSELECTED | SP | B701_BCUApplication$USER10$ST$SPS4 | stVal | √
212 |  |  |  | CB READY | SP | B701_BCUCB$XCBR1$ST$Rdy | stVal | √
213 |  |  |  | EMERGENCY/MANUAL CB CLOSE | SP | B701_BCUCB$GAPC2$ST$Detected | stVal | √
214 |  |  |  | GOOSE RECEIPT FAIL/TROUBLE | SP | B701_BCUApplication$USER10$ST$SPS3 | stVal | √ | √
215 |  |  |  | CB POSITION NO SYNC | SP | B701_BCUCB$CSWI1$ST$Pos | noSync | √
216 |  |  |  | CB CLOSE INTERLOCK | SP | B701_BCUCB$CILO1$ST$EnaCls | stVal | √
217 |  |  |  | 89AE1 OPEN INTERLOCK | SP | B701_BCUES89AE1$CILO3$ST$EnaOpn | stVal | √
218 |  |  |  | 89AE2 OPEN INTERLOCK | SP | B701_BCUES89AE2$CILO10$ST$EnaOpn | stVal | √
219 |  |  |  | 89BE OPEN INTERLOCK | SP | B701_BCUES89BE$CILO5$ST$EnaOpn | stVal | √
220 |  |  |  | 89TE B-PH OPEN INTERLOCK | SP | B701_BCUES89TEB$CILO7$ST$EnaOpn | stVal | √
221 |  |  |  | 89TE R-PH OPEN INTERLOCK | SP | B701_BCUES89TER$CILO7$ST$EnaOpn | stVal | √
222 |  |  |  | 89TE Y-PH OPEN INTERLOCK | SP | B701_BCUES89TEY$CILO7$ST$EnaOpn | stVal | √
223 |  |  |  | TSE1 B-PH OPEN INTERLOCK | SP | B701_BCUESTSE1B$CILO9$ST$EnaOpn | stVal | √
224 |  |  |  | TSE1 R-PH OPEN INTERLOCK | SP | B701_BCUESTSE1R$CILO9$ST$EnaOpn | stVal | √
225 |  |  |  | TSE1 Y-PH OPEN INTERLOCK | SP | B701_BCUESTSE1Y$CILO9$ST$EnaOpn | stVal | √
226 |  |  |  | TSE2 OPEN INTERLOCK | SP | B701_BCUESTSE2$CILO11$ST$EnaOpn | stVal | √
227 |  |  |  | 89A OPEN INTERLOCK | SP | B701_BCUIS89A$CILO2$ST$EnaOpn | stVal | √
228 |  |  |  | 89B OPEN INTERLOCK | SP | B701_BCUIS89B$CILO4$ST$EnaOpn | stVal | √
229 |  |  |  | 89T B-PH OPEN INTERLOCK | SP | B701_BCUIS89TB$CILO6$ST$EnaOpn | stVal | √
230 |  |  |  | 89T R-PH OPEN INTERLOCK | SP | B701_BCUIS89TR$CILO6$ST$EnaOpn | stVal | √
231 |  |  |  | 89T Y-PH OPEN INTERLOCK | SP | B701_BCUIS89TY$CILO6$ST$EnaOpn | stVal | √
232 |  |  |  | 89TS1_TS2 B-PH OPEN INTERLOCK | SP | B701_BCUIS89TS1_TS2B$CILO8$ST$EnaOpn | stVal | √
233 |  |  |  | 89TS1_TS2 R-PH OPEN INTERLOCK | SP | B701_BCUIS89TS1_TS2R$CILO8$ST$EnaOpn | stVal | √
234 |  |  |  | 89TS1_TS2 Y-PH OPEN INTERLOCK | SP | B701_BCUIS89TS1_TS2Y$CILO8$ST$EnaOpn | stVal | √
235 |  |  |  | RELAY IN TEST MODE |  |  |  | √ | √
236 |  |  |  | SETTINGS CHANGED |  |  |  | √ | √
237 |  |  |  | ICT-n R PH OUT OF SERVICE |  |  |  | √
238 |  |  |  | ICT-n Y PH OUT OF SERVICE |  |  |  | √
239 |  |  |  | ICT-n B PH OUT OF SERVICE |  |  |  | √
240 |  |  |  | ICT SPARE PH IN SERVICE IN ICT-N |  |  |  | √
241 |  |  |  | CB MANUAL TRIP |  |  |  | √
242 |  |  |  | CB MANUAL CLOSE |  |  |  | √
243 |  |  |  | BUSBAR OPERATED |  |  |  | √ | √
244 |  |  |  | BCU IN LOCAL/REMOTE |  |  |  | √
245 |  |  |  | CB TC-1 R-PHASE FAULTY |  |  |  | √ | √
246 |  |  |  | CB TC-1 Y-PHASE FAULTY |  |  |  | √ | √
247 |  |  |  | CB TC-1 B-PHASE FAULTY |  |  |  | √ | √
248 |  |  |  | CB TC-2 R-PHASE FAULTY |  |  |  | √ | √
249 |  |  |  | CB TC-2 Y-PHASE FAULTY |  |  |  | √ | √
250 |  |  |  | CB TC-2 B-PHASE FAULTY |  |  |  | √ | √
251
252 |  |  |  | MEASUREMENT
253
254 |  |  |  | POWER FACTOR | ME_FL | B701_BCUVI3p1_OperationalValues$PPRE_MMXU1$MX$TotPF:1 | mag$f
255 |  |  |  | FREQUENCY | ME_FL | B701_BCUVI3p1_OperationalValues$PPRE_MMXU1$MX$Hz:1 | mag$f
256 |  |  |  | ACTIVE POWER | ME_FL | B701_BCUVI3p1_OperationalValues$PPRE_MMXU1$MX$TotW:1 | mag$f
257 |  |  |  | REACTIVE POWER | ME_FL | B701_BCUVI3p1_OperationalValues$PPRE_MMXU1$MX$TotVAr:1 | mag$f
258 |  |  |  | APPARENT POWER | ME_FL | B701_BCUVI3p1_OperationalValues$PPRE_MMXU1$MX$TotVA:1 | mag$f
259 |  |  |  | I-R-PH CURRENT | ME_FL | B701_BCUVI3p1_OperationalValues$RPRE_MMXU1$MX$A:1 | phsA$cVal$mag$f
260 |  |  |  | I-Y-PH CURRENT | ME_FL | B701_BCUVI3p1_OperationalValues$RPRE_MMXU1$MX$A:1 | phsB$cVal$mag$f
261 |  |  |  | I-B-PH CURRENT | ME_FL | B701_BCUVI3p1_OperationalValues$RPRE_MMXU1$MX$A:1 | phsC$cVal$mag$f
262 |  |  |  | R-Y VOLTAGE | ME_FL | B701_BCUVI3p1_OperationalValues$RPRE_MMXU1$MX$PPV:1 | phsAB$cVal$mag$f
263 |  |  |  | Y-B VOLTAGE | ME_FL | B701_BCUVI3p1_OperationalValues$RPRE_MMXU1$MX$PPV:1 | phsBC$cVal$mag$f
264 | 400kV | 400kV ICT | BCU | B-R VOLYAGE | ME_FL | B701_BCUVI3p1_OperationalValues$RPRE_MMXU1$MX$PPV:1 | phsCA$cVal$mag$f
265 |  |  |  | CB-B-PH COUNTER | ME_I | B701_BCUCBB$XCBR1$ST$OpCnt | stVal
266 |  |  |  | CB-R-PH COUNTER | ME_I | B701_BCUCBR$XCBR1$ST$OpCnt | stVal
267 |  |  |  | CB-Y-PH COUNTER | ME_I | B701_BCUCBY$XCBR1$ST$OpCnt | stVal
268
269 |  |  |  | COMMANDS
270
271 |  |  |  | CB CONTROL | DC | B701_BCUCB$CSWI1$CO$Pos:8 | Oper$ctlVal | √
272 |  |  |  | 89AE1 CONTROL | DC | B701_BCUES89AE1$CSWI3$CO$Pos:8 | Oper$ctlVal | √ |  | NO command in AIS.
273 |  |  |  | 89AE2 CONTROL | DC | B701_BCUES89AE2$CSWI10$CO$Pos:8 | Oper$ctlVal | √
274 |  |  |  | 89BE CONTROL | DC | B701_BCUES89BE$CSWI5$CO$Pos:8 | Oper$ctlVal | √
275 |  |  |  | 89TE B-PH CONTROL | DC | B701_BCUES89TEB$CSWI7$CO$Pos:8 | Oper$ctlVal | √
276 |  |  |  | 89TE R-PH CONTROL | DC | B701_BCUES89TER$CSWI7$CO$Pos:8 | Oper$ctlVal | √
277 |  |  |  | 89TE Y-PH CONTROL | DC | B701_BCUES89TEY$CSWI7$CO$Pos:8 | Oper$ctlVal | √
278 |  |  |  | TSE1 B-PH CONTROL | DC | B701_BCUESTSE1B$CSWI9$CO$Pos:8 | Oper$ctlVal | √
279 |  |  |  | TSE1 R-PH CONTROL | DC | B701_BCUESTSE1R$CSWI9$CO$Pos:8 | Oper$ctlVal | √
280 |  |  |  | TSE1 Y-PH CONTROL | DC | B701_BCUESTSE1Y$CSWI9$CO$Pos:8 | Oper$ctlVal | √
281 |  |  |  | TSE2 CONTROL | DC | B701_BCUESTSE2$CSWI11$CO$Pos:8 | Oper$ctlVal | √
282 |  |  |  | 89A CONTROL | DC | B701_BCUIS89A$CSWI2$CO$Pos:8 | Oper$ctlVal | √
283 |  |  |  | 89B CONTROL | DC | B701_BCUIS89B$CSWI4$CO$Pos:8 | Oper$ctlVal | √
284 |  |  |  | 89T B-PH CONTROL | DC | B701_BCUIS89TB$CSWI6$CO$Pos:8 | Oper$ctlVal | √
285 |  |  |  | 89T R-PH CONTROL | DC | B701_BCUIS89TR$CSWI6$CO$Pos:8 | Oper$ctlVal | √
286 |  |  |  | 89TS1_TS2 B-PH CONTROL | DC | B701_BCUIS89TS1_TS2B$CSWI8$CO$Pos:8 | Oper$ctlVal | √
287 |  |  |  | 89TS1_TS2 R-PH CONTROL | DC | B701_BCUIS89TS1_TS2R$CSWI8$CO$Pos:8 | Oper$ctlVal | √
288 |  |  |  | 89TS1_TS2 Y-PH CONTROL | DC | B701_BCUIS89TS1_TS2Y$CSWI8$CO$Pos:8 | Oper$ctlVal | √
289 |  |  |  | 89T Y-PH CONTROL | DC | B701_BCUIS89TY$CSWI6$CO$Pos:8 | Oper$ctlVal | √
290 |  |  |  | CB CONTROL NO SYN | SC | B701_BCUCB$CSWI1$CO$Pos | Oper$noSync | √
291 |  |  |  | 86A TRIP RELAY RESET COMMAND | SC | B701_BCUApplication$USER2$CO$SPC:8 | Oper$ctlVal | √
292 |  |  |  | 86B TRIP RELAY RESET COMMAND | SC | B701_BCUApplication$USER2$CO$SPC1:8 | Oper$ctlVal | √
293 |  |  |  | TAP RAISER | SC | B701_BCUApplication$USER8$CO$SPC:8 | Oper$ctlVal | √
294 |  |  |  | TAP LOWER | SC | B701_BCUApplication$USER8$CO$SPC1:8 | Oper$ctlVal | √
Note: 1. All the switchgear status signals as per the actual primary equipment status. 2. Additional signal for CB Trouble, etc as per scheme 3. 10 Nos of GGIO signal need to be configured as SPARE till the SCADA Database 4. The Logical Device LD is for reference only and vendors may use the same as per their own stndardized way, however the logical nodes used are to be used only as specified. 5. If the logical nodes have been made more specific under the same logical node class by adding prefixes, same can be used as per the application. For example, PDIFF has been specified for all types of differential functions, but if some vendor, under the same logical node class, made the function more specific by adding prefix HZD1PDIFF for 1 phase High Impedance Differential function & T3WPDIFF for 3 winding Low Impedance differential protection, same may be used.

## 7SJ8_51N
400kV ICT- 51N-(7SJ80)
Sr. No. | Voltage Level | Feeder Name | Source
|  |  |  | Signal Decription | INFORMATION TYPE | Telegram Address | POSITION | EVENT | ALARM
BINARY INPUT (Single Point)
1 | 400kV | 400kV ICT | 7SJ80 | DMT EARTHFAULT STAGE 1 TRIP | SP | B701_51NPROT$PTOC8$ST$Op | general | √ | √
2 |  |  |  | DMT EARTHFAULT STAGE 1 PICKUP | SP | B701_51NPROT$PTOC8$ST$Str | general | √
3 |  |  |  | DMT EARTHFAULT STAGE 2 TRIP | SP | B701_51NPROT$PTOC9$ST$Op | general | √ | √
4 |  |  |  | DMT EARTHFAULT STAGE 2 PICKUP | SP | B701_51NPROT$PTOC9$ST$Str | general | √
5 |  |  |  | IDMT EARTHFAULT TRIP | SP | B701_51NPROT$PTOC2$ST$Op | general | √ | √
6 |  |  |  | IDMT EARTHFAULT PICKUP | SP | B701_51NPROT$PTOC2$ST$Str | general | √
7 |  |  |  | GENERAL TRIP | SP | B701_51NPROT$PTRC1$ST$Tr | general | √ | √
8 |  |  |  | GENERAL PICKUP | SP | B701_51NPROT$PTRC1$ST$Str | general | √
9 |  |  |  | DEVICE HEALTHY | SP | B701_51NPROT$LPHD1$ST$PhyHealth:0 | stVal:1 | √
10 |  |  |  | TIME SYNCHRONISATION ERROR | SP | B701_51NEXT$pdGGIO2$ST$SPCSO4:0 | stVal | √ | √
11 |  |  |  | VT FUSE FAILURE | SP | B701_51NEXT$pdGGIO3$ST$SPCSO41:0 | stVal | √ | √
12 |  |  |  | OLTC OSR TRIP R PH | SP | B701_51NCTRL$GGIO1$ST$SPCSO2:0 | stVal | √ | √
13 |  |  |  | OLTC OSR TRIP Y PH | SP | B701_51NCTRL$GGIO1$ST$SPCSO3:0 | stVal | √ | √
14 |  |  |  | OLTC OSR TRIP B PH | SP | B701_51NCTRL$GGIO1$ST$SPCSO4:0 | stVal | √ | √
15 |  |  |  | OIL FLOW SENSITIVE VALVE TRIP R PH | SP | B701_51NCTRL$GGIO1$ST$SPCSO5:0 | stVal | √ | √
16 |  |  |  | OIL FLOW SENSITIVE VALVE TRIP Y PH | SP | B701_51NCTRL$GGIO1$ST$SPCSO6:0 | stVal | √ | √
17 |  |  |  | GOOSE RECEIPT FAIL/TROUBLE | SP | B701_51NCTRL$GGIO1$ST$SPCSO1:0 | stVal | √ | √
18 |  |  |  | SETTINGS CHANGED |  |  |  | √ | √
19 |  |  |  | RELAY IN TEST MODE |  |  |  | √ | √
Note: 1. Additional signal for CB Trouble, etc as per scheme & As per standard DR signal requirement the input not considered in HMI signal list 2. 5 Nos of GGIO signal need to be configured as SPARE till the SCADA Database 3. The Logical Device LD is for reference only and vendors may use the same as per their own stndardized way, however the logical nodes used are to be used only as specified. 4. If the logical nodes have been made more specific under the same logical node class by adding prefixes, same can be used as per the application. For example, PDIFF has been specified for all types of differential functions, but if some vendor, under the same logical node class, made the function more specific by adding prefix HZD1PDIFF for 1 phase High Impedance Differential function & T3WPDIFF for 3 winding Low Impedance differential protection, same may be used.
Note on A3: 1087:

## 7SJ8_64T.2B
400kV ICT- 64T.2B-(7SJ80)
Sr. No. | Voltage Level | Feeder Name | Source | NAME (BAY-701 ICT-1)
|  |  |  | Signal Decription | INFORMATION TYPE | Telegram Address | POSITION | EVENT | ALARM
BINARY INPUT (Single Point)
1 | 400kV | 400kV ICT | 7SJ80 | 99LV_51N RELAY UNHEALTHY | SP | B701_64T_2BCTRL$GGIO1$ST$SPCSO1:0 | stVal | √ | √
2 |  |  |  | RAPID PRESSURE TRIP B-PH | SP | B701_64T_2BCTRL$GGIO1$ST$SPCSO2:0 | stVal | √ | √
3 |  |  |  | REF STAGE 1 TRIP | SP | B701_64T_2BPROT$PTOC16$ST$Op | general | √ | √
4 |  |  |  | REF STAGE 1 PICKUP | SP | B701_64T_2BPROT$PTOC16$ST$Str | general | √
5 |  |  |  | REF STAGE 2 TRIP | SP | B701_64T_2BPROT$PTOC17$ST$Op | general | √ | √
6 |  |  |  | REF STAGE 2 PICKUP | SP | B701_64T_2BPROT$PTOC17$ST$Str | general | √
7 |  |  |  | GENERAL TRIP | SP | B701_64T_2BPROT$PTRC1$ST$Tr | general | √ | √
8 |  |  |  | GENERAL PICKUP | SP | B701_64T_2BPROT$PTRC1$ST$Str | general | √
9 |  |  |  | DEVICE HEALTHY | SP | B701_64T_2BPROT$LPHD1$ST$PhyHealth:0 | stVal:1 | √
10 |  |  |  | TIME SYNCHRONISATION ERROR | SP | B701_64T_2BEXT$pdGGIO2$ST$SPCSO4:0 | stVal | √ | √
11 |  |  |  | GOOSE RECEIPT FAIL/TROUBLE | SP | B701_64T_2BCTRL$GGIO1$ST$SPCSO7:0 | stVal | √ | √
12 |  |  |  | BUCHHOLZ 1 TRIP B-PH | SP | B701_64T_2BCTRL$GGIO1$ST$SPCSO5:0 | stVal | √ | √
13 |  |  |  | OTI TRIP B-PH | SP | B701_64T_2BCTRL$GGIO1$ST$SPCSO6:0 | stVal | √ | √
14 |  |  |  | BUCHHOLZ 2 ALARM B-PH | SP | B701_64T_2BCTRL$GGIO1$ST$SPCSO3:0 | stVal | √ | √
15 |  |  |  | PRD OLTC TRIP B-PH | SP | B701_64T_2BCTRL$GGIO1$ST$SPCSO4:0 | stVal | √ | √
16 |  |  |  | SETTINGS CHANGED |  |  |  | √ | √
17 |  |  |  | RELAY IN TEST MODE |  |  |  | √ | √
Note: 1. Additional signal for CB Trouble, Mechanical trips, alarms etc as per scheme & As per standard DR signal requirement the input not considered in HMI signal list 2. 5 Nos of GGIO signal need to be configured as SPARE till the SCADA Database 3. The Logical Device LD is for reference only and vendors may use the same as per their own stndardized way, however the logical nodes used are to be used only as specified. 4. If the logical nodes have been made more specific under the same logical node class by adding prefixes, same can be used as per the application. For example, PDIFF has been specified for all types of differential functions, but if some vendor, under the same logical node class, made the function more specific by adding prefix HZD1PDIFF for 1 phase High Impedance Differential function & T3WPDIFF for 3 winding Low Impedance differential protection, same may be used.

## 7SJ8_64T.2R
400kV ICT- 64T.2R-(7SJ80)
Sr. No. | Voltage Level | Feeder Name | Source | NAME (BAY-701 ICT-1)
|  |  |  | Signal Decription | INFORMATION TYPE | Telegram Address | POSITION | EVENT | ALARM
BINARY INPUT (Single Point)
1 | 400kV | 400kV ICT | 7SJ80 | MAIN CB OPEN | SP | B701_64T_2RCTRL$GGIO1$ST$SPCSO1:0 | stVal | √
2 |  |  |  | TIE CB OPEN | SP | B701_64T_2RCTRL$GGIO1$ST$SPCSO2:0 | stVal | √
3 |  |  |  | BUCHHOLZ 1 TRIP R-PH | SP | B701_64T_2RCTRL$GGIO1$ST$SPCSO4:0 | stVal | √ | √
4 |  |  |  | BUCHHOLZ 2 ALARM R-PH |  | B701_64T_2RCTRL$GGIO1$ST$SPCSO7:0 | stVal | √ | √
5 |  |  |  | OTI TRIP R-PH | SP | B701_64T_2RCTRL$GGIO1$ST$SPCSO5:0 | stVal | √ | √
6 |  |  |  | PRD OLTC TRIP R-PH | SP | B701_64T_2RCTRL$GGIO1$ST$SPCSO3:0 | stVal | √ | √
7 |  |  |  | REF STAGE 1 TRIP | SP | B701_64T_2RPROT$PTOC16$ST$Op | general | √ | √
8 |  |  |  | REF STAGE 1 PICKUP | SP | B701_64T_2RPROT$PTOC16$ST$Str | general | √
9 |  |  |  | REF STAGE 2 TRIP | SP | B701_64T_2RPROT$PTOC17$ST$Op | general | √ | √
10 |  |  |  | REF STAGE 2 PICKUP | SP | B701_64T_2RPROT$PTOC17$ST$Str | general | √
11 |  |  |  | GENERAL TRIP | SP | B701_64T_2RPROT$PTRC1$ST$Tr | general | √ | √
12 |  |  |  | GENERAL PICKUP | SP | B701_64T_2RPROT$PTRC1$ST$Str | general | √
13 |  |  |  | DEVICE HEALTHY | SP | B701_64T_2RPROT$LPHD1$ST$PhyHealth:0 | stVal:1 | √
14 |  |  |  | TIME SYNCHRONISATION ERROR | SP | B701_64T_2REXT$pdGGIO2$ST$SPCSO4:0 | stVal | √ | √
15 |  |  |  | GOOSE RECEIPT FAIL/TROUBLE | SP | B701_64T_2RCTRL$GGIO1$ST$SPCSO6:0 | stVal | √ | √
16 |  |  |  | SETTINGS CHANGED |  |  |  | √ | √
17 |  |  |  | RELAY IN TEST MODE |  |  |  | √ | √
Note: 1. Additional signal for CB Trouble, Mechanical trips, alarms etc as per scheme & As per standard DR signal requirement the input not considered in HMI signal list 2. 5 Nos of GGIO signal need to be configured as SPARE till the SCADA Database 3. The Logical Device LD is for reference only and vendors may use the same as per their own stndardized way, however the logical nodes used are to be used only as specified. 4. If the logical nodes have been made more specific under the same logical node class by adding prefixes, same can be used as per the application. For example, PDIFF has been specified for all types of differential functions, but if some vendor, under the same logical node class, made the function more specific by adding prefix HZD1PDIFF for 1 phase High Impedance Differential function & T3WPDIFF for 3 winding Low Impedance differential protection, same may be used.

## 7SJ8_64T.2Y
400kV ICT- 64T.2Y-(7SJ80)
Sr. No. | Voltage Level | Feeder Name | Source | NAME (BAY-701 ICT-1)
|  |  |  | Signal Decription | INFORMATION TYPE | Telegram Address | POSITION | EVENT | ALARM
BINARY INPUT (Single Point)
1 | 400kV | 400kV ICT | 7SJ80 | BUCHHOLZ 1 TRIP Y-PH | SP | B701_64T_2YCTRL$GGIO1$ST$SPCSO2:0 | stVal | √ | √
2 |  |  |  | OTI TRIP Y-PH | SP | B701_64T_2YCTRL$GGIO1$ST$SPCSO3:0 | stVal | √ | √
3 |  |  |  | PRD OLTC TRIP Y-PH | SP | B701_64T_2YCTRL$GGIO1$ST$SPCSO1:0 | stVal | √ | √
4 |  |  |  | REF STAGE 1 TRIP | SP | B701_64T_2YPROT$PTOC16$ST$Op | general | √ | √
5 |  |  |  | REF STAGE 1 PICKUP | SP | B701_64T_2YPROT$PTOC16$ST$Str | general | √
6 |  |  |  | REF STAGE 2 TRIP | SP | B701_64T_2YPROT$PTOC17$ST$Op | general | √ | √
7 |  |  |  | REF STAGE 2 PICKUP | SP | B701_64T_2YPROT$PTOC17$ST$Str | general | √
8 |  |  |  | GENERAL TRIP | SP | B701_64T_2YPROT$PTRC1$ST$Tr | general | √ | √
9 |  |  |  | GENERAL PICKUP | SP | B701_64T_2YPROT$PTRC1$ST$Str | general | √
10 |  |  |  | DEVICE HEALTHY | SP | B701_64T_2YPROT$LPHD1$ST$PhyHealth:0 | stVal:1 | √
11 |  |  |  | TIME SYNCHRONISATION ERROR | SP | B701_64T_2YEXT$pdGGIO2$ST$SPCSO4:0 | stVal | √ | √
12 |  |  |  | BUCHHOLZ 2 ALARM Y-PH | SP | B701_64T_2YCTRL$GGIO1$ST$SPCSO4:0 | stVal | √ | √
13 |  |  |  | GOOSE RECEIPT FAIL/TROUBLE | SP | B701_64T_2YCTRL$GGIO1$ST$SPCSO7:0 | stVal | √ | √
16 |  |  |  | SETTINGS CHANGED |  |  |  | √ | √
17 |  |  |  | RELAY IN TEST MODE |  |  |  | √ | √
Note: 1. Additional signal for CB Trouble, Mechanical trips, alarms etc as per scheme & As per standard DR signal requirement the input not considered in HMI signal list 2. 5 Nos of GGIO signal need to be configured as SPARE till the SCADA Database 3. The Logical Device LD is for reference only and vendors may use the same as per their own stndardized way, however the logical nodes used are to be used only as specified. 4. If the logical nodes have been made more specific under the same logical node class by adding prefixes, same can be used as per the application. For example, PDIFF has been specified for all types of differential functions, but if some vendor, under the same logical node class, made the function more specific by adding prefix HZD1PDIFF for 1 phase High Impedance Differential function & T3WPDIFF for 3 winding Low Impedance differential protection, same may be used.

## 7SJ8_67_1 LV
400kV ICT- 67-1-LV (7SJ80)
Sr. No. | Voltage Level | Feeder Name | Source | NAME (BAY-701 ICT-1)
|  |  |  | Signal Decription | INFORMATION TYPE | Telegram Address | POSITION | EVENT | ALARM
BINARY INPUT (Single Point)
1 | 400kV | 400kV ICT | 7SJ80 | 67. 2 HV RELAY UNHEALTHY | SP | B701_67_1_LVCTRL$GGIO1$ST$SPCSO2:0 | stVal | √ | √
2 |  |  |  | 87.1_99HV HV RELAY UNHEALTHY | SP | B701_67_1_LVCTRL$GGIO1$ST$SPCSO1:0 | stVal | √ | √
3 |  |  |  | BCU UNHEALTHY | SP | B701_67_1_LVCTRL$GGIO1$ST$SPCSO3:0 | stVal | √ | √
4 |  |  |  | DIRECTIONAL DMT OVERCURRENT STAGE-1 BLOCKED | SP | B701_67_1_LVPROT$PTOC10$ST$Blk | stVal | √
5 |  |  |  | DIRECTIONAL DMT OVERCURRENT STAGE-1 TRIP | SP | B701_67_1_LVPROT$PTOC10$ST$Op | general | √ | √
6 |  |  |  | DIRECTIONAL DMT OVERCURRENT STAGE-1 PICKUP | SP | B701_67_1_LVPROT$PTOC10$ST$Str | general | √
7 |  |  |  | DIRECTIONAL DMT OVERCURRENT STAGE-2 BLOCKED | SP | B701_67_1_LVPROT$PTOC11$ST$Blk | stVal | √
8 |  |  |  | DIRECTIONAL DMT OVERCURRENT STAGE-2 TRIP | SP | B701_67_1_LVPROT$PTOC11$ST$Op | general | √ | √
9 |  |  |  | DIRECTIONAL DMT OVERCURRENT STAGE-2 PICKUP | SP | B701_67_1_LVPROT$PTOC11$ST$Str | general | √
10 |  |  |  | DIRECTIONAL DMT OVERCURRENT STAGE-3 TRIP | SP | B701_67_1_LVPROT$PTOC19$ST$Op | general | √ | √
11 |  |  |  | DIRECTIONAL DMT OVERCURRENT STAGE-3 PICKUP | SP | B701_67_1_LVPROT$PTOC19$ST$Str | general | √
12 |  |  |  | DIRECTIONAL DMT EARTHFAULT STAGE-1 BLOCKED | SP | B701_67_1_LVPROT$PTOC12$ST$Blk | stVal | √
13 |  |  |  | DIRECTIONAL DMT EARTHFAULT STAGE-1 TRIP | SP | B701_67_1_LVPROT$PTOC12$ST$Op | general | √ | √
14 |  |  |  | DIRECTIONAL DMT EARTHFAULT STAGE-1 PICKUP | SP | B701_67_1_LVPROT$PTOC12$ST$Str | general | √
15 |  |  |  | DIRECTIONAL DMT EARTHFAULT STAGE-2 BLOCKED | SP | B701_67_1_LVPROT$PTOC13$ST$Blk | stVal | √
16 |  |  |  | DIRECTIONAL DMT EARTHFAULT STAGE-2 TRIP | SP | B701_67_1_LVPROT$PTOC13$ST$Op | general | √ | √
17 |  |  |  | DIRECTIONAL DMT EARTHFAULT STAGE-2 PICKUP | SP | B701_67_1_LVPROT$PTOC13$ST$Str | general | √
18 |  |  |  | DIRECTIONAL DMT EARTHFAULT STAGE-3 TRIP | SP | B701_67_1_LVPROT$PTOC20$ST$Op | general | √ | √
19 |  |  |  | DIRECTIONAL DMT EARTHFAULT STAGE-3 PICKUP | SP | B701_67_1_LVPROT$PTOC20$ST$Str | general | √
20 |  |  |  | DIRECTIONAL IDMT OVERCURRENT BLOCKED | SP | B701_67_1_LVPROT$PTOC4$ST$Blk | stVal | √
21 |  |  |  | DIRECTIONAL IDMT OVERCURRENT TRIP | SP | B701_67_1_LVPROT$PTOC4$ST$Op | general | √ | √
22 |  |  |  | DIRECTIONAL IDMT EARTHFAULT BLOCKED | SP | B701_67_1_LVPROT$PTOC3$ST$Blk | stVal | √
23 |  |  |  | DIRECTIONAL IDMT EARTHFAULT TRIP | SP | B701_67_1_LVPROT$PTOC3$ST$Op | general | √ | √
24 |  |  |  | GENERAL TRIP | SP | B701_67_1_LVPROT$PTRC1$ST$Tr | general | √ | √
25 |  |  |  | GENERAL PICKUP | SP | B701_67_1_LVPROT$PTRC1$ST$Str | general | √
26 |  |  |  | DEVICE HEALTHY | SP | B701_67_1_LVPROT$LPHD1$ST$PhyHealth:0 | stVal:1 | √
27 |  |  |  | TIME SYNCHRONISATION ERROR | SP | B701_67_1_LVEXT$pdGGIO2$ST$SPCSO4:0 | stVal | √ | √
28 |  |  |  | GOOSE RECEIPT FAIL/TROUBLE | SP | B701_67_1_LVCTRL$GGIO1$ST$SPCSO7:0 | stVal | √ | √
16 |  |  |  | SETTINGS CHANGED |  |  |  | √ | √
17 |  |  |  | RELAY IN TEST MODE |  |  |  | √ | √
Note: 1. Additional signal for CB Trouble, Mechanical trips, alarms etc as per scheme & As per standard DR signal requirement the input not considered in HMI signal list 2. 5 Nos of GGIO signal need to be configured as SPARE till the SCADA Database 3. The Logical Device LD is for reference only and vendors may use the same as per their own stndardized way, however the logical nodes used are to be used only as specified. 4. If the logical nodes have been made more specific under the same logical node class by adding prefixes, same can be used as per the application. For example, PDIFF has been specified for all types of differential functions, but if some vendor, under the same logical node class, made the function more specific by adding prefix HZD1PDIFF for 1 phase High Impedance Differential function & T3WPDIFF for 3 winding Low Impedance differential protection, same may be used.

## 7SJ8_67_2HV
400kV ICT-67-2HV (7SJ80)
Sr. No. | Voltage Level | Feeder Name | Source | NAME (BAY-701 ICT-1)
|  |  |  | Signal Decription | INFORMATION TYPE | Telegram Address | POSITION | EVENT | ALARM
BINARY INPUT (Single Point)
1 | 400kV | 400kV ICT | 7SJ80 | RAPID PRESSURE TRIP R-PH | SP | B701_67_2HVCTRL$GGIO1$ST$SPCSO5:0 | stVal | √ | √
2 |  |  |  | BUCHHOLZ 2 TRIP SP-PH | SP | B701_67_2HVCTRL$GGIO1$ST$SPCSO1:0 | stVal | √ | √
3 |  |  |  | WTI HV_IV_LV TRIP SP-PH | SP | B701_67_2HVCTRL$GGIO1$ST$SPCSO3:0 | stVal | √ | √
4 |  |  |  | WTI HV_LV_IV TRIP B-PH | SP | B701_67_2HVCTRL$GGIO1$ST$SPCSO6:0 | stVal | √ | √
5 |  |  |  | WTI HV_LV_IV TRIP R-PH | SP | B701_67_2HVCTRL$GGIO1$ST$SPCSO2:0 | stVal | √ | √
6 |  |  |  | WTI HV_LV_IV TRIP Y-PH | SP | B701_67_2HVCTRL$GGIO1$ST$SPCSO4:0 | stVal | √ | √
7 |  |  |  | DIRECTIONAL DMT OVERCURRENT STAGE-1 BLOCKED | SP | B701_67_2HVPROT$PTOC10$ST$Blk | stVal | √
8 |  |  |  | DIRECTIONAL DMT OVERCURRENT STAGE-1 TRIP | SP | B701_67_2HVPROT$PTOC10$ST$Op | general | √ | √
9 |  |  |  | DIRECTIONAL DMT OVERCURRENT STAGE-1 PICKUP | SP | B701_67_2HVPROT$PTOC10$ST$Str | general | √
10 |  |  |  | DIRECTIONAL DMT OVERCURRENT STAGE-2 BLOCKED | SP | B701_67_2HVPROT$PTOC11$ST$Blk | stVal | √
11 |  |  |  | DIRECTIONAL DMT OVERCURRENT STAGE-2 TRIP | SP | B701_67_2HVPROT$PTOC11$ST$Op | general | √ | √
12 |  |  |  | DIRECTIONAL DMT OVERCURRENT STAGE-2 PICKUP | SP | B701_67_2HVPROT$PTOC11$ST$Str | general | √
13 |  |  |  | DIRECTIONAL DMT OVERCURRENT STAGE-3 TRIP | SP | B701_67_2HVPROT$PTOC19$ST$Op | general | √ | √
14 |  |  |  | DIRECTIONAL DMT OVERCURRENT STAGE-3 PICKUP | SP | B701_67_2HVPROT$PTOC19$ST$Str | general | √
15 |  |  |  | DIRECTIONAL DMT EARTHFAULT STAGE-1 BLOCKED | SP | B701_67_2HVPROT$PTOC12$ST$Blk | stVal | √
16 |  |  |  | DIRECTIONAL DMT EARTHFAULT STAGE-1 TRIP | SP | B701_67_2HVPROT$PTOC12$ST$Op | general | √ | √
17 |  |  |  | DIRECTIONAL DMT EARTHFAULT STAGE-1 PICKUP | SP | B701_67_2HVPROT$PTOC12$ST$Str | general | √
18 |  |  |  | DIRECTIONAL DMT EARTHFAULT STAGE-2 BLOCKED | SP | B701_67_2HVPROT$PTOC13$ST$Blk | stVal | √
19 |  |  |  | DIRECTIONAL DMT EARTHFAULT STAGE-2 TRIP | SP | B701_67_2HVPROT$PTOC13$ST$Op | general | √ | √
20 |  |  |  | DIRECTIONAL DMT EARTHFAULT STAGE-2 PICKUP | SP | B701_67_2HVPROT$PTOC13$ST$Str | general | √
21 |  |  |  | DIRECTIONAL DMT EARTHFAULT STAGE-3 TRIP | SP | B701_67_2HVPROT$PTOC20$ST$Op | general | √ | √
22 |  |  |  | DIRECTIONAL DMT EARTHFAULT STAGE-3 PICKUP | SP | B701_67_2HVPROT$PTOC20$ST$Str | general | √
23 |  |  |  | GENERAL TRIP | SP | B701_67_2HVPROT$PTRC1$ST$Tr | general | √ | √
24 |  |  |  | GENERAL PICKUP | SP | B701_67_2HVPROT$PTRC1$ST$Str | general | √
25 |  |  |  | DEVICE HEALTHY | SP | B701_67_2HVPROT$LPHD1$ST$PhyHealth:0 | stVal:1 | √
26 |  |  |  | TIME SYNCHRONISATION ERROR | SP | B701_67_2HVEXT$pdGGIO2$ST$SPCSO4:0 | stVal | √ | √
27 |  |  |  | GOOSE RECEIPT FAIL/TROUBLE | SP | B701_67_2HVCTRL$GGIO1$ST$SPCSO7:0 | stVal | √ | √
28 |  |  |  | SETTINGS CHANGED |  |  |  | √ | √
29 |  |  |  | RELAY IN TEST MODE |  |  |  | √ | √
Note: 1. Additional signal for CB Trouble, Mechanical trips, alarms etc as per scheme & As per standard DR signal requirement the input not considered in HMI signal list 2. 5 Nos of GGIO signal need to be configured as SPARE till the SCADA Database 3. The Logical Device LD is for reference only and vendors may use the same as per their own stndardized way, however the logical nodes used are to be used only as specified. 4. If the logical nodes have been made more specific under the same logical node class by adding prefixes, same can be used as per the application. For example, PDIFF has been specified for all types of differential functions, but if some vendor, under the same logical node class, made the function more specific by adding prefix HZD1PDIFF for 1 phase High Impedance Differential function & T3WPDIFF for 3 winding Low Impedance differential protection, same may be used.

## 7RW_99LV
400kV ICT-99LV (7RW)
Sr. No. | Voltage Level | Feeder Name | Source | NAME (BAY-701 ICT-1)
|  |  |  | Signal Decription | INFORMATION TYPE | Telegram Address | POSITION | EVENT | ALARM
BINARY INPUT (Single Point)
1 | 400kV | 400kV ICT | 7RW | 64.2 R_Y_B_SP RELAY UNHEALTHY | SP | B701_99LVCTRL$GGIO1$ST$SPCSO1:0 | stVal | √ | √
2 |  |  |  | 67.1 LV RELAY UNHEALTHY | SP | B701_99LVCTRL$GGIO1$ST$SPCSO4:0 | stVal | √ | √
3 |  |  |  | RAPID PRESSURE TRIP Y-PH | SP | B701_99LVCTRL$GGIO1$ST$SPCSO2:0 | stVal | √ | √
4 |  |  |  | OIL FLOW SENSITIVE VALVE TRIP B PH | SP | B701_99LVCTRL$GGIO1$ST$SPCSO5:0 | stVal | √ | √
5 |  |  |  | OIL FLOW SENSITIVE VALVE TRIP SP PH |  | B701_99LVCTRL$GGIO1$ST$SPCSO3:0
6 |  |  |  | OVERFLUX STAGE-2 OPERATED | SP | B701_99LVPROT$PVPH2$ST$Op | general | √ | √
7 |  |  |  | OVERFLUX STAGE-2 PICKUP | SP | B701_99LVPROT$PVPH2$ST$Str | general | √
8 |  |  |  | OVERFLUX STAGE-1 OPERATED | SP | B701_99LVPROT$PVPH1$ST$Op | general | √ | √
9 |  |  |  | OVERFLUX STAGE-1 PICKUP | SP | B701_99LVPROT$PVPH1$ST$Str | general | √
10 |  |  |  | GENERAL TRIP | SP | B701_99LVPROT$PTRC1$ST$Tr | general | √ | √
11 |  |  |  | GENERAL PICKUP | SP | B701_99LVPROT$PTRC1$ST$Str | general | √
12 |  |  |  | DEVICE HEALTHY | SP | B701_99LVPROT$LPHD1$ST$PhyHealth:0 | stVal:1 | √
13 |  |  |  | TIME SYNCHRONISATION ERROR | SP | B701_99LVEXT$pdGGIO2$ST$SPCSO4:0 | stVal | √ | √
14 |  |  |  | OVERFLUX ALARM | SP | B701_99LVEXT$pdGGIO84$ST$SPCSO55:0 | stVal | √ | √
15 |  |  |  | GOOSE RECEIPT FAIL/TROUBLE | SP | B701_99LVCTRL$GGIO1$ST$SPCSO7:0 | stVal | √ | √
16 |  |  |  | SETTINGS CHANGED |  |  |  | √ | √
17 |  |  |  | RELAY IN TEST MODE |  |  |  | √ | √
Note: 1. Additional signal for CB Trouble, Mechanical trips, alarms etc as per scheme & As per standard DR signal requirement the input not considered in HMI signal list 2. 5 Nos of GGIO signal need to be configured as SPARE till the SCADA Database 3. The Logical Device LD is for reference only and vendors may use the same as per their own stndardized way, however the logical nodes used are to be used only as specified. 4. If the logical nodes have been made more specific under the same logical node class by adding prefixes, same can be used as per the application. For example, PDIFF has been specified for all types of differential functions, but if some vendor, under the same logical node class, made the function more specific by adding prefix HZD1PDIFF for 1 phase High Impedance Differential function & T3WPDIFF for 3 winding Low Impedance differential protection, same may be used.

## 7UT85_99HV
400kV ICT- 99HV-(7UT85)
Sr. No. | Voltage Level | Feeder Name | Source | NAME (BAY-701 ICT-1)
|  |  |  | Signal Decription | INFORMATION TYPE | Telegram Address | POSITION | EVENT | ALARM
BINARY INPUT (Single Point)
1 | 400kV | 400kV ICT | 7UT85 | TIME SYNCHRONISATION ERROR | SP | B701_87T_1_99HVApplication$LPHD0$ST$ClkFail | stVal | √ | √
2 |  |  |  | MAIN CB OPEN | SP | B701_87T_1_99HVApplication$USER1$ST$SPS | stVal | √
3 |  |  |  | MAIN CB CLOSE | SP | B701_87T_1_99HVApplication$USER1$ST$SPS1 | stVal | √
4 |  |  |  | REF PROTECTION OPERATED | SP | B701_87T_1_99HVApplication$USER1$ST$SPS11 | stVal | √ | √
5 |  |  |  | 86 A/86 B RELAY OPERATED | SP | B701_87T_1_99HVApplication$USER1$ST$SPS12 | stVal | √ | √
6 |  |  |  | BUCHHOLZ 2 TRIP R-PH | SP | B701_87T_1_99HVApplication$USER1$ST$SPS13 | stVal | √ | √
7 |  |  |  | BUCHHOLZ 2 TRIP Y-PH | SP | B701_87T_1_99HVApplication$USER1$ST$SPS14 | stVal | √ | √
8 |  |  |  | BUCHHOLZ 2 TRIP B-PH | SP | B701_87T_1_99HVApplication$USER1$ST$SPS15 | stVal | √ | √
9 |  |  |  | BUCHHOLZ 1 ALARM R-PH | SP | B701_87T_1_99HVApplication$USER1$ST$SPS3 | stVal | √ | √
10 |  |  |  | BUCHHOLZ 1 ALARM Y-PH | SP | B701_87T_1_99HVApplication$USER1$ST$SPS4 | stVal | √ | √
11 |  |  |  | BUCHHOLZ 1ALARM B-PH | SP | B701_87T_1_99HVApplication$USER1$ST$SPS5 | stVal | √ | √
12 |  |  |  | BUCHHOLZ 1 ALARM SP-PH | SP | B701_87T_1_99HVApplication$USER1$ST$SPS10 | stVal | √ | √
13 |  |  |  | TIE CB OPEN | SP | B701_87T_1_99HVApplication$USER1$ST$SPS2 | stVal | √
14 |  |  |  | PRD1, 2 & 3 TRIP SP-PH | SP | B701_87T_1_99HVApplication$USER1$ST$SPS6 | stVal | √ | √
15 |  |  |  | PRD1, 2 & 3 TRIP R-PH | SP | B701_87T_1_99HVApplication$USER1$ST$SPS7 | stVal | √ | √
16 |  |  |  | PRD1, 2 & 3 TRIP Y-PH | SP | B701_87T_1_99HVApplication$USER1$ST$SPS8 | stVal | √ | √
17 |  |  |  | PRD1, 2 & 3 TRIP B-PH | SP | B701_87T_1_99HVApplication$USER1$ST$SPS9 | stVal | √ | √
18 |  |  |  | 2nd HARMONIC BLOCK PH-R | SP | B701_87T_1_99HVPTD1_87TrafoDiffProt1$TR_PDIF1$ST$Irs2HaDet | phsA | √
19 |  |  |  | 2nd HARMONIC BLOCK PH-Y | SP | B701_87T_1_99HVPTD1_87TrafoDiffProt1$TR_PDIF1$ST$Irs2HaDet | phsB | √
20 |  |  |  | 2nd HARMONIC BLOCK PH-B | SP | B701_87T_1_99HVPTD1_87TrafoDiffProt1$TR_PDIF1$ST$Irs2HaDet | phsC | √
21 |  |  |  | 5th HARMONIC BLOCK PH-R | SP | B701_87T_1_99HVPTD1_87TrafoDiffProt1$TR_PDIF1$ST$Irs5HaDet | phsA | √
22 |  |  |  | 5th HARMONIC BLOCK PH-Y | SP | B701_87T_1_99HVPTD1_87TrafoDiffProt1$TR_PDIF1$ST$Irs5HaDet | phsB | √
23 |  |  |  | 5th HARMONIC BLOCK PH-B | SP | B701_87T_1_99HVPTD1_87TrafoDiffProt1$TR_PDIF1$ST$Irs5HaDet | phsC | √
24 |  |  |  | DIFFERENTIAL TRIP | SP | B701_87T_1_99HVPTD1_87TrafoDiffProt1$TR_PDIF1$ST$Op | general | √ | √
25 |  |  |  | DIFFERENTIAL TRIP R-PH | SP | B701_87T_1_99HVPTD1_87TrafoDiffProt1$TR_PDIF1$ST$Op | phsA | √ | √
26 |  |  |  | DIFFERENTIAL TRIP Y-PH | SP | B701_87T_1_99HVPTD1_87TrafoDiffProt1$TR_PDIF1$ST$Op | phsB | √ | √
27 |  |  |  | DIFFERENTIAL TRIP B-PH | SP | B701_87T_1_99HVPTD1_87TrafoDiffProt1$TR_PDIF1$ST$Op | phsC | √ | √
28 |  |  |  | DIFFERENTIAL STAGE-1 TRIP | SP |  | general | √ | √
29 |  |  |  | DIFFERENTIAL STAGE-1 PICKUP
30 |  |  |  | DIFFERENTIAL STAGE-2 TRIP
31 |  |  |  | DIFFERENTIAL STAGE-2 PICKUP
34 |  |  |  | OVER FLUX TRIP | SP | B701_87T_1_99HVPTS1$PTRC1$ST$Op | general | √ | √
35 |  |  |  | OVERFLUX STAGE-2 TRIP | SP | B701_87T_1_99HVPTS1_24Overexcitation1$ODP_PVPH1$ST$Op | general | √ | √
36 |  |  |  | OVERFLUX STAGE-1 TRIP | SP | B701_87T_1_99HVPTS1_24Overexcitation1$ODP_PVPH2$ST$Op | general | √ | √
37 |  |  |  | OVERFLUX HV ALARM | SP | B701_87T_1_99HVEXT$pdGGIO84$ST$SPCSO55:0 | stVal | √ | √
38 |  |  |  | DEVICE HEALTHY | SP | B701_87T_1_99HVApplication$LPHD0$ST$PhyHealth:0 | stVal:1 | √
39 |  |  |  | GOOSE RECEIPT FAIL/TROUBLE | SP | B701_87T_1_99HVApplication$USER1$ST$SPS16 | stVal | √ | √
40 |  |  |  | SETTINGS CHANGED |  |  |  | √ | √
41 |  |  |  | RELAY IN TEST MODE |  |  |  | √ | √
Note: 1. Additional signal for CB Trouble, Mechanical trips, alarms etc as per scheme & As per standard DR signal requirement the input not considered in HMI signal list 2. 5 Nos of GGIO signal need to be configured as SPARE till the SCADA Database 3. The Logical Device LD is for reference only and vendors may use the same as per their own stndardized way, however the logical nodes used are to be used only as specified. 4. If the logical nodes have been made more specific under the same logical node class by adding prefixes, same can be used as per the application. For example, PDIFF has been specified for all types of differential functions, but if some vendor, under the same logical node class, made the function more specific by adding prefix HZD1PDIFF for 1 phase High Impedance Differential function & T3WPDIFF for 3 winding Low Impedance differential protection, same may be used.

## 21R_1_7SA522
400kV BUS REACTOR (7SA522)
Sr. No. | Voltage Level | Feeder Name | Source
Signal Decription
[5 empty] | INFORMATION TYPE | Telegram Address | POSITION | Event | Alarm
BINARY INPUT (Single Point)
1 | 400kV | 400kV BUS REACTOR | 7SA522 | GOOSE RECEIPT FAIL/TROUBLE | SP | B403_21R_1CTRL$GGIO1$ST$SPCSO1:0 | stVal | √ | √
2 |  |  |  | WTI TRIP B-PH | SP | B403_21R_1CTRL$GGIO1$ST$SPCSO4:0 | stVal | √ | √
3 |  |  |  | WTI TRIP Y-PH | SP | B403_21R_1CTRL$GGIO1$ST$SPCSO2:0 | stVal | √ | √
4 |  |  |  | 64.2-R_Y_B SP RELAY UNHEALTHY | SP | B403_21R_1CTRL$GGIO1$ST$SPCSO3:0 | stVal | √ | √
5 |  |  |  | TIME SYNCHRONISATION ERROR | SP | B403_21R_1EXT$pdGGIO2$ST$SPCSO4:0 | stVal | √ | √
6 |  |  |  | BACKUP IMPEDENCE ZONE-1 START | SP | B403_21R_1PROT$PDIS1$ST$Str | general | √
7 |  |  |  | BACKUP IMPEDENCE ZONE-1 TRIP | SP | B403_21R_1PROT$PDIS1$ST$Op | general | √ | √
8 |  |  |  | BACKUP IMPEDENCE R-PH TRIP | SP | B403_21R_1PROT$PDIS1$ST$Op | phsA | √ | √
9 |  |  |  | BACKUP IMPEDENCE Y-PH TRIP | SP | B403_21R_1PROT$PDIS1$ST$Op | phsB | √ | √
10 |  |  |  | BACKUP IMPEDENCE B-PH TRIP | SP | B403_21R_1PROT$PDIS1$ST$Op | phsC | √ | √
11 |  |  |  | BACKUP IMPEDENCE BLOCKED | SP | B403_21R_1PROT$PDIS1$ST$Blk | stVal | √
12 |  |  |  | GENERAL TRIP | SP | B403_21R_1PROT$PTRC1$ST$Tr | general | √ | √
13 |  |  |  | NON-DIRECTIONAL OVERCURRENT TRIP | SP | B403_21R_1PROT$PTOC2$ST$Op | general | √ | √
14 |  |  |  | NON-DIRECTIONAL OVERCURRENT START | SP | B403_21R_1PROT$PTOC2$ST$Str | general | √
15 |  |  |  | DEVICE HEALTHY | SP | B403_21R_1PROT$LPHD1$ST$PhyHealth:0 | stVal:1 | √
16 |  |  |  | NO VOLTAGE IN LINE | SP | B403_21R_1EXT$pdGGIO3$ST$SPCSO40:0 | stVal | √ | √
17 |  |  |  | VT FUSE FAILURE | SP | B403_21R_1EXT$pdGGIO3$ST$SPCSO42:0 | stVal | √ | √
18 |  |  |  | SETTINGS CHANGED |  |  |  | √ | √
19 |  |  |  | RELAY IN TEST MODE |  |  |  | √ | √
20 |  |  |  | NON-DIRECTIONAL EARTHFAULT TRIP |  |  |  | √ | √
21 |  |  |  | NON-DIRECTIONAL EARTHFAULT START |  |  |  | √
Note: 1. Additional signal for CB Trouble, etc as per scheme & As per standard DR signal requirement the input not considered in HMI signal list 2. 5 Nos of GGIO signal need to be configured as SPARE till the SCADA Database 3. The Logical Device LD is for reference only and vendors may use the same as per their own stndardized way, however the logical nodes used are to be used only as specified. 4. If the logical nodes have been made more specific under the same logical node class by adding prefixes, same can be used as per the application. For example, PDIFF has been specified for all types of differential functions, but if some vendor, under the same logical node class, made the function more specific by adding prefix HZD1PDIFF for 1 phase High Impedance Differential function & T3WPDIFF for 3 winding Low Impedance differential protection, same may be used.