## LEGEND
SIEMENS SCADA GENERAL SIGNAL LIST FOR VARIOUS PROTECTION & CONTROL SIGNALS - REV03 (INDEX)
Sheet Ref. | IED MODEL | IED SYMBOLIC NAME(TYPICAL) | APPLICATION | IED NAME IN SCD | Additional Remarks
1 | 6MD66 | BCU | ICT BCU | STNM4XXBCU | BCU is for each bay so 4XX refers to Bay
2 | 7SJ80 | 7SJ8_64T.2B | REF RELAY PHASE B FOR ICT | STNM4XXTREFB | Bay No. 4XX will be always the main bay number for the ICT feeder
3 | 7UT85 | 7UT85_99HV | ICT DIFFERENTIAL RELAY | STNM4XXTDIF | Bay No. 4XX will be always the main bay number for the ICT feeder
4 | 7SA522 | 7SA522_21R | ICT BACKUP IMPEDANCE RELAY | STNM4XXTBUIMP | Bay No. 4XX will be always the main bay number for the ICT feeder
NOTE 1: The characters "STNM" stand for Substation Name with maximum 4 characters, this code will be given by POWERGRID for each project.
NOTE 2: The characters "4XX" stand for Bay name, example if the bay no 401 then same has to be implemented like STNM401BCU

## BCU
400kV LINE REACTOR-(BCU)
Sr. No. | Voltage Level | Feeder Name | Source
|  |  |  | SIGNAL DESCRIPTION | INFORMATION TYPE | Telegram Address | POSITION | EVENT | ALARM
BINARY INPUT (Double Point)
1 | 400kV | 400kV LINE REACTOR | BCU | CB R-PH POSITION | DP | B707_BCUCBs3$XCBR1$ST$Pos:2 | stVal | √
2 |  |  |  | CB Y-PH POSITION | DP | B707_BCUCBs1$XCBR1$ST$Pos:2 | stVal | √
3 |  |  |  | CB B-PH POSITION | DP | B707_BCUCBs2$XCBR1$ST$Pos:2 | stVal | √
4 |  |  |  | CB POSITION | DP | B707_BCUCB$CSWI1$ST$Pos:2 | stVal | √
5 |  |  |  | 89AE POSITION | DP | B707_BCU89AE$CSWI4$ST$Pos:2 | stVal | √
6 |  |  |  | 89BE POSITION | DP | B707_BCU89BE$CSWI5$ST$Pos:2 | stVal | √
7 |  |  |  | 89LRE1 POSITION | DP | B707_BCU89LE$CSWI7$ST$Pos:2 | stVal | √
8 |  |  |  | 89RE-B POSITION | DP | B707_BCU89REB$CSWI9$ST$Pos:2 | stVal | √
9 |  |  |  | 89RE-R POSITION | DP | B707_BCU89RER$CSWI9$ST$Pos:2 | stVal | √
10 |  |  |  | 89RE-Y POSITION | DP | B707_BCU89REY$CSWI9$ST$Pos:2 | stVal | √
11 |  |  |  | 89RSE1-B POSITION | DP | B707_BCU89RSE1B$CSWI11$ST$Pos:2 | stVal | √
12 |  |  |  | 89RSE1-R POSITION | DP | B707_BCU89RSE1R$CSWI11$ST$Pos:2 | stVal | √
13 |  |  |  | 89RSE1-Y POSITION | DP | B707_BCU89RSE1Y$CSWI11$ST$Pos:2 | stVal | √
14 |  |  |  | 89A POSITION | DP | B707_BCU89A$CSWI2$ST$Pos:2 | stVal | √
15 |  |  |  | 89B POSITION | DP | B707_BCU89B$CSWI3$ST$Pos:2 | stVal | √
16 |  |  |  | 89LR POSITION | DP | B707_BCU89L$CSWI6$ST$Pos:2 | stVal | √
17 |  |  |  | 89R-B POSITION | DP | B707_BCU89RB$CSWI8$ST$Pos:2 | stVal | √
18 |  |  |  | 89R-R POSITION | DP | B707_BCU89RR$CSWI8$ST$Pos:2 | stVal | √
19 |  |  |  | 89R-Y POSITION | DP | B707_BCU89RY$CSWI8$ST$Pos:2 | stVal | √
20 |  |  |  | 89RS1_RS2-B POSITION | DP | B707_BCU89RS1RS2B$CSWI10$ST$Pos:2 | stVal | √
21 |  |  |  | 89RS1_RS2-R POSITION | DP | B707_BCU89RS1RS2R$CSWI10$ST$Pos:2 | stVal | √
22 |  |  |  | 89RS1_RS2-Y POSITION | DP | B707_BCU89RS1RS2Y$CSWI10$ST$Pos:2 | stVal | √
S89R-R POSITION
S89R-Y POSITION
S89R-B POSITION
23 |  |  |  | NGR CB POSITION | DP | B707_BCUNGRCB$CSWI1$ST$Pos:2 | stVal | √
24
25 |  |  |  | BINARY INPUT (Single Point)
26
27 |  |  |  | AUX POWER FAIL | SP | B707_BCUApplication$LPHD0$ST$AuxPwrFail | stVal | √ | √
28 |  |  |  | TIME SYNCHRONISATION ERROR | SP | B707_BCUApplication$LMTS0$ST$TmSynErr | stVal | √ | √
29 |  |  |  | GOOSE RECEIPT FAIL/TROUBLE | SP | B707_BCUApplication$LLN0$ST$SPS | stVal | √ | √
30 |  |  |  | BCU MODE | SP | B707_BCUApplication$LLN0$ST$LocKey | stVal | √
31 |  |  |  | CB DC SUPPLY-1/2 FAIL | SP | B707_BCUApplication$USER3$ST$SPS1 | stVal | √ | √
32 |  |  |  | CB SPRING CHARGED B-PH | SP | B707_BCUApplication$USER3$ST$SPS4 | stVal | √
33 |  |  |  | CB SPRING CHARGED R-PH | SP | B707_BCUApplication$USER3$ST$SPS2 | stVal | √
34 |  |  |  | CB SPRING CHARGED Y-PH | SP | B707_BCUApplication$USER3$ST$SPS3 | stVal | √
35 |  |  |  | CB SF6 GAS PRESSURE LOCKOUT | SP | B707_BCUApplication$USER3$ST$SPS | stVal | √ | √
36 |  |  |  | CT SF6 GAS PRESSURE REFILL LOW ALARM | SP | B707_BCUApplication$USER1$ST$SPS | stVal | √ | √
37 |  |  |  | CT SF6 GAS PRESSURE LOCKOUT | SP | B707_BCUApplication$USER1$ST$SPS1 | stVal | √ | √
38 |  |  |  | A/R BLOCK MAIN1-1 | SP | B707_BCUApplication$USER8$ST$SPS6 | stVal | √ | √
39 |  |  |  | A/R BLOCK MAIN-2 | SP | B707_BCUApplication$USER8$ST$SPS7 | stVal | √ | √
40 |  |  |  | SPARE REACTOR B-PH SELECTED | SP | B707_BCUApplication$USER8$ST$SPS2 | stVal | √
41 |  |  |  | SPARE REACTOR R-PH SELECTED | SP | B707_BCUApplication$USER8$ST$SPS | stVal | √
42 |  |  |  | SPARE REACTOR Y-PH SELECTED | SP | B707_BCUApplication$USER8$ST$SPS1 | stVal | √
43 |  |  |  | SURGE ARRESTER B-PH | SP | B707_BCUApplication$USER8$ST$SPS5 | stVal | √
44 |  |  |  | SURGE ARRESTER R-PH | SP | B707_BCUApplication$USER8$ST$SPS3 | stVal | √
45 |  |  |  | SURGE ARRESTER Y-PH | SP | B707_BCUApplication$USER8$ST$SPS4 | stVal | √
46 |  |  |  | 86A TRIP RELAY SUPERVISION | SP | B707_BCUApplication$USER9$ST$SPS2 | stVal | √ | √
47 |  |  |  | 86A TRIP RELAY OPERATED | SP | B707_BCUApplication$USER9$ST$SPS1 | stVal | √ | √
48 |  |  |  | 86B TRIP RELAY SUPERVISION | SP | B707_BCUApplication$USER9$ST$SPS6 | stVal | √ | √
49 |  |  |  | 86B TRIP RELAY OPERATED | SP | B707_BCUApplication$USER9$ST$SPS5 | stVal | √ | √
50 |  |  |  | CARRIER CHANNEL-1 OUT | SP | B707_BCUApplication$USER9$ST$SPS3 | stVal | √ | √
51 |  |  |  | CARRIER CHANNEL-2 OUT | SP | B707_BCUApplication$USER9$ST$SPS7 | stVal | √ | √
52 |  |  |  | MAIN-2 RELAY UNHEALTHY | SP | B707_BCUApplication$USER9$ST$SPS8 | stVal | √ | √
53 |  |  |  | EMERGENCY/MANUAL CB TRIP | SP | B707_BCUApplication$USER9$ST$SPS10 | stVal | √ | √
54 |  |  |  | MAIN TANK HIGH LEVEL ALARM B-PH | SP | B707_BCUApplication$USER9$ST$SPS25 | stVal | √ | √
55 |  |  |  | MAIN TANK HIGH LEVEL ALARM R-PH | SP | B707_BCUApplication$USER9$ST$SPS15 | stVal | √ | √
56 |  |  |  | MAIN TANK HIGH LEVEL ALARM Y-PH | SP | B707_BCUApplication$USER9$ST$SPS20 | stVal | √ | √
57 |  |  |  | MAIN TANK LOW LEVEL ALARM B-PH | SP | B707_BCUApplication$USER9$ST$SPS24 | stVal | √ | √
58 |  |  |  | MAIN TANK LOW LEVEL ALARM R-PH | SP | B707_BCUApplication$USER9$ST$SPS14 | stVal | √ | √
59 |  |  |  | MAIN TANK LOW LEVEL ALARM Y-PH | SP | B707_BCUApplication$USER9$ST$SPS19 | stVal | √ | √
60 |  |  |  | OTI ALARM B-PH | SP | B707_BCUApplication$USER9$ST$SPS23 | stVal | √ | √
61 |  |  |  | OTI ALARM R-PH | SP | B707_BCUApplication$USER9$ST$SPS13 | stVal | √ | √
62 |  |  |  | OTI ALARM Y-PH | SP | B707_BCUApplication$USER9$ST$SPS18 | stVal | √ | √
63 |  |  |  | SPEECH CHANNEL FAIL | SP | B707_BCUApplication$USER9$ST$SPS9 | stVal | √ | √
64 |  |  |  | CB TC-1 FAULTY | SP | B707_BCUApplication$USER9$ST$SPS | stVal | √ | √
65 |  |  |  | CB TC-2 FAULTY | SP | B707_BCUApplication$USER9$ST$SPS4 | stVal | √ | √
66 |  |  |  | WTI ALARM B-PH | SP | B707_BCUApplication$USER9$ST$SPS22 | stVal | √ | √
67 |  |  |  | WTI ALARM R-PH | SP | B707_BCUApplication$USER9$ST$SPS12 | stVal | √ | √
68 |  |  |  | WTI ALARM Y-PH | SP | B707_BCUApplication$USER9$ST$SPS17 | stVal | √ | √
69 |  |  |  | CB POLE DESCREPENCY ALARM | SP | B707_BCUApplication$USER2$ST$SPS1 | stVal | √ | √
70 |  |  |  | CB SF6 GAS PRESSURE REFILL LOW ALARM | SP | B707_BCUApplication$USER2$ST$SPS | stVal | √ | √
71 |  |  |  | TIME SYNCHRONISATION ERROR | SP | B707_BCUApplication$LTMS0$ST$TmSynErr | stVal | √ | √
72 |  |  |  | BUS-1 VT RESET | SP | B707_BCUApplication$USER11$ST$SPS1 | stVal | √
73 |  |  |  | BUS-2 VT RESET | SP | B707_BCUApplication$USER11$ST$SPS3 | stVal | √
74 |  |  |  | LINE VT RESET | SP | B707_BCUApplication$USER11$ST$SPS5 | stVal | √
75 |  |  |  | BUS-1 VT SELECTED | SP | B707_BCUApplication$USER11$ST$SPS | stVal | √
76 |  |  |  | BUS-2 VT SELECTED | SP | B707_BCUApplication$USER11$ST$SPS2 | stVal | √
77 |  |  |  | LINE VT SELECTED | SP | B707_BCUApplication$USER11$ST$SPS4 | stVal | √
78 |  |  |  | EMERGENCY/MANUAL CB CLOSE | SP | B707_BCUCB$GAPC2$ST$Detected | stVal | √
79 |  |  |  | A/R FUNCTION ON | SP | B707_BCUCB1_79AutoReclosing$GEN_RREC1$ST$On | stVal | √
80 |  |  |  | CB READY FOR A/R | SP | B707_BCUCB1_79AutoReclosing$GEN_RREC1$ST$AutoRecSt:0 | stVal:1 | √
81 |  |  |  | A/R UNSUCCESSFUL | SP | B707_BCUCB1_79AutoReclosing$GEN_RREC1$ST$AutoRecSt:0 | stVal:10 | √ | √
82 |  |  |  | A/R SUCCESSFUL | SP | B707_BCUCB1_79AutoReclosing$GEN_RREC1$ST$Successful | stVal | √
83 |  |  |  | CB NOT READY | SP | B707_BCUCB1_79AutoReclosing$GEN_RREC1$ST$CBnotRdy | stVal | √
84 |  |  |  | A/R CLOSE COMMAND INDICATION | SP | B707_BCUCB1_79AutoReclosing$GEN_RREC1$ST$OpCls | general | √
85 |  |  |  | A/R IN PROGRESS | SP | B707_BCUCB1_79AutoReclosing$GEN_RREC1$ST$RecInit | stVal | √
86 |  |  |  | A/R FUNCTION OFF | SP | B707_BCUCB1_79AutoReclosing$GEN_RREC1$ST$Off | stVal | √
87 |  |  |  | A/R FUNCTION ON | SP | B707_BCUCB1_79AutoReclosing$GEN_RREC1$ST$On | stVal | √
88 |  |  |  | CB POSITION NO SYNC | SP | B707_BCUCB$CSWI1$ST$Pos | noSync | √
89 | 400kV | 400kV LINE REACTOR | BCU | CB CLOSE INTERLOCK | SP | B707_BCUCB$CILO1$ST$EnaCls | stVal | √
90 |  |  |  | 89AE OPEN INTERLOCK | SP | B707_BCU89AE$CILO1$ST$EnaOpn | stVal | √
91 |  |  |  | 89BE OPEN INTERLOCK | SP | B707_BCU89BE$CILO1$ST$EnaOpn | stVal | √
92 |  |  |  | 89LE OPEN INTERLOCK | SP | B707_BCU89LE$CILO1$ST$EnaOpn | stVal | √
93 |  |  |  | 89RE-B-PH OPEN INTERLOCK | SP | B707_BCU89REB$CILO1$ST$EnaOpn | stVal | √
94 |  |  |  | 89RE-R-PH OPEN INTERLOCK | SP | B707_BCU89RER$CILO1$ST$EnaOpn | stVal | √
95 |  |  |  | 89RE-Y-PH OPEN INTERLOCK | SP | B707_BCU89REY$CILO1$ST$EnaOpn | stVal | √
96 |  |  |  | 89RSE1-B-PH OPEN INTERLOCK | SP | B707_BCU89RSE1B$CILO1$ST$EnaOpn | stVal | √
97 |  |  |  | 89RSE1-R-PH OPEN INTERLOCK | SP | B707_BCU89RSE1R$CILO1$ST$EnaOpn | stVal | √
98 |  |  |  | 89RSE1-Y-PH OPEN INTERLOCK | SP | B707_BCU89RSE1Y$CILO1$ST$EnaOpn | stVal | √
99 |  |  |  | 89A-PH OPEN INTERLOCK | SP | B707_BCU89A$CILO1$ST$EnaOpn | stVal | √
100 |  |  |  | 89B-PH OPEN INTERLOCK | SP | B707_BCU89B$CILO1$ST$EnaOpn | stVal | √
101 |  |  |  | 89L-PH OPEN INTERLOCK | SP | B707_BCU89L$CILO1$ST$EnaOpn | stVal | √
102 |  |  |  | 89R-B-PH OPEN INTERLOCK | SP | B707_BCU89RB$CILO1$ST$EnaOpn | stVal | √
103 |  |  |  | 89R-R-PH OPEN INTERLOCK | SP | B707_BCU89RR$CILO1$ST$EnaOpn | stVal | √
104 |  |  |  | 89R-Y-PH OPEN INTERLOCK | SP | B707_BCU89RY$CILO1$ST$EnaOpn | stVal | √
105 |  |  |  | 89RS1_RS2-B-PH OPEN INTERLOCK | SP | B707_BCU89RS1RS2B$CILO1$ST$EnaOpn | stVal | √
106 |  |  |  | 89RS1_RS2-R-PH OPEN INTERLOCK | SP | B707_BCU89RS1RS2R$CILO1$ST$EnaOpn | stVal | √
107 |  |  |  | 89RS1_RS2-Y-PH OPEN INTERLOCK | SP | B707_BCU89RS1RS2Y$CILO1$ST$EnaOpn | stVal | √
108 |  |  |  | NGR CB CLOSE INTERLOCK | SP | B707_BCUNGRCB$CILO1$ST$EnaCls | stVal | √
109 |  |  |  | RELAY IN TEST MODE |  |  |  | √ | √
110 |  |  |  | SETTINGS CHANGED |  |  |  | √ | √
111 |  |  |  | REACTOR-n R PH OUT OF SERVICE |  |  |  | √
112 |  |  |  | REACTOR-n Y PH OUT OF SERVICE |  |  |  | √
113 |  |  |  | REACTOR-n B PH OUT OF SERVICE |  |  |  | √
114 |  |  |  | REACTOR SPARE PH IN SERVICE IN REACTOR-N |  |  |  | √
115 |  |  |  | CB MANUAL TRIP |  |  |  | √
116 |  |  |  | CB MANUAL CLOSE |  |  |  | √
117 |  |  |  | BUSBAR OPERATED |  |  |  | √ | √
118 |  |  |  | BCU IN LOCAL/REMOTE |  |  |  | √
119 |  |  |  | CB TC-1 R-PHASE FAULTY |  |  |  | √ | √
120 |  |  |  | CB TC-1 Y-PHASE FAULTY |  |  |  | √ | √
121 |  |  |  | CB TC-1 B-PHASE FAULTY |  |  |  | √ | √
122 |  |  |  | CB TC-2 R-PHASE FAULTY |  |  |  | √ | √
123 |  |  |  | CB TC-2 Y-PHASE FAULTY |  |  |  | √ | √
124 |  |  |  | CB TC-2 B-PHASE FAULTY |  |  |  | √ | √
125 |  |  |  | NGR CB TC-1 FAULTY
125 |  |  |  | NGR CB TC-2 FAULTY
125 |  |  |  | NGR CB DC FAULTY
125 |  |  |  | NGR CB AC FAULTY
125 |  |  |  | NGR CB SPRING NOT CHARGED
125 |  |  |  | NGR CB SF6 GAS LOW
125 |  |  |  | NGR CB SF6 CB TROUBLE ALARM
125 |  |  |  | NGR MECHANICAL TRIPPING IF ASSIGNED
126
127 |  |  |  | MEASUREMENTS
128
129 |  |  |  | POWER FACTOR | ME_FL | B707_BCUVI3p1_OperationalValues$PPRE_MMXU1$MX$TotPF:1 | mag$f
130 |  |  |  | FREQUENCY | ME_FL | B707_BCUVI3p1_OperationalValues$PPRE_MMXU1$MX$Hz:1 | mag$f
131 |  |  |  | ACTIVE POWER | ME_FL | B707_BCUVI3p1_OperationalValues$PPRE_MMXU1$MX$TotW:1 | mag$f
132 |  |  |  | REACTIVE POWER | ME_FL | B707_BCUVI3p1_OperationalValues$PPRE_MMXU1$MX$TotVAr:1 | mag$f
133 |  |  |  | APPARENT POWER | ME_FL | B707_BCUVI3p1_OperationalValues$PPRE_MMXU1$MX$TotVA:1 | mag$f
134 |  |  |  | I-R-PH CURRENT | ME_FL | B707_BCUVI3p1_OperationalValues$RPRE_MMXU1$MX$A:1 | phsA$cVal$mag$f
135 |  |  |  | I-Y-PH CURRENT | ME_FL | B707_BCUVI3p1_OperationalValues$RPRE_MMXU1$MX$A:1 | phsB$cVal$mag$f
136 |  |  |  | I-B-PH CURRENT | ME_FL | B707_BCUVI3p1_OperationalValues$RPRE_MMXU1$MX$A:1 | phsC$cVal$mag$f
137 |  |  |  | R-Y VOLTAGE | ME_FL | B707_BCUVI3p1_OperationalValues$RPRE_MMXU1$MX$PPV:1 | phsAB$cVal$mag$f
138 |  |  |  | Y-B VOLTAGE | ME_FL | B707_BCUVI3p1_OperationalValues$RPRE_MMXU1$MX$PPV:1 | phsBC$cVal$mag$f
139 |  |  |  | B-R VOLYAGE | ME_FL | B707_BCUVI3p1_OperationalValues$RPRE_MMXU1$MX$PPV:1 | phsCA$cVal$mag$f
140
141 |  |  |  | COMMANDS
142
143 |  |  |  | CB CONTROL | DC | B707_BCUCB$CSWI1$CO$Pos:8 | Oper$ctlVal | √
144 |  |  |  | 89AE CONTROL | DC | B707_BCU89AE$CSWI4$CO$Pos:8 | Oper$ctlVal | √
145 |  |  |  | 89BE CONTROL | DC | B707_BCU89BE$CSWI5$CO$Pos:8 | Oper$ctlVal | √
146 |  |  |  | 89LE CONTROL | DC | B707_BCU89LE$CSWI7$CO$Pos:8 | Oper$ctlVal | √
147 |  |  |  | 89RE-B CONTROL | DC | B707_BCU89REB$CSWI9$CO$Pos:8 | Oper$ctlVal | √
148 |  |  |  | 89RE-R CONTROL | DC | B707_BCU89RER$CSWI9$CO$Pos:8 | Oper$ctlVal | √
149 |  |  |  | 89RE-Y CONTROL | DC | B707_BCU89REY$CSWI9$CO$Pos:8 | Oper$ctlVal | √
150 |  |  |  | 89RSE1-B CONTROL | DC | B707_BCU89RSE1B$CSWI11$CO$Pos:8 | Oper$ctlVal | √
151 |  |  |  | 89RSE1-R CONTROL | DC | B707_BCU89RSE1R$CSWI11$CO$Pos:8 | Oper$ctlVal | √
152 |  |  |  | 89RSE1-Y CONTROL | DC | B707_BCU89RSE1Y$CSWI11$CO$Pos:8 | Oper$ctlVal | √
153 |  |  |  | 89A CONTROL | DC | B707_BCU89A$CSWI2$CO$Pos:8 | Oper$ctlVal | √
154 |  |  |  | 89B CONTROL | DC | B707_BCU89B$CSWI3$CO$Pos:8 | Oper$ctlVal | √
155 |  |  |  | 89L CONTROL | DC | B707_BCU89L$CSWI6$CO$Pos:8 | Oper$ctlVal | √
156 |  |  |  | 89R-B CONTROL | DC | B707_BCU89RB$CSWI8$CO$Pos:8 | Oper$ctlVal | √
157 |  |  |  | 89R-R CONTROL | DC | B707_BCU89RR$CSWI8$CO$Pos:8 | Oper$ctlVal | √
158 |  |  |  | 89R-Y CONTROL | DC | B707_BCU89RY$CSWI8$CO$Pos:8 | Oper$ctlVal | √
159 |  |  |  | 89RS1_RS2-B CONTROL | DC | B707_BCU89RS1RS2B$CSWI10$CO$Pos:8 | Oper$ctlVal | √
160 |  |  |  | 89RS1_RS2-R CONTROL | DC | B707_BCU89RS1RS2R$CSWI10$CO$Pos:8 | Oper$ctlVal | √
161 |  |  |  | 89RS1_RS2-Y CONTROL | DC | B707_BCU89RS1RS2Y$CSWI10$CO$Pos:8 | Oper$ctlVal | √
162 |  |  |  | NGR CB CONTROL | DC | B707_BCUNGRCB$CSWI1$CO$Pos:8 | Oper$ctlVal | √
163 |  |  |  | CB CONTROL NO SYNC | SC | B707_BCUCB$CSWI1$CO$Pos | Oper$noSync | √
164 |  |  |  | NGR CB CONTROL NO SYNC | SC | B707_BCUNGRCB$CSWI1$CO$Pos | Oper$noSync | √
165 |  |  |  | 86B TRIP RELAY RESET COMMAND | SC | B707_BCUApplication$USER2$CO$SPC:8 | Oper$ctlVal | √
166 |  |  |  | 86A TRIP RELAY RESET COMMAND | SC | B707_BCUApplication$USER2$CO$SPC1:8 | Oper$ctlVal | √
167 |  |  |  | A/R ON CONTROL | SC | B707_BCUApplication$USER12$CO$SPC:8 | Oper$ctlVal | √
168 |  |  |  | A/R OFF CONTROL | SC | B707_BCUApplication$USER12$CO$SPC1:8 | Oper$ctlVal | √
Note: 1. All the switchgear status signals as per the actual primary equipment status. 2. Additional signal for CB Trouble, etc as per scheme 3. 10 Nos of GGIO signal need to be configured as SPARE till the SCADA Database 4. The Logical Device LD is for reference only and vendors may use the same as per their own stndardized way, however the logical nodes used are to be used only as specified. 5. If the logical nodes have been made more specific under the same logical node class by adding prefixes, same can be used as per the application. For example, PDIFF has been specified for all types of differential functions, but if some vendor, under the same logical node class, made the function more specific by adding prefix HZD1PDIFF for 1 phase High Impedance Differential function & T3WPDIFF for 3 winding Low Impedance differential protection, same may be used.

## 7SA52_21R1
400kV LINE REACTOR-(7SA52)
Sr. No. | Voltage Level | Feeder Name | Source
|  |  |  | SIGNAL DESCRIPTION | INFORMATION TYPE | Telegram Address | POSITION | REMARKS | Events | Alarms
BINARY INPUT (Single Point)
1 | 400kV | Line Reactor | 7SA522 | WTI TRIP B-PH | SP | B407_21R_1CTRL$GGIO1$ST$SPCSO2:0 | stVal |  | √ | √
2 |  |  |  | WTI TRIP Y-PH | SP | B407_21R_1CTRL$GGIO1$ST$SPCSO1:0 | stVal |  | √ | √
3 |  |  |  | OTI TRIP B-PH | SP | B407_64R_2CTRL$GGIO1$ST$SPCSO4:0 | stVal |  | √ | √
4 |  |  |  | OTI TRIP R-PH | SP | B407_64R_2CTRL$GGIO1$ST$SPCSO5:0 | stVal |  | √ | √
5 |  |  |  | BUCHHOLZ-1/2 TRIP R-PH | SP | B407_21R_1CTRL$GGIO1$ST$SPCSO3:0 | stVal |  | √ | √
6 |  |  |  | BUCHHOLZ-1/2 TRIP Y-PH | SP | B407_21R_1CTRL$GGIO1$ST$SPCSO6:0 | stVal |  | √ | √
7 |  |  |  | BUCHHOLZ-1/2 TRIP B-PH | SP | B407_21R_1CTRL$xGGIO1$ST$SPCSO7:0 | stVal |  | √ | √
8 |  |  |  | NGR PRV TRIP
9 |  |  |  | BCU-1/2 RELAY FAIL
10 |  |  |  | REACTOR DC-2 FAIL
11 |  |  |  | GROUP-B PROTECTION RELAY FAIL
12 |  |  |  | BACKUP IMPEDENCE ZONE-1 PICKUP | SP | B407_21R_1PROT$PDIS1$ST$Str | general |  | √
13 |  |  |  | BACKUP IMPEDENCE ZONE-1 TRIP | SP | B407_21R_1PROT$PDIS1$ST$Op | general |  | √ | √
14 |  |  |  | BACKUP IMPEDENCE R-PH TRIP | SP | B407_21R_1PROT$PDIS1$ST$Op | phsA |  | √ | √
15 |  |  |  | BACKUP IMPEDENCE Y-PH TRIP | SP | B407_21R_1PROT$PDIS1$ST$Op | phsB |  | √ | √
16 |  |  |  | BACKUP IMPEDENCE B-PH TRIP | SP | B407_21R_1PROT$PDIS1$ST$Op | phsC |  | √ | √
17 |  |  |  | GENERAL TRIP | SP | B407_21R_1PROT$PTRC1$ST$Tr | general |  | √ | √
18 |  |  |  | BACKUP IMPEDENCE BLOCKED | SP | B407_21R_1PROT$PDIS1$ST$Blk | stVal |  | √
19 |  |  |  | DEVICE HEALTHY | SP | B407_21R_1PROT$LPHD1$ST$PhyHealth:0 | stVal:1 |  | √
20 |  |  |  | GOOSE RECEIPT FAIL/TROUBLE | SP | B407_21R_1CTRL$GGIO1$ST$SPCSO8:0 | stVal |  | √ | √
21 |  |  |  | VOLTAGE ABSENT | SP | B407_21R_1EXT$pdGGIO3$ST$SPCSO40:0 | stVal |  | √ | √
22 |  |  |  | VT FUSE FAILURE | SP | B407_21R_1EXT$pdGGIO3$ST$SPCSO42:0 | stVal |  | √ | √
23 |  |  |  | TIME SYNCHRONISATION ERROR | SP | B407_21R_2EXT$pdGGIO2$ST$SPCSO4:0 | stVal |  | √ | √
24 |  |  |  | BROKEN CONDUCTOR | SP | B407_21R_1EXT$pdGGIO4$ST$SPCSO3:0 | stVal |  | √ | √
25 |  |  |  | NON-DIRECTIONAL OVERCURRENT TRIP | SP | B407_21R_1PROT$PTOC2$ST$Op | general |  | √ | √
26 |  |  |  | NON-DIRECTIONAL OVERCURRENT START | SP | B407_21R_1PROT$PTOC2$ST$Str | general |  | √
27 |  |  |  | NON-DIRECTIONAL EARTHFAULT TRIP |  |  |  |  | √ | √
28 |  |  |  | NON-DIRECTIONAL EARTHFAULT START |  |  |  |  | √
29 |  |  |  | SETTINGS CHANGED |  |  |  |  | √
30 |  |  |  | RELAY IN TEST MODE |  |  |  |  | √
31 |  |  |  | NGR CLOSE COMMAND BY E/F PICKUP(5 SEC) |  |  |  |  | √ | √
32 |  |  |  | NGR CLOSE COMMAND BY MECH TRIP |  |  |  |  | √ | √
Note: 1. Additional signal for CB Trouble, etc as per scheme & As per standard DR signal requirement the input not considered in HMI signal list 2. 5 Nos of GGIO signal need to be configured as SPARE till the SCADA Database 3. The Logical Device LD is for reference only and vendors may use the same as per their own stndardized way, however the logical nodes used are to be used only as specified. 4. If the logical nodes have been made more specific under the same logical node class by adding prefixes, same can be used as per the application. For example, PDIFF has been specified for all types of differential functions, but if some vendor, under the same logical node class, made the function more specific by adding prefix HZD1PDIFF for 1 phase High Impedance Differential function & T3WPDIFF for 3 winding Low Impedance differential protection, same may be used.

## 7SJ8_64R2
400kV LINE REACTOR-(7SJ80)
Sr. No. | Voltage Level | Feeder Name | Source |  | NOTE: THESE SIGNAL STANDARDIZATION IS SCHEME BASED
|  |  |  | SIGNAL DESCRIPTION | INFORMATION TYPE | Telegram Address | POSITION | Events | Alarms
BINARY INPUT (Single Point)
1 | 400kV | 400kV LINE REACTOR | 7SJ80 | BUCHHOLZ TRIP B-PH | SP | B707_64R_2CTRL$GGIO1$ST$SPCSO5:0 | stVal | √ | √
2 |  |  |  | BUCHHOLZ TRIP R-PH | SP | B707_64R_2CTRL$GGIO1$ST$SPCSO1:0 | stVal | √ | √
3 |  |  |  | BUCHHOLZ TRIP Y-PH | SP | B707_64R_2CTRL$GGIO1$ST$SPCSO3:0 | stVal | √ | √
4 |  |  |  | OTI TRIP Y-PH | SP | B707_64R_2CTRL$GGIO1$ST$SPCSO4:0 | stVal | √ | √
5 |  |  |  | REF STAGE 1 TRIP | SP | B707_64R_2PROT$PTOC16$ST$Op | general | √ | √
6 |  |  |  | REF STAGE 1 PICKUP | SP | B707_64R_2PROT$PTOC16$ST$Str | general | √
7 |  |  |  | REF STAGE 2 TRIP | SP | B707_64R_2PROT$PTOC17$ST$Op | general | √ | √
8 |  |  |  | REF STAGE 2 PICKUP | SP | B707_64R_2PROT$PTOC17$ST$Str | general | √
9 |  |  |  | GENERAL TRIP | SP | B707_64R_2PROT$PTRC1$ST$Tr | general | √ | √
10 |  |  |  | DEVICE HEALTHY | SP | B707_64R_2PROT$LPHD1$ST$PhyHealth:0 | stVal:1 | √
11 |  |  |  | GOOSE RECEIPT FAIL/TROUBLE | SP | B707_64R_2CTRL$GGIO1$ST$SPCSO7:0 | stVal | √ | √
12 |  |  |  | NGR THERMAL OVERLOAD TRIP | SP | B707_64R_2PROT$PTTR1$ST$OP | stVal | √ | √
13 |  |  |  | TIME SYNCHRONISATION ERROR | SP | B707_64R_2EXT$pdGGIO2$ST$SPCSO4:0 | stVal | √ | √
14 |  |  |  | SETTINGS CHANGED |  |  |  | √
15 |  |  |  | RELAY IN TEST MODE |  |  |  | √
Note: 1. Additional signal for CB Trouble, etc as per scheme & As per standard DR signal requirement the input not considered in HMI signal list 2. 5 Nos of GGIO signal need to be configured as SPARE till the SCADA Database 3. The Logical Device LD is for reference only and vendors may use the same as per their own stndardized way, however the logical nodes used are to be used only as specified. 4. If the logical nodes have been made more specific under the same logical node class by adding prefixes, same can be used as per the application. For example, PDIFF has been specified for all types of differential functions, but if some vendor, under the same logical node class, made the function more specific by adding prefix HZD1PDIFF for 1 phase High Impedance Differential function & T3WPDIFF for 3 winding Low Impedance differential protection, same may be used.

## 7UT_87R1
400kV LINE REACTOR-(7UT)
Sr. No. | Voltage Level | Feeder Name | Source |  | NOTE: THESE SIGNAL STANDARDIZATION IS SCHEME BASED
|  |  |  | SIGNAL DESCRIPTION | INFORMATION TYPE | Telegram Address | POSITION | Events | Alarms
BINARY INPUT (Single Point)
1 | 400kV | 400kV LINE REACTOR | 7UT | PRV-1 TRIP B-PH(NO) | SP |  | stVal | √ | √
2 |  |  |  | PRV-1 TRIP R-PH(NO) | SP |  | stVal | √ | √
3 |  |  |  | PRV-1 TRIP Y-PH(NO) | SP |  | stVal | √ | √
4 |  |  |  | PRV-1 TRIP B-PH(NC) | SP |  | stVal | √ | √
5 |  |  |  | PRV-1 TRIP R-PH(NC) | SP |  | stVal | √ | √
6 |  |  |  | PRV-1 TRIP Y-PH(NC) | SP |  | stVal | √ | √
7 |  |  |  | PRV-2 TRIP B-PH(NO) | SP |  | stVal | √ | √
8 |  |  |  | PRV-2 TRIP R-PH(NO) | SP |  | stVal | √ | √
9 |  |  |  | PRV-2 TRIP Y-PH(NO) | SP |  | stVal | √ | √
10 |  |  |  | PRV-2 TRIP B-PH(NC) | SP |  | stVal | √ | √
11 |  |  |  | PRV-2 TRIP R-PH(NC) | SP |  | stVal | √ | √
12 |  |  |  | PRV-2 TRIP Y-PH(NC) | SP |  | stVal | √ | √
13 |  |  |  | PRV-1 TRIP B-PH | SP |  | stVal | √ | √
14 |  |  |  | PRV-1 TRIP R-PH | SP |  | stVal | √ | √
15 |  |  |  | PRV-1 TRIP Y-PH | SP |  | stVal | √ | √
16 |  |  |  | PRV-2 TRIP B-PH | SP |  | stVal | √ | √
17 |  |  |  | PRV-2 TRIP R-PH | SP |  | stVal | √ | √
18 |  |  |  | PRV-2 TRIP Y-PH | SP |  | stVal | √ | √
19 |  |  |  | WTI TRIP R-PH | SP |  | stVal | √ | √
20 |  |  |  | DIFFERENTIAL TRIP R-PH | SP | B707_87R_1EXT$pdGGIO89$ST$SPCSO40:0 | stVal | √ | √
21 |  |  |  | DIFFERENTIAL TRIP Y-PH | SP | B707_87R_1EXT$pdGGIO89$ST$SPCSO41:0 | stVal | √ | √
22 |  |  |  | DIFFERENTIAL TRIP B-PH | SP | B707_87R_1EXT$pdGGIO89$ST$SPCSO42:0 | stVal | √ | √
23 |  |  |  | DIFFERENTIAL STAGE 1 OPERATED | SP | B707_87R_1PROT$PDIF1$ST$Op | general | √ | √
24 |  |  |  | DIFFERENTIAL STAGE 1 PICKUP | SP | B707_87R_1PROT$PDIF1$ST$Str | general | √
25 |  |  |  | DIFFERENTIAL STAGE 2 OPERATED | SP | B707_87R_1PROT$PDIF2$ST$Op | general | √ | √
26 |  |  |  | DIFFERENTIAL STAGE 2 PICKUP | SP | B707_87R_1PROT$PDIF2$ST$Str | general | √
27 |  |  |  | GENERAL TRIP | SP | B707_87R_1PROT$PTRC1$ST$Tr | general | √ | √
28 |  |  |  | DEVICE HEALTHY | SP | B707_87R_1PROT$LPHD1$ST$PhyHealth:0 | stVal:1 | √
29 |  |  |  | GOOSE RECEIPT FAIL/TROUBLE | SP | B707_87R_1CTRL$GGIO1$ST$SPCSO5:0 | stVal | √ | √
30 |  |  |  | TIME SYNCHRONISATION ERROR | SP | B707_87R_1EXT$pdGGIO2$ST$SPCSO4:0 | stVal | √ | √
31 |  |  |  | SETTINGS CHANGED |  |  |  | √
32 |  |  |  | RELAY IN TEST MODE |  |  |  | √
Note: 1. Additional signal for CB Trouble, etc as per scheme & As per standard DR signal requirement the input not considered in HMI signal list 2. 5 Nos of GGIO signal need to be configured as SPARE till the SCADA Database 3. The Logical Device LD is for reference only and vendors may use the same as per their own stndardized way, however the logical nodes used are to be used only as specified. 4. If the logical nodes have been made more specific under the same logical node class by adding prefixes, same can be used as per the application. For example, PDIFF has been specified for all types of differential functions, but if some vendor, under the same logical node class, made the function more specific by adding prefix HZD1PDIFF for 1 phase High Impedance Differential function & T3WPDIFF for 3 winding Low Impedance differential protection, same may be used.