## LEGEND
SIEMENS SCADA GENERAL SIGNAL LIST FOR VARIOUS PROTECTION & CONTROL SIGNALS - REV03 (INDEX)
Sheet Ref. | IED MODEL | IED SYMBOLIC NAME(TYPICAL) | APPLICATION | IED NAME IN SCD | Additional Remarks
1 | 6MD66 | BCU | TIE BCU | STNM4XXTBCU | BCU is for each bay so 4XX refers to Bay
4 | 7VK61 | 7VK_50ZT | TIE STAND ALONE LBB RELAY | STNM4XXTBFR | Bay No. 4XX will be always the main bay number for the ICT feeder
NOTE 1: The characters "STNM" stand for Substation Name with maximum 4 characters, this code will be given by POWERGRID for each project.
NOTE 2: The characters "4XX" stand for Bay name, example if the bay no 401 then same has to be implemented like STNM401BCU

## BCU
400kV TIE
Sr. No. | Voltage Level | Feeder Name |  | INFORMATION TYPE | Telegram Address | POSITION | Event | Alarm
BINARY INPUT (Double Point)
1 | 400kV | 400kV TIE | CB R-PH POSITION | DP | B702_BCUCBB$XCBR1$ST$Pos:2 | stVal | √
2 |  |  | CB Y-PH POSITION | DP | B702_BCUCBR$XCBR1$ST$Pos:2 | stVal | √
3 |  |  | CB B-PH POSITION | DP | B702_BCUCBY$XCBR1$ST$Pos:2 | stVal | √
4 |  |  | CB POSITION | DP | B702_BCUCB$CSWI1$ST$Pos:2 | stVal | √
5 |  |  | 89AE POSITION | DP | B702_BCU89AE$CSWI3$ST$Pos:2 | stVal | √
6 |  |  | 89BE POSITION | DP | B702_BCU89BE$CSWI5$ST$Pos:2 | stVal | √
7 |  |  | 89A POSITION | DP | B702_BCU89A$CSWI2$ST$Pos:2 | stVal | √
8 |  |  | 89B POSITION | DP | B702_BCU89B$CSWI4$ST$Pos:2 | stVal | √
9
10 |  |  | BINARY INPUT (Single Point)
11
12 |  |  | AUX POWER FAIL | SP | B702_BCUApplication$LPHD0$ST$AuxPwrFail | stVal | √ | √
13 |  |  | TIME SYNCHRONISATION ERROR | SP | B702_BCUApplication$LMTS0$ST$TmSynErr | stVal | √ | √
14 |  |  | BCU MODE | SP | B702_BCUApplication$LLN0$ST$LocKey | stVal | √
15 |  |  | CT SF6 GAS PRESSURE REFILL LOW ALARM | SP | B702_BCUApplication$USER1$ST$SPS | stVal | √ | √
16 |  |  | CT SF6 GAS PRESSURE LOCKOUT | SP | B702_BCUApplication$USER1$ST$SPS1 | stVal | √ | √
17 |  |  | CB DC SUPPLY-1/2 FAIL | SP | B702_BCUApplication$USER3$ST$SPS1 | stVal | √ | √
18 |  |  | CB SPRING NOT CHARGED B-PH | SP | B702_BCUApplication$USER3$ST$SPS4 | stVal | √
19 |  |  | CB SPRING NOT CHARGED R-PH | SP | B702_BCUApplication$USER3$ST$SPS2 | stVal | √
20 |  |  | CB SPRING NOT CHARGED Y-PH | SP | B702_BCUApplication$USER3$ST$SPS3 | stVal | √
21 |  |  | CB SF6 GAS PRESSURE LOCKOUT | SP | B702_BCUApplication$USER3$ST$SPS | stVal | √ | √
22 |  |  | MAIN DC-1 SUPPLY Fail | SP | B702_BCUApplication$USER3$ST$SPS5 | stVal | √ | √
23 |  |  | 89A POLE DESCREPENCY | SP | B702_BCUApplication$USER4$ST$SPS | stVal | √ | √
24 |  |  | 89B POLE DESCREPENCY | SP | B702_BCUApplication$USER4$ST$SPS1 | stVal | √ | √
25 |  |  | 86A TRIP RELAY SUPERVISION | SP | B702_BCUApplication$USER5$ST$SPS2 | stVal | √ | √
26 |  |  | 86A TRIP RELAY OPERATED | SP | B702_BCUApplication$USER5$ST$SPS1 | stVal | √ | √
27 |  |  | 86B TRIP RELAY SUPERVISION | SP | B702_BCUApplication$USER5$ST$SPS5 | stVal | √ | √
28 |  |  | 86B TRIP RELAY OPERATED | SP | B702_BCUApplication$USER5$ST$SPS4 | stVal | √ | √
29 |  |  | CB TC-1 R-PHASE FAULTY
30 |  |  | CB TC-1 Y-PHASE FAULTY
31 |  |  | CB TC-1 B-PHASE FAULTY
32 |  |  | CB TC-2 R-PHASE FAULTY
33 |  |  | CB TC-2 Y-PHASE FAULTY | SP | B702_BCUApplication$USER5$ST$SPS | stVal | √ | √
34 |  |  | CB TC-2 B-PHASE FAULTY | SP | B702_BCUApplication$USER5$ST$SPS3 | stVal | √ | √
35 |  |  | KIOSK AC 1_2 Power Fail | SP | B702_BCUApplication$USER6$ST$SPS7 | stVal | √ | √
36 |  |  | KIOSK AC 1_2 ON STATUS | SP | B702_BCUApplication$USER6$ST$SPS6 | stVal | √
37 |  |  | DC SOURCE-2 FAIL | SP | B702_BCUApplication$USER6$ST$SPS2 | stVal | √ | √
38 |  |  | KIOSK HEAT DETECTED | SP | B702_BCUApplication$USER6$ST$SPS5 | stVal | √ | √
39 |  |  | KIOSK SMOKE DETECTED | SP | B702_BCUApplication$USER6$ST$SPS4 | stVal | √ | √
40 |  |  | EMERGENCY/MANUAL CB TRIP | SP | B702_BCUApplication$USER6$ST$SPS | stVal | √ | √
41 |  |  | PSD DEVICE HEALTHY | SP | B702_BCUApplication$USER6$ST$SPS8 | stVal | √
42 |  |  | PSD DEVICE IN SERVICE | SP | B702_BCUApplication$USER6$ST$SPS9 | stVal | √
43 |  |  | PSD SENSSOR ERROR/CB VOLTAGE ERROR
44 |  |  | PSD BYPASS
45 |  |  | PSD SYNCH OPERATION FAIL/DEFECTIVE SYNC DATA ALARM | SP | B702_BCUApplication$USER6$ST$SPS10 | stVal | √ | √
46 |  |  | SYNC OPERATION FAIL | SP | B702_BCUApplication$USER6$ST$SPS11 | stVal | √ | √
47 |  |  | TIE LBB RELAY UNHEALTHY | SP | B702_BCUApplication$USER6$ST$SPS1 | stVal | √ | √
48 |  |  | TIE LBB OPTD
49 |  |  | CB POLE DESCREPENCY | SP | B702_BCUApplication$USER2$ST$SPS1 | stVal | √ | √
50 |  |  | CB SF6 GAS PRESSURE REFILL LOW ALARM | SP | B702_BCUApplication$USER2$ST$SPS | stVal | √ | √
51 |  |  | BUS-1 VT SELECTED | SP | B702_BCUApplication$USER7$ST$SPS | stVal | √
52 |  |  | BUS-2 VT SELECTED | SP | B702_BCUApplication$USER7$ST$SPS1 | stVal | √
53 |  |  | ICT LV VT SELECTED | SP | B702_BCUApplication$USER7$ST$SPS2 | stVal | √
54 |  |  | CB READY | SP | B702_BCUCB$XCBR1$ST$Rdy | stVal | √
55 |  |  | EMERGENCY/MANUAL CB TRIP | SP | B702_BCUCB$GAPC2$ST$Detected | stVal | √ | √
56 |  |  | CB MANUAL CLOSE
57 |  |  | CB CONTROL NO SYNC | SP | B702_BCUCB$CSWI1$ST$Pos | noSync | √
58 |  |  | CB CLOSE INTERLOCK | SP | B702_BCUCB$CILO1$ST$EnaCls | stVal | √
59 |  |  | 89AE OPEN INTERLOCK | SP | B702_BCU89AE$CILO3$ST$EnaOpn | stVal | √
60 |  |  | 89BE OPEN INTERLOCK | SP | B702_BCU89BE$CILO5$ST$EnaOpn | stVal | √
61 |  |  | 89A OPEN INTERLOCK | SP | B702_BCU89A$CILO2$ST$EnaOpn | stVal | √
62 |  |  | 89B OPEN INTERLOCK | SP | B702_BCU89B$CILO4$ST$EnaOpn | stVal | √
63 |  |  | DEVICE HEALTHY | SP | B702_BCUApplication$LPHD0$ST$PhyHealth:0 | stVal:1 | √ | √
64 |  |  | GOOSE RECEIPT FAIL/TROUBLE | SP | B702_BCUApplication$USER7$ST$SPS3 | stVal | √ | √
65 |  |  | A/R BLOCK
66 |  |  | A/R FUNCTION OFF
67 |  |  | A/R FUNCTION ON
68 |  |  | A/R READY
69 |  |  | A/R UNSUCCESSFUL
70 |  |  | A/R START
71 |  |  | A/R SUCCESSFUL
72 |  |  | RECLAIM IN PROGRESS
73 |  |  | MAIN A/R LOCKOUT
74 |  |  | TIE A/R LOCKOUT
75 |  |  | Tie CB A/R PRIORITY CLOSE
76 |  |  | MAIN/TIE BCU HEALTHY
77 |  |  | AR SINGLE PHASE TRIP PERMITTED
78 |  |  | CB NOT READY
79 |  |  | A/R CLOSE COMMAND INDICATION
80 |  |  | A/R IN PROGRESS
81 |  |  | RELAY IN TEST MODE
82 |  |  | SETTINGS CHANGED
83 |  |  | CB MANUAL TRIP
84 |  |  | CB MANUAL CLOSE
85 |  |  | BUSBAR OPERATED
86 |  |  | BCU IN LOCAL/REMOTE
87 |  |  | MEASUREMENT
88
89 |  |  | POWER FACTOR | ME_FL | B702_BCUVI3p1_OperationalValues$PPRE_MMXU1$MX$TotPF:1 | mag$f
90 |  |  | FREQUENCY | ME_FL | B702_BCUVI3p1_OperationalValues$PPRE_MMXU1$MX$Hz:1 | mag$f
91 | 400kV | 400kV TIE | ACTIVE POWER | ME_FL | B702_BCUVI3p1_OperationalValues$PPRE_MMXU1$MX$TotW:1 | mag$f
92 |  |  | REACTIVE POWER | ME_FL | B702_BCUVI3p1_OperationalValues$PPRE_MMXU1$MX$TotVAr:1 | mag$f
93 |  |  | APPARENT POWER | ME_FL | B702_BCUVI3p1_OperationalValues$PPRE_MMXU1$MX$TotVA:1 | mag$f
94 |  |  | I-R -PH CURRENT | ME_FL | B702_BCUVI3p1_OperationalValues$RPRE_MMXU1$MX$A:1 | phsA$cVal$mag$f
95 |  |  | I-Y -PH CURRENT | ME_FL | B702_BCUVI3p1_OperationalValues$RPRE_MMXU1$MX$A:1 | phsB$cVal$mag$f
96 |  |  | I-B -PH CURRENT | ME_FL | B702_BCUVI3p1_OperationalValues$RPRE_MMXU1$MX$A:1 | phsC$cVal$mag$f
97 |  |  | R-Y VOLTAGE | ME_FL | B702_BCUVI3p1_OperationalValues$RPRE_MMXU1$MX$PPV:1 | phsAB$cVal$mag$f
98 |  |  | Y-B VOLTAGE | ME_FL | B702_BCUVI3p1_OperationalValues$RPRE_MMXU1$MX$PPV:1 | phsBC$cVal$mag$f
99 |  |  | B-R VOLYAGE | ME_FL | B702_BCUVI3p1_OperationalValues$RPRE_MMXU1$MX$PPV:1 | phsCA$cVal$mag$f
100 |  |  | KIOSK TEMPERATURE | ME_FL
101 |  |  | CB-B-PH COUNTER | ME_I | B702_BCUCBB$XCBR1$ST$OpCnt | stVal
102 |  |  | CB-R-PH COUNTER | ME_I | B702_BCUCBR$XCBR1$ST$OpCnt | stVal
103 |  |  | CB-Y-PH COUNTER | ME_I | B702_BCUCBY$XCBR1$ST$OpCnt | stVal
104
105 |  |  | COMMANDS
106
107 |  |  | 89B CONTROL | DC | B702_BCU89B$CSWI4$CO$Pos:8 | Oper$ctlVal | √
108 |  |  | 89A CONTROL | DC | B702_BCU89A$CSWI2$CO$Pos:8 | Oper$ctlVal | √
109 |  |  | 89BE CONTROL | DC | B702_BCU89BE$CSWI5$CO$Pos:8 | Oper$ctlVal | √
110 |  |  | 89AE CONTROL | DC | B702_BCU89AE$CSWI3$CO$Pos:8 | Oper$ctlVal | √
111 |  |  | CB CONTROL | DC | B702_BCUCB$CSWI1$CO$Pos:8 | Oper$ctlVal | √
112 |  |  | 89B CONTROL NO LOCK | SC | B702_BCU89B$CSWI4$CO$Pos | Oper$noLock | √
113 |  |  | 89A CONTROL NO LOCK | SC | B702_BCU89A$CSWI2$CO$Pos | Oper$noLock | √
114 |  |  | 89BE CONTROL NO LOCK | SC | B702_BCU89BE$CSWI5$CO$Pos | Oper$noLock | √
115 |  |  | 89AE CONTROL NO LOCK | SC | B702_BCU89AE$CSWI3$CO$Pos | Oper$noLock | √
116 |  |  | CB CONTROL NO SYNC | SC | B702_BCUCB$CSWI1$CO$Pos | Oper$noSync | √
117 |  |  | CB CONTROL NO LOCK | SC | B702_BCUCB$CSWI1$CO$Pos | Oper$noLock | √
118 |  |  | 86B TRIP RELAY RESET COMMAND | SC | B702_BCUApplication$USER2$CO$SPC1:8 | Oper$ctlVal | √
119 |  |  | 86A TRIP RELAY RESET COMMAND | SC | B702_BCUApplication$USER2$CO$SPC:8 | Oper$ctlVal | √
120 |  |  | BAY BLOCK | SC
121 |  |  | TELECONTROL BLOCK | SC
122 |  |  | GOOSE RECEIPT FAIL/TROUBLE | SP | B702_BCUApplication$LLN0$ST$SPS | stVal | √ | √
123 |  |  | A/R ON CONTROL | SC | B706_BCUApplication$USER8$CO$SPC:8 | Oper$ctlVal | √
124 |  |  | A/R OFF CONTROL | SC | B706_BCUApplication$USER8$CO$SPC1:8 | Oper$ctlVal | √
125 |  |  | A/R BLOCK | SP | B706_BCUCB1_79AutoReclosing$GEN_RREC1$ST$BlkFct | stVal | √
126 |  |  | A/R FUNCTION OFF | SP | B706_BCUCB1_79AutoReclosing$GEN_RREC1$ST$Off | stVal | √
127 |  |  | A/R FUNCTION ON | SP | B706_BCUCB1_79AutoReclosing$GEN_RREC1$ST$On | stVal | √
128 |  |  | CB READY FOR A/R | SP | B706_BCUCB1_79AutoReclosing$GEN_RREC1$ST$AutoRecSt:0 | stVal:1 | √
129 |  |  | A/R UNSUCCESSFUL | SP | B706_BCUCB1_79AutoReclosing$GEN_RREC1$ST$AutoRecSt:0 | stVal:10 | √ | √
130 |  |  | A/R SUCCESSFUL | SP | B706_BCUCB1_79AutoReclosing$GEN_RREC1$ST$Successful | stVal | √
131 |  |  | CB NOT READY | SP | B706_BCUCB1_79AutoReclosing$GEN_RREC1$ST$CBnotRdy | stVal | √
132 |  |  | A/R CLOSE COMMAND INDICATION | SP | B706_BCUCB1_79AutoReclosing$GEN_RREC1$ST$OpCls | general | √
133 |  |  | TIE A/R START |  |  |  | √
134 |  |  | A/R IN PROGRESS | SP | B706_BCUCB1_79AutoReclosing$GEN_RREC1$ST$RecInit | stVal | √
135 |  |  | SETTINGS CHANGED
136 |  |  | RELAY IN TEST MODE
Note: 1. Additional signal for CB Trouble, etc as per scheme & As per standard DR signal requirement the input not considered in HMI signal list 2. 5 Nos of GGIO signal need to be configured as SPARE till the SCADA Database 3. The Logical Device LD is for reference only and vendors may use the same as per their own stndardized way, however the logical nodes used are to be used only as specified. 4. If the logical nodes have been made more specific under the same logical node class by adding prefixes, same can be used as per the application. For example, PDIFF has been specified for all types of differential functions, but if some vendor, under the same logical node class, made the function more specific by adding prefix HZD1PDIFF for 1 phase High Impedance Differential function & T3WPDIFF for 3 winding Low Impedance differential protection, same may be used.

## 7VK_50ZT
400kV TIE
Sr. No. | Voltage Level | Feeder Name
|  |  | SIGNAL DESCRIPTION | INFORMATION TYPE | Telegram Address | POSITION | Event | Alarm
BINARY INPUT (Single Point)
1 | 400kV | 400kV TIE | BREAKER FAILURE RPH- RETRIP | SP | B702_50ZTPROT$RBRF1$ST$OpIn | phsC | √ | √
2 |  |  | BREAKER FAILURE YPH- RETRIP | SP | B702_50ZTPROT$RBRF1$ST$OpIn | phsB | √ | √
3 |  |  | BREAKER FAILURE BPH- RETRIP | SP | B702_50ZTPROT$RBRF1$ST$OpIn | phsA | √ | √
4 |  |  | BREAKER FAILURE BACKTRIP | SP | B702_50ZTPROT$RBRF1$ST$OpIn | general | √ | √
5 |  |  | BREAKER FAILURE TRIP EXTERNAL | SP | B702_50ZTPROT$RBRF1$ST$OpEx | general | √ | √
6 |  |  | GENERAL TRIP | SP | B702_50ZTPROT$PTRC1$ST$Tr | general | √ | √
7 |  |  | BREAKER FAILURE INITIATION 3-PH | SP | B702_50ZTPROT$RBRF1$ST$Str | general | √ | √
8 |  |  | TIE CB FAIL | SP | B702_50ZTCTRL$GGIO1$ST$SPCSO2:0 | stVal | √ | √
9 |  |  | TIE BCU UNHEALTHY | SP | B702_50ZTCTRL$GGIO1$ST$SPCSO1:0 | stVal | √ | √
10 |  |  | DEVICE HEALTHY | SP | B702_50ZTPROT$LPHD1$ST$PhyHealth:0 | stVal:1 | √
11 |  |  | LBB EXTERNAL INITIATION 3-PH | SP | B702_50ZTEXT$pdGGIO23$ST$SPCSO7:0 | stVal | √ | √
12 |  |  | TIME SYNCHRONISATION ERROR | SP | B702_50ZTEXT$pdGGIO2$ST$SPCSO4:0 | stVal | √ | √
13 |  |  | LBB EXTERNAL INITIATION R-PH | SP | B702_50ZTEXT$pdGGIO23$ST$SPCSO27:0 | stVal | √ | √
14 |  |  | LBB EXTERNAL INITIATION Y-PH | SP | B702_50ZTEXT$pdGGIO23$ST$SPCSO28:0 | stVal | √ | √
15 |  |  | LBB EXTERNAL INITIATION B-PH | SP | B702_50ZTEXT$pdGGIO23$ST$SPCSO29:0 | stVal | √ | √
16 |  |  | POLE DISCREPANCY PICKUP | SP | B702_50ZTEXT$pdGGIO24$ST$SPCSO24:0 | stVal | √
17 |  |  | POLE DISCREPANCY TRIP | SP | B702_50ZTEXT$pdGGIO24$ST$SPCSO28:0 | stVal | √ | √
18 |  |  | LBB ACTIVE | SP | B702_50ZTEXT$pdGGIO23$ST$SPCSO45:0 | stVal | √
19 |  |  | DC-1 Fail
20 |  |  | GOOSE RECEIPT FAIL/TROUBLE | SP | B702_50ZTCTRL$GGIO1$ST$SPCSO3:0 | stVal | √ | √
21 |  |  | SETTINGS CHANGED
22 |  |  | RELAY IN TEST MODE
Note: 1. Additional signal for CB Trouble, etc as per scheme & As per standard DR signal requirement the input not considered in HMI signal list 2. 5 Nos of GGIO signal need to be configured as SPARE till the SCADA Database 3. The Logical Device LD is for reference only and vendors may use the same as per their own stndardized way, however the logical nodes used are to be used only as specified. 4. If the logical nodes have been made more specific under the same logical node class by adding prefixes, same can be used as per the application. For example, PDIFF has been specified for all types of differential functions, but if some vendor, under the same logical node class, made the function more specific by adding prefix HZD1PDIFF for 1 phase High Impedance Differential function & T3WPDIFF for 3 winding Low Impedance differential protection, same may be used.