| Sl. No. | Clause No. | Provision as per the bidding document | Bidder’s Queries | POWERGRID Reply |
| --- | --- | --- | --- | --- |
| Volume-I: Conditions of Contract |  |  |  |  |
| 1 | ITB cl. No. 11.3, BDS, Section-III | # Bidders are not required to quote the Local Transportation, In-transit insurance, loading and unloading charges (hereinafter referred to as F&I charges) in their bid. Prices regarding F&I charges shall be finalized with the Contractor based on actual destination decided by Employer prior to scheduled dispatch of the equipment in the following manner: After decision in respect of Destination has been taken by Employer, Contractor shall be asked to submit F&I charges for the finalized destination along with documentary evidence towards justification of prices such as copy of Rate Contract entered into by Contractor, Quotation etc. This activity shall be started preferably five months prior to the scheduled dispatch of the Equipment. | As site is not known to us at bidding stage, we are considering all 17 reactors are required for one site. If there are multiple site, PGCIL to provide additional charges for site ETC activities. | Since this package is meant for Bulk Procurement, the delivery sites for the reactors can be more than one location. No additional charges shall be considered separately. |
| 2 | ITB cl. No. 24.1 (c), , BDS, Section-III | The Time for Completion for delivery of 17 nos. Shunt Reactors – Engineering: 0-8 months Dispatch: 16-18 months Rcpt at site:17-19 months Erection & Ready for Commissioning:18-21 months (1st-5th) 5 units by 21 months Engineering: 0-10 months Dispatch: 19-21 months Rcpt at site:20-22 months Erection & Ready for Commissioning:21-24 months (6th-11th) 6 units by 24 months Engineering: 0-11 months Dispatch: 22-24 months Rcpt at site:23-25 months | As per your delivery schedule time provided for erection & readiness for commissioning of one no. single phase, 765 kV shunt reactor is one month. Based on our experience in previous orders one month for complete ETC of SR is not sufficient. Hence we request you to provide additional 2 - 3 months for ETC after receipt of SR at site | Completion schedule of the units shall as per provisions of bid documents. |
| 3 |  | The Time for Completion shall be as under: Duration in months from the effective date of Contract Unit-1 to Unit-5 : 21 Months Unit-6 to Unit-11 : 24 Months Unit-12 to Unit-17 : 27 Month | We request to please help with modifying the timelines as below considering the current Market Situation & availabilities : Duration in months from the effective date of Contract : Unit-1 to Unit-5 : 24 Months Unit-6 to Unit-11 : 27 Months Unit-12 to Unit-17 : 30 Months |  |
| Volume-II: Technical Specifications |  |  |  |  |
| 4 | Cl. No 1.3 of Technical Specification, 765kV Shunt Reactor, C/ENGG/MODEL-SPEC/765kV SR Rev. 08 | Any material and equipment not specifically stated in this specification but which are necessary for satisfactory operation of the equipment shall be deemed to be included unless specifically excluded and shall be supplied without any extra cost. | Our offer shall be with fittings & accessories as per technical specification, which is suitable for satisfactory operation of reactor. Any additional material and equipment if required shall be provided with cost implication. Any civil work related to foundation etc are not in bidder scope. | Bidder shall quote meeting the requirement of bidding documents |
| 5 | Cl. No 3.2 of Technical Specification, 765kV Shunt Reactor , C/ENGG/MODEL-SPEC/765kV SR Rev. 08 | The contractor shall carry out the route survey along with the transporter and finalise the detail methodology for transportation of reactor and based on route survey; any modification/ extension/ improvement to existing road, bridges, culverts etc. if required, shall be in the scope of the contractor. | Details of route survey i.e. transport weight / dimension limitations are not available. Hence, transport details shall be as per our previous supplies (80 MVAr) to PGCIL. Any modification or strengthing work ( substation main gate, approach road, shifting of pole etc.) required for smooth and safe shipment of the reactor upto foundation from main gate shall be in PGCIL scop | Bidder shall quote meeting the requirement of bidding documents |
| 6 | Cl. No 3.5 of Technical Specification, 765kV Shunt Reactor , C/ENGG/MODEL-SPEC/765kV SR Rev. 08 | The Contractor shall despatch the Reactor filled with dry air at positive pressure. The necessary arrangement shall be ensured by the contractor to take care of pressure drop of dry air during transit and storage till completion of oil filling during erection. A dry air pressure testing valve with necessary pressure gauge and adaptor valve shall be provided. The dry air cylinder(s) provided to maintain positive pressure can be taken back by the contractor after oil filling. | Reactor can be stored with dry air filled condition upto 6 months after dispatch from factory. For longer storage, reactor need filled with oil as per OEM manual. | Bidder shall quote meeting the requirement of bidding documents |
| 7 | Cl. No 7.1.2 of Technical Specification, 765kV Shunt Reactor , C/ENGG/MODEL-SPEC/765kV SR Rev. 08 | The requirement of post weld heat treatment of tank/stress relieving shall be based on recommendation of IS 10801. | IS 10801 is applicable to pressurize piping and pressure vessel. As inside pressure of reactor tank is approx. 1 kg/cm2 and hence not come to Pressure vessel category. Hence, Not applicable | Bidder shall quote meeting the requirement of bidding documents |
| 8 | Cl. No 7.1.6 of Technical Specification, 765kV Shunt Reactor , C/ENGG/MODEL-SPEC/765kV SR Rev. 08 | The base of each tank shall be so designed that it shall be possible to move the complete transformer unit by skidding in any direction without damage when using plates or rails and the base plate shall have following minimum thickness. Length of Tank (m); Minimum plate thickness (mm). Flat Base. Ovr 2.5m but less than 5m; 20. Over5m but less than 7.5m; 26. Exceed 7.5m; 32. | MS Plate IS 2062:2011 refer IS 1730:1989 for dimension of steel plate. 26mm thk Plate is not in IS standard, alternate solution is 25mm thk plate. Hence requesting for length of tank over 5m but less than 7.5m plate thickness shall be 25 mm thk. Kindly accept. | Bidder shall quote meeting the requirement of bidding documents |
| 9 | Cl. No 7.1.8 of Technical Specification, 765kV Shunt Reactor , C/ENGG/MODEL-SPEC/765kV SR Rev. 08 | Tank, tank cover and associated structure should be adequately designed to withstand, without damage or permanent deflection / deformation, the forces arising out of normal oil pressure, test pressures, vacuum, seismic conditions and short circuit forces specified. | There is contradiction in the requirement. We understand the permanent deflection will be acceptable up to the values specified in clause no. 17 (ii) of DOC. No.: POWERGRID/STD/TEST PROCEDURE/TR-RT/REV02. Page No. 52 of 69. Kindly confirm. | Bidder shall quote meeting the requirement of bidding documents |
| 10 | Cl. No. 7.2.7 & 14.7.1.7 of Technical Specification,SECTION- 765 KV SHUNT REACTOR, C/ENGG/MODEL-SPEC/765kV SR Rev. 8 | Clause No.7.2.7: The Reactor shall be provided with a 150 mm nominal diameter butterfly valve and bolted blanking plate, gasket and shall be fitted at the highest point of the Reactor for maintaining vacuum in the tank. Clause No.14.7.1.7: Valve for vacuum application on Tank : Type Gate | Since there is contradictory requirement in the specification in two different clauses. Our preference is 100 mm Gate valve. Customer acceptance required. | Gate type valve shall be provided for vaccum application. Bidder shall quote meeting the requirement of bidding documents |
| 11 | Cl. No. 7.4 of Technical Specification,SECTION- 765 KV SHUNT REACTOR, C/ENGG/MODEL-SPEC/765kV SR Rev. 8 | 7.4 Foundation, Roller Assembly & Anti Earthquake Clamping Device The Reactor shall be placed directly on concrete plinth foundation. To facilitate the movement of reactor to its foundation over rail track, bi-directional flanged rollers shall be provided. It shall be suitable for fixing to the under carriage of Reactor. The rail track gauge shall be 1676 mm. Two rails shall be provided as per the drawing mentioned at Annexure-C. | Rails shall not be in bidder scope. Also, drawing referred in Annexure C is not available with the given specification Rev08. Kindly provide the drawing | Bidder shall quote meeting the requirement of bidding documents |
| 12 | Cl. No. 7.8, 7.9, 7.10 & 22.1 (i) of Technical Specification,SECTION- 765 KV SHUNT REACTOR, C/ENGG/MODEL-SPEC/765kV SR Rev. 8 | 7.8 Pressure Relief Device suitable canopy shall be provided to prevent ingress of rain water. 7.9 Sudden Pressure Relay suitable canopy shall be provided to prevent ingress of rain water. 7.10 Buchholz Relay suitable canopy shall be provided to prevent ingress of rain water. 22.1 (i) Magnetic oil level gauge | Canopy shall be provided as per bidder standard practice. If any specify requirement, kindly share the drawing of canopy to consider in our scope of supply | Bidder shall quote meeting the requirement of bidding documents |
| 13 | Cl. No. 7.19.14 of Technical Specification,SECTION- 765 KV SHUNT REACTOR, C/ENGG/MODEL-SPEC/765kV SR Rev. 8 | Winding paper moisture shall be less than 0.5% | Noted, However testing shall be done with Karl fischer method. Kindly confirm. | Bidder shall quote meeting the requirement of bidding documents |
| 14 | Cl. No. 14.1 of Technical Specification,SECTION- 765 KV SHUNT REACTOR, C/ENGG/MODEL-SPEC/765kV SR Rev. 8 | All valves upto and including 100 mm shall be of gun metal or of cast steel/cast iron. Larger valves may be of gun metal or may have cast iron bodies with gun metal fittings. They shall be of full way type with internal screw and shall open when turned counter clock wise when facing the hand wheel. | As all Butterfly valve above 100mm are of Cast Iron bodies and brass fittings. For 100mm and 80mm Butterfly valve used at radiator also need to supply as Cast Iron bodies and brass fitting which is superseding the technical specification requirement of Cast Iron valve(i.e cast iron bodies and mild steel fittings). As we are superseding the technical specification requirement. Customer acceptance required. | Bidder shall quote meeting the requirement of bidding documents |
| 15 | Cl. No. 14.6 of Technical Specification,SECTION- 765 KV SHUNT REACTOR, C/ENGG/MODEL-SPEC/765kV SR Rev. 8 | Gland packing/gasket material shall be of “O” ring of nitrile rubber for all the valve‟s flanges. All the flanges shall be machined. | All “O” ring used for Valve mounting flange are as per technical specification and of “NBR” material. Valve Gland Packing is of “PTFE” (Teflon) material suitable to transformer oil and atmospheric air. PTFE required for better Oil sealing purpose compared to NBR as per Approved valve supplier. Customer acceptance required. | Bidder shall quote meeting the requirement of bidding documents |
| 16 | Cl. No. 14.7.2 of Technical Specification,SECTION- 765 KV SHUNT REACTOR, C/ENGG/MODEL-SPEC/765kV SR Rev. 8 | All valves shall be painted with a shade (preferably red or yellow) distinct and different from of main tank surface and as per the painting system and procedure specified. | There is no such painting system and procedure specified in technical specification and in Annexure-E. Painting specification shall be follwed as per PGCIL approved supplier recommendation. Customer acceptance required | Bidder shall quote meeting the requirement of bidding documents |
| 17 | GTR Rev 15, Annexure B | SEISMIC WITHSTAND TEST PROCEDURE | Seismic withstand test is not applicable on offered reactors. Kindly confirm. | Seismic withstand test is not applicable on offered reactors. However Reactors shall be designed for Seismic Level of Zone-V (as per IS 1893) |
| 18 | Clause No. 2.2 d, Section Project | One No. CMB shall be supplied for 2 x 1-Ph or 3 x 1-Ph 765KV Class Reactor unit at one location. | Our offer is for 17 Nos. shunt reactors and we are considering only 5 No. CMB against 17 Nos. Shunt reactors. Based on 3 x 1 Phase 765 kV class reactor. | One No. CMB shall be supplied for 2 x 1-Ph or 3 x 1-Ph 765KV Class Reactor unit at one location. LIU & associated Patch cords & One Ethernet switch , as part of each CMB, shall also be provided. Bidder shall quote meeting requirment of of Section Project. |
| 19 | S. No. 1,2, Section Project | 80 MVAR Reactor and Insulating Oil | Request PGCIL to split bushing as separate line item in BPS as bushing deliveries are more critical now-a-days. | Bidder shall quote meeting the requirement of bidding documents |
| 20 | Reactor Technical Specification Rev08, Annexure-L | On-line insulating oil drying system (Cartridge type) | We request to keep the On-line insulating oil drying system (Cartridge type) as a separate line item in the BPS. Currently including it in the main transformer line item creates difficulties while dispatching & invoicing the equipment | Bidder shall quote meeting the requirement of bidding documents |