## Pre-Bid Queries
Clarification No.–I dated 15/06/2023 to Bidding Document for 765kV AIS Extn. Substation Package SS-01 for (i) Construction of 2 nos. of 765kV line bays at Sikar II for Sikar II – Bhadla II 765kV D/c line (ii) Construction of 2 nos. of 765kV line bays at Bhadla II for Sikar II – Bhadla II 765kV D/c line associated with Transmission Scheme for evacuation of power from Solar Energy Zones in Rajasthan (8.1 GW) under Phase II-Part E. Spec. No.: CC/T/W-AIS/DOM/A06/23/02699
Sl.No | Volume / Section | Clause | Bidder's Query | POWERGRID's Reply
1 | Appendix – 2 : PRICE ADJUSTMENT THE PRICES SHALL REMAIN FIRM AND FIXED DURING THE CURRENCY OF THE CONTRACT. | Appendix-2 (Price Adjustment), Section-VI: Sample Forms and Procedures | As the work completion period is 15 Months and the current volatile market .We request you to Kindly make PVC applicable for this bid as per PGCIL standard practise. | The provisions of the Bidding Documents shall remain unchanged.
2 | GCC Clause No. 3.1, Section-IV: General Conditions of Contract | 3. Scope of Facilities 3.1 Unless otherwise expressly limited in the Technical Specifications, the Contractor's obligation shall include the provision of all Plant and Equipment and the performance of all Installation Services required for the design, the manufacture (including procurement, quality assurance, construction, installation, associated civil works, Precommissioning and delivery) of the Plant and Equipment and the installation, completion, commissioning and performance testing of the facilities in accordance with the plans, procedures, specifications, drawings, codes and any other documents as specified in the Technical specifications. Such specifications include, but are not limited to, the provision of supervision and engineering services; the supply of labour, materials, equipment, spare parts (as specified in GCC Sub-Clause 3.3 below) and accessories; Contractor's Equipment; construction utilities and supplies; temporary materials, structures and facilities; transportation (including without limitation, all clearances, handling etc.); storage and training except for those supplies, works and services that will be provided or performed by the Employer, as set forth in Appendix-6 (Scope of Works and Supply by the Employer) to the Contract Agreement. | Please confirm on availability of land by Employer for construction of stores by contractor. | The Contractor has to ensure the suitable arrangements of storage during execution stage and overall responsibility of the same lies with him in line with the provision of the Bidding Documents. Further, for providing land for such construction store, the same can be done in coordination with site during execution stage depending upon the availability of space. However, the Employer has no binding to provide the same.
3 | GCC Clause No. 6.2, Section-IV: General Conditions of Contract | 6. Employer’s Responsibilities ………………………………… ………………………………… 6.2 The Employer shall be responsible for acquiring and providing legal and physical possession of the Site and access thereto, and for providing possession of and access to all other areas reasonably required for the proper execution of the Contract, including all requisite rights of way, as specified in the corresponding Appendix – 6 (Scope of Works and Supply by the Employer) to the Contract Agreement. The Employer shall give full possession of and accord all rights of access thereto on or before the date(s) specified in that Appendix. | Please confirm upon availability of encumbrance free land at the time of award of NOA/LOA. | Please refer provisions of Bidding Documents at clause 6.2 of General Conditions of Contract, Section – IV, Volume-I, which are amply clear.
4 | GCC Clause No. 6.3, Section-IV: General Conditions of Contract | 6. Employer’s Responsibilities ………………………………… ………………………………… 6.3 The Employer shall acquire and pay for all permits, approvals and/or licenses from all local, state or national government authorities or public service undertakings in the country where the Site is located which such authorities or undertakings require the Employer to obtain them in the Employer's name, are necessary for the execution of the Contract (they include those required for the performance by both the Contractor and the Employer of their respective obligations under the Contract), including those specified in Appendix 6 (Scope of Works and Supply by the Employer) to the Contract Agreement. | Please provide clarity on liability of obtaining Environment clearance for the Project. | Please refer provisions of Bidding Documents at clause 6.3 of General Conditions of Contract, Section – IV, Volume-I, which are amply clear.
5 | GCC Clause No. 9.3.3 at Sr. No. 12, Section-V: Special Conditions of Contract | Reduction in the security pro rata to the Contract Price of any part of the Facilities is not admissible. However, if the Defects Liability Period has been extended on any part of the Facilities pursuant to GCC Sub-Clause 22.8 hereof, the Contractor shall issue an additional security in an amount proportionate to the Contract Price of that part. The security shall be returned to the Contractor immediately after its expiration, provided, however, that if the Contractor pursuant to GCC Sub-Clause 22, is liable for an extended warranty obligation, the performance security shall be reduced to Ten Percent (10%) of the value of the component covered by the extended warranty. | Please allow for proportionate reduction of PBG based on completion of facilities. | The provisions of the Bidding Documents shall remain unchanged.
6 | GCC Clause No. 34.1, Section-IV: General Conditions of Contract | The Time(s) for Completion specified in the SCC shall be extended if the Contractor is delayed or impeded in the performance of any of its obligations under the Contract by reason of any of the following: (a) any Change in the Facilities as provided in GCC Clause 33 (b) any occurrence of Force Majeure as provided in GCC Clause 32 (c) any suspension order given by the Employer under GCC Clause 35 hereof or reduction in the rate of progress pursuant to GCC Sub-Clause 35.2 or (d) any changes in laws and regulations as provided in GCC Clause 31 or (e) any other matter specifically mentioned in the Contract by such period as shall be fair and reasonable in all the circumstances and as shall fairly reflect the delay or impediment sustained by the Contractor. | Please include the below mentioned provision in stated clause: (f) Any delay caused due to delay/failure in fulfilment of Employer's obligations . The contractor is entitled for extension of time along with reimbursement of additional cost incurred. | The provisions of the Bidding Documents shall remain unchanged.
7 | Appendix-1 (Terms and Procedures of Payment), Section-VI: Sample Forms and Procedures | ……………….. C Final Payment ……………………………………. However, in case of delay in testing and commissioning & issuance of taking over certificate by Employer beyond six (6) months from the date of receipt of equipment at site, the last 10% of Ex-Works price of respective equipment shall be paid after issuance of a certificate by Employer’s representative that the equipment have been received in good condition and on submission of a bank guarantee of equivalent amount, which shall be kept valid initially for a period of twelve (12) months or until three (3) months after the expected date of commissioning (in case it is possible to anticipate the same), whichever is earlier, provided all other conditions as per above are complied with by the Contractor. If the commissioning does not take place within the validity period of BG, the validity of BG shall be extended from time to time. The bank guarantee shall, however, be released within one month of successful commissioning of the respective equipment by the Employer. | Please rephrase this clause as under: In case of delay in testing and commissioning & issuance of taking over certificate by Employer beyond One (1) month from the date of receipt of equipment at site, the last 10% of Ex-Works price of respective equipment shall be paid after issuance of a certificate by Employer’s representative that the equipment have been received in good condition and on submission of a bank guarantee of equivalent amount, which shall be kept valid initially for a period of twelve (12) months or until three (3) months after the expected date of commissioning (in case it is possible to anticipate the same), whichever is earlier, provided all other conditions as per above are complied with by the Contractor. If the commissioning does not take place within the validity period of BG, the validity of BG shall be extended from time to time. The bank guarantee shall, however, be released within one month of successful commissioning of the respective equipment by the Employer." | The provisions of the Bidding Documents shall remain unchanged.
8 | Appendix-1 (Terms and Procedures of Payment), Section-VI: Sample Forms and Procedures | Interest rate applicable on advance payment to the Contractor shall be at the rate equal to one year MCLR rate [One Year Tenor rate p.a.] published by State Bank of India prevailing as on the date of drawal of advance. The said interest rate shall remain fixed and shall be applicable till the advance amount is fully repaid. ………………………………………………… ………………………………………………… | Please include provision of interest on delayed payments by Employer @ SBI PLR for the prevailing year. | The provisions of Terms and Procedures of Payment referred to in Appendix-1 to Contract Agreement in Section-VI - Sample forms and Procedures in Volume-I of the Bidding Documents shall prevail.
9 | GCC Clause No. 32.1, Section-IV: General Conditions of Contract | 32. Force Majeure 32.1 “Force Majeure” shall mean any event beyond the reasonable control of the Employer or of the Contractor, as the case may be, and which is unavoidable notwithstanding the reasonable care of the party affected, and shall include, without limitation, the following (a) war, hostilities or warlike operations (whether war be declared or not), invasion, act of foreign enemy and civil war, (b) rebellion, revolution, insurrection, mutiny, usurpation of government, conspiracy, riot and civil commotion, (c) earthquake, landslide, volcanic activity, flood or cyclone, or other inclement weather condition, nuclear and pressure waves or other natural or physical disaster, | We understand that Epidemics/Pandemic such as Novel Coronavirus ( e.g. COVID 19) etc., Terrorism, Bandhs, Infrastructure failures and Shortage of certain components required for the performance of the scope of work are covered under force majeure. Please Confirm. | The provisions of Bidding Documents are amply clear and same shall prevail.
10 | GCC Clause No. 31.1, Section-IV: General Conditions of Contract | 31. Change in Laws and Regulations 31.1 If, after the date seven (07) days prior to the date of Bid Opening, any law, regulation, ordinance, order or by-law having the force of law is enacted, promulgated, abrogated or changed in India (which shall be deemed to include any change in interpretation or application by the competent authorities) that subsequently affects the costs and expenses of the Contractor and/or the Time for Completion, the Contract Price shall be correspondingly increased or decreased, and/or the Time for Completion shall be reasonably adjusted to the extent that the Contractor has thereby been affected in the performance of any of its obligations under the Contract. These adjustments shall be applicable for all transactions between the Employer and the Contractor for supply of goods and services under the Contract but shall not be applicable on procurement of raw materials, intermediary components etc. by the Contractor for which the Employer shall be the sole judge. Notwithstanding the foregoing, such additional or reduced costs shall not be separately paid or credited if the same has already been accounted for in the price adjustment provisions where applicable, in accordance with the Appendix-2 to the Contract Agreement. | We understand that, If any new law or regulation imposed social responsibility on Contractor which hamper the progress of work with financial burden out of Contract, the same shall be borne by Employer. Please Confirm. | The Provisions of Bidding Documents are amply clear and same shall prevail.
11 | General | Site Storage Facility | We presume that space shall be provided at site for storage & site office construction at free of cost. Please confirm. | The provisions of the Bidding Documents are amply clear.
12 | General | TCS | W.e.f. 01/10/2020, TCS is implemented . The seller is required to collect the TCS from buyer TCS @ .1% of sales consideration on sale of goods when Seller receives amount Rs 50 lakh from any single buyer in current financial year. In current tender, bidder will have to collect TCS on sale of goods @ 0.1% on value of goods excluding GST. Bidder will issue certificate to client and the same will be subject to credit to client However on service invoice no TCS will be applicable. Please confirm our understanding. | Bidder have to comply with all the statutory requirements.
13 | GCC Clause No. 39, Section-IV: General Conditions of Contract | 39. Arbitration 39.1 All disputes or differences in respect of which the decision, if any, of the Project Manager and/or the Head of the Implementing Authority has not become final or binding as aforesaid shall be settled by arbitration in the manner provided herein below: 39.2 The arbitration shall be conducted by a sole arbitrator in case the amount of claim is less than Rs. 25 Crore and by three member arbitral tribunal in case the amount of claim is greater than Rs. 25 Crore. Sole Arbitration ………………………………………… | We request for settlement of disputes arising out of contract or in connection with the contract , to be settled with panel of three arbitrators, one from each party and a presiding arbitrator. Also the claim about shall not be the basis of deciding the number of arbitrators. Please confirm. | The Provisions of Bidding Documents shall prevail.
14 | Appendix-2 (Price Adjustment), Section-VI: Sample Forms and Procedures | Appendix – 2 : PRICE ADJUSTMENT THE PRICES SHALL REMAIN FIRM AND FIXED DURING THE CURRENCY OF THE CONTRACT. | In view of high price fluctuation in the present market for raw material, we request you to please consider the price variation for raw material based items like Conductor, IPS tube, Erection Hardwares, Clamps & Connectors, Bus Post Insulators, etc Please confirm. | The provisions of the Bidding Documents shall remain unchanged.
15 | Appendix-2 (Price Adjustment), Section-VI: Sample Forms and Procedures | Appendix – 2 : PRICE ADJUSTMENT THE PRICES SHALL REMAIN FIRM AND FIXED DURING THE CURRENCY OF THE CONTRACT. | We request you to kindly incorporate the Price Adjustment for Circuit Breaker, CVT, Power & Control Cables, Earthing Materials, IPS Tube, Conductor, Hardware, Clamps & Connectors. Please confirm. | The provisions of the Bidding Documents shall remain unchanged.
16 | GCC Clause No. 33.2.3 at Sr. No. 42, Section-V: Special Conditions of Contract | Supplementing Clause GCC 33.2.3 Percentage for the Change Proposal under this Clause shall be limited to Fifteen (15) percent. | As per referred clause " Percentage for the Change Proposal under this Clause shall be limited to Fifteen (15) percent". Hope the current change proposal is limited to the project duration. Kindly confirm our understanding. | The provisions of the Bidding Documents are amply clear.
17 | In Annexure-A Section Project 2.2.1 Extension of 765kV Sikar-II S/s: E. Complete Relay & Protection System as per Section-‘Control and Relay Panels’ for 765kV bays under present scope. Make of existing bus bar protection system shall be provided during detailed engineering. F. Sikar-II S/s is being equipped with substation automation system based on IEC-61850 (make of existing SAS system shall be provided during detailed engineering). | Vol-II Part 01 of 08 | E : Please provide us the Make of existing bus bar protection system as it is to be integrated with CRP to be supplied under present scope. In current monopolistic situation for CRP vendors it is very challenging to estimate the price of CRP equipments and its integration without taking consent of exisitng make vendors. Further there is no price variation on CRP, makes the situation worst. F: Please provide us the Make of existing SAS as it is to be integrated with SAS to be supplied under present scope. In current monopolistic situation for SAS vendors it is very challenging to estimate the price of SAS equipments and its integration without taking consent of exisitng make vendors. Further there is no price variation as well, makes the situation worst. | E: Pleae refer clause no. 2.2.1.1.E for detail scope. Only Augmentation of existing Busbar protection scheme including modifications of scheme to be done by the contractor. make & Model of Bus bar protection shall be shared during detail engineering. F: SAS for 765kV Sikar-II s/s: Only Augmentation of existing SAS including modifications of scheme to be done by the contractor, details for Augmentation shall be shared during detailed engineering. Bidders to quote accordingly.
18 | For the Site Visit related: |  | Please Share the contact details of the concern site person for coordinationg for site visit | Northern Region-1, RHQ Faridabd
19 | Mandatory Spares List for Equipments | Attachment Missing | Attachment Break-up is missing.Kindly provide the details | Please refer Amendment No I
20 | Creepage |  | We understand that 25mm/kV Creepage is required. Kindly confirm. | Minimum specific creepage distance for insulator string/ longrod insulators/ outdoor bushings shall be 31 mm/kV. However, minimum specific creepage distance of other outdoor equipment shall be 25mm/kV in line with requirement of Technical Specification.
21 | X/R ratio of the system |  | Kindly provide the X/R ratio of the system for both substation. | It shall be provided during detailed Engineering
22 | SLD & LAYOUT |  | Please share existing SLD & LAYOUT of sikar substation for necessary reference. | Refer Cl. No. 6.2 of section project- ...the drawings shall be provided during detailed engineering"
23 | Mandatory Spare |  | Please share the list of Mandatory Spare. | Please refer Amendment No I
24 | Existing system |  | No work / no modification / no strengthening work envisaged at existing system under present scope of bidder. Please confirm. | Bidders to quote inline with requirement of Bidding documents.
25 | Existing system |  | Please share existing trench/road layout, existing DSLP layout, existing illumination layout , existing VMS layout for better tender quantity estimation. | Please refer clause no. 2.4 of Section-Project for site visit.
26 | Existing earthmat spacing. |  | Please share the existing system earth grid spacing. | For estimation purpose, please refer clause no. M.3 of Specific Requirement, Rev-7. Bidders to quote accordingly.
27 | Existing 765kV bus bar protection scheme |  | For existing 765kV bus bar protection scheme, as per Section project clause Peripheral Bay Units for present scope are considered in separate package and shall be made available during detail engineering. Pls share existing bus bar prot. make at sikar SS. Please confirm. | Refer reply to simmilar query above.
28 | Insulators |  | Disc Insulator/Composite Long rod: Please confirm disc or long rod insulator both can be considered. | Scope /Requirement is ample clear in Bidding documents.Bidder to quote accordingly.
29 | Insulators |  | Please confirm polymer/ porcelain long rod insulator both can be considered. | Scope /Requirement is ample clear in Bidding documents.Bidder to quote accordingly.
30 | Control & Power Cable |  | Control & Power Cabling: Kindly Confirm the below Points: i) Isolator, CT & CVT cabling will be provided in PVC pipe. No provision of RCC trench is envisaged. PVC pipes will be connected to nearest cable trench. ii) We are not considering any cable tray for indoor / outdoor cable laying. iii) Power & Control cables in switchyard shall be laid on cable support angles. | Scope /Requirement is ample clear in Bidding documents.Bidder to quote accordingly.
31 | Relay test kit |  | We understand No numerical relay test kit is envisaged under present scope of bidder. Please confirm. | Confirmed.
32 | Substation automation system |  | Please confirm router/firewall/modem/gateways are not envisaged under present scope as the present scope bays shall be integrated with existing substation automation system of the local substation. | Scope /Requirement is ample clear in Bidding documents.Bidder to quote accordingly.
33 | Integration/interface-Other end/Remote end |  | We understand, any interface or integration work at local substation in third party equipments is excluded from bidder's scope. All interface/integration support is required at present scope supplied equipment end only. Please confirm. | Scope /Requirement is ample clear in Bidding documents.Bidder to quote accordingly.
34 | Integration/interface-Dispatch centers |  | We understand, configuration/database modification works at RLDC (RSCC) /NLDC/National Transmission Asset Management Centre (NTAMC)/RTAMC is excluded from bidder scope. Please confirm. | Scope /Requirement is ample clear in Bidding documents.Bidder to quote accordingly.
35 | Existing VMS System |  | Please specify make for exiting VMS system, to accommodate the necessary VMS integration. | Existing make of VMS for Bhadla-II is M/s Delcom make . For Sikar-II VMS system, details shall be shared during detailed engineering.
36 | Existing VMS System |  | Please confirm existing system having license for present scope cameras. | Scope /Requirement is ample clear in Bidding documents.Bidder to quote accordingly.
37 | Existing VMS System |  | As tender documents doesn’t calls for outdoor camera range criteria. So we understand camera range (100 meter or 200 meter etc.) restriction is not applicable. Bidder to meet annexure S9 VMS requirement. Please confirm. | Bidders to quote inline with requirement of Bidding documents.
38 | Existing Fire Fighting System |  | Please furnish existing fire fighting piping layout and confirm the tapping point required for present scope i.e. line reactors. Please also confirm the existing system head is suitable for present scope HVW/hydrant system considering pressure. | Bidder is advised to visit the site as per clause no. 2.4 of Section-Project.
39 | Existing Fire Fighting System |  | Please confirm necessary I/O's availability in Fire annunciation panel for accommodating fire zones for present scope of work. | Bidder is advised to visit the site as per clause no. 2.4 of Section-Project.
40 | Existing Fire Fighting System |  | Any Shifting of existing fire-fighting piping in existing switchyard area are not under present scope, please confirm. | Scope /Requirement is ample clear in Bidding documents.Bidder to quote accordingly.
41 | PMU & associated Equipments |  | Please confirm the make of existing PMU system. | The PMU scope for the subject package does not need the details of existing PMU system. PMU supplied under subject package has to comply standard IEEE protocol as specified in technical specification.
42 | PMU & associated Equipments |  | We understand, integration of PMU with Phasor data Concentrator (PDC) at RLDC/SLDC is excluded from bidder's scope. Please confirm. | Confimed. However, all the configuration work of PMU at substation end required for integration with PDC at RLDC/SLDC end shall be in the scope of Bidder.
43 | Existing LT switchgear |  | Please confirm availability & adequate capacity of the required AC/DC feeders and switchgear required for present scope. Please share the LT SLD for available feeder rating details . | Extension of LT switchgear is not envisaged under present scope. LT SLD shall be shared during detailed engineering. However, bidder is advised to visit site as per clause no. 2.4 of Section-project.
44 | LT switchgear, battery & charger |  | No such LT switchgear is envisaged under present scope of bidder, Please confirm. | Confirmed.
45 | Oil filtration unit & its power supply |  | 250Amps oil filtration unit power receptacle shall be provided under present scope . Power cable for the same shall be brought out from existing switchgear feeder. | Confirmed
46 | Distance |  | Please confirm all LT switchgear are located in existing control room building. Please confirm the distance is not more then 200 meter in between present scope reactor units and existing control room building. | Bidder is advised to visit the site as per clause no. 2.4 of Section-project.
47 | Earth mat layout |  | We understand that , Main earth mat for the New Line bay extn. Shall be extended as per the existing system. Earthing Calculation is not applicable for the same. However existing Earthmat drawing of substation required. Please confirm and provide the same for LOT item estimation. | Please refer clarification Sl.No.11
48 | Relay Settings calculation |  | Relay Setting calculation Shall be provided by PGCIL, Please Confirm. | Scope /Requirement is ample clear in Bidding documents.Bidder to quote accordingly.
49 | Scope/BPS |  | We understand that in case of any discrepancy between tender provided drawings / specifications/ section project and price schedule, the price schedule shall govern. Please confirm. | in case of any discrepancy between tender provided drawings / specifications/ section project and price schedule, the price schedule shall govern. If suffcient detail is not there, Technical specification has to be referred to.
50 | Pipes for FO cables |  | Please confirm bidder may choose type of pipe for FO cable laying. | The fibre optic cables shall be run in G. I. conduit pipes. Please refer clause no. 2.2 of Section-SAS, Rev-04
51 | Annexure-S1 |  | The Inter-pole cables between Circuit Breaker, Isolator and associated Marshalling box shall be deemed to be included in price of Equipment. and same shall not included in BPS.Please confirm | Confirmed. Refer Annexure S1 of Specific requirement, Rev-07
52 | Annexure-S1 |  | Cables from ACPs to fixtures shall be deemed to be included in price of luminaires and same shall not included in BPS.Please confirm | Confirmed. Refer Annexure S1 of Specific requirement, Rev-07
53 | General |  | The installation of 1.1kV grade power and control cables (including inter-pole cable of Equipment & illumination cables) shall be quoted in “LOT” basis. Please confirm | Confirmed. Refer Annexure S1 of Specific requirement, Rev-07
54 | Section Project |  | As per section project revision number 00, we understand 765kV reactors(at each site 6 numbers single phase reactors) are not in scope of supply including all accessories and associated systems. We understand no spare reactor is in present scope of supply or any connection is envisaged for spare reactor as the same shall come in future . Also pls confirm 1.1kV control power cables/FO cable/LIU/Ethernet or any items required from reactors to common MB are part of separate package and is excluded from bidder's scope of present package. | Scope /Requirement is ample clear in Bidding documents. Please refer clause no. 3,9.5, 9.6 of Section-project.
55 | Terminal & clamp connector Mandatory spare |  | We understand circuit breaker and isolator terminal connectors only required as mandatory spares , Kindly confirm. LA, CVT , CT and BPI terminal connectors are not required as mandatory spares. | Please refer Amendment No I
56 | Switchyard Work |  | Switchyard system is four tower arrangement. For line reactor jack bus is envisaged under present scope whereas no jack bus or main bus is envisaged under present scope of bidder which must be existing. Kindly confirm our understanding. | For Bhadla, the switchyard scheme is four gantry structure and however for Sikar switchyard scheme detail shall be provided during detail engineering, bidder to quote as per provision of the bidding documents.
57 | PLCC |  | Please confirm PLCC envisaged under present scope is analog PLCC. No items for digital PLCC required except mentioned in PGCIL BOQ/BPS. No license for digital PLCC is envisaged under present scope of bidder. | Scope /Requirement is ample clear in Bidding documents.Bidder to quote accordingly.
58 | Line side string hardware & insulators |  | We understand as per BPS "765kV tension string suitable for Hexa conductor" is line side tension string which shall be suitable for line side conductor . Please confirm hex conductor is zebra for clarity. | Bidders to quote inline with requirement of Bidding documents.
59 | Panel placement |  | We understand PLCC and CRP panels shall be placed in present scope one number SPR. Present scope SPR shall be suitable for present scope line with switchable line reactor bays CRP, PLCC only. Please share the location where present scope FOTE panel shall be placed. Please confirm the distance from present bays to existing bus bar protection panels . | Bidders to quote inline with requirement of Bidding documents.
60 | Galvanizing thickness for steel structures |  | We understand that Galvanizing shall be 610gm/Sq Mtr for present scope substation. Please confirm | Confirmed.
61 | RTV Coating requirement |  | We have not envisaged any kind of RTV coating. Please confirm | Confirmed.
62 | Fire fighting pump house location |  | We understand that location of fire fighting pump house to be located near to control room building to limit power cable from MSB to FFPH motor feeder within 100 mtr. | Bidders to quote inline with requirement of Bidding documents.
63 | Please provide SLD & GA of Sikar-II substation |  |  | Refer Cl. No. 6.2 of section project- "Sikar II PS, is under parallel development and the drawings shall be provided during detailed engineering"
64 | Fire Fighting System |  | Kindly provide existing firefighting layout of both s/s and water tapping point distance for hydrant & HVWS system of Reactor under present scope for both S/s. | For Bhadla-II substation, please visit site as per clause no. 2.4 of Section-Project. SLD & GA of Sikar-II substation, the drawings shall be provided during detailed engineering"
65 | Sikar - II PS - location of spare reactor | TS, cl.no. 2.1 , scope, page 3/ 28 | As per specificaiton clause, it is mentioned as "Spare unit of 765kV, 1x110 MVAR Reactor, to be provided under separate package(s) shall be utilized as common spare for 6x110 MVAR Switchable Line Reactors to be utilized at Sikar-II PS". We assume that the existing spare reactor is on the same side of line with reactors bays and is beside the present scope of line with reactor bays, accordingly all interconnection materials are considered for spare reactor connection. Please confirm. If not then please convey the location of spare reactor. | Bidders to quote inline with requirement of Bidding documents.
66 | Bhadla-II - Erection hardware | SLD & BPS item 31, 33 | As per SLD Line bay, Reactor bay, Tie bay & spare bay connection to Bus -1 are shown in red color as present scope. However as per the BPS item nos 31, 33 only refers to Line bay & Line reactor bay erection hardware materials. Hence we consider the scope of erection hardware for Line bay & Line reactor bay only. Please confirm. | The erection hardware of Tie bay is part of Line bay. Please refer Typical module drawing enclosed as Tender drawing. Bidders to quote accordingly.
67 | Bhadla-II - Bus Isolators | SLD & BPS item 21, 22, 23 | As per the SLD the connection of Tie bay to Bus-I needs 1 number 3ph Isolator with ES , however the same is not included in BPS. Please check and confirm the connection arrangement. | For tie bays please refer BPS item no.27, where Isolator with two earth switch are envisaged. Further, the connection of Tie-Bay with Bus-I shall connected directly without any additional Isolator in future bay.
68 | Bhadla-II - Erection hardware for Misc. works | TS, cl.no. 9.6 , scope, page 18/ 28 | The said clause of TS refers to " For Bhadla-II : “ERECTION H/W FOR MISCELLANEOUS WORK AS PER TECHNICAL SPECIFICATION “. However there is no such item in BPS. We assume that the above item is not applicable for the present scope of work. Please confirm. | Bidders are to quote in line with BPS.
69 | Bhadla-II & Sikar-II - Mandatory spares | BPS item 87 to 97 | As per the BPS items Bhadla -II & Sikar - II , the list of Mandatory spares for respective equipment are not available in TS. Please provide the list of mandatory spares to consider. | Please refer Amendment No I
70 | Sikar - II PS - Drawings SLD , GA | SLD , GA | Please provide SLD & layout drawings of existing station. | Refer Cl. No. 6.2 of section project- "Sikar II PS, is under parallel development and the drawings shall be provided during detailed engineering"
71 | 765kV & 145kV BPI for Reactor Auxiliary bus formation | BPS item no. 25 , 29 (Bhadla - II) & item no. 10, 5 (Sikar-II) | We understood that the BPIs required for auxiliary bus formation of Reactors both HV (765kV) & Neutral bus (145kV) for connection of spare reactor are payable under respective equipment BPS item nos. Please confirm. | BPI's for both HV (765kV) & Neutral bus (145kV) for connection of spare reactor are part of respective Erection Hardware items . Pleae refer refer clause M.7 of specific requirement Rev. 07 and BPS for clarity. Bidders to quote accordingly.
72 | Plot level | - | We presume that the plot is of one level without any level difference. Please confirm. | Refer Cl. No. 6.2 of section project- "Sikar II PS, is under parallel development and the drawings shall be provided during detailed engineering". Bidders to quote as per BPS.
73 | Lighting cables | BPS item "power & control cables" | In absence of the layout & location of LT switchgear, we could not be able to estimate the cables pertaining to outdoor Lighting (MLDB to ACP to Lighting JB). And so we presume that the cables required for lighting purpose (MLDB to ACP to Lighting JB) shall be payable under BPS item "Power & control cables". Please confirm. | Please refer Annexsure-S1, methodology for supply, installation & sizing of cables in Section: Specific requirement, Rev 07. Further, the cables between MLDB to ACP shall be payble under BPS item :Power & Control Cable". Bidders to quote accordingly.
74 | HVW system | BPS - 1.1kV Power & control cables | In absence of the layout & location of Pump house builidng/ control room building, the cables (power & control) required for HVW fire fighting system (Between HVW equipment to Pumphouse / CRB) shall be considered part of BPS item "Power & Control cables , item no. 40 to 53". Please confirm. | Confirmed.
75 | CRP - Busbar protection augmentation | Section - project | We preume that where ever the busbar augmentation is to be considered for the present scope of work and to integrate with the existing system, in such cases the offered relays /BCUs for the present scope shall be suitable with respect to the existing Relays/ BCUs interms of version/edition/hardware requirements. If any contradiction between the individual section (CRP-SAS) specificaiton and the existing system of relays then we follow the existing system of relays for augmentation / integration. Please confirm. | Please refer Amendment No I
76 | Missing Mandatory Spares List | - |  | Please refer Amendment No I
77 | Contour map | - | Please provide the contour data of proposed substation extension to evaluate the tender quantities. | Sikar-II: Site leveling in under contractor's scope. Bhadla-II: Site is levelled. FGL data shall be shared during detailed engineering. Bidder to qoute as per BPS. | Sikar-II: Site leveling in under contractor's scope. Bhadla-II: Site is levelled. FGL data shall be shared during detailed engineering. Bidder to qoute as per BPS. | Sikar-II: Site leveling in under contractor's scope. Bhadla-II: Site is levelled. FGL data shall be shared during detailed engineering. Bidder to qoute as per BPS. | Sikar-II: Site leveling in under contractor's scope. Bhadla-II: Site is levelled. FGL data shall be shared during detailed engineering. Bidder to qoute as per BPS.
78 | Soil Investigation Report | - | Kindly request you to provide soil investigation reports for proposed extension for tender working. | Soil Investigation Report will be made available during detailed engineering. Bidder to qoute as per BPS. | Soil Investigation Report will be made available during detailed engineering. Bidder to qoute as per BPS. | Soil Investigation Report will be made available during detailed engineering. Bidder to qoute as per BPS. | Soil Investigation Report will be made available during detailed engineering. Bidder to qoute as per BPS.
79 | Excavation - Soil Strata | Price Schedule Bhadla Si.No -81 & Sikar Si.No-90 Excavation | Since the excvation in all types of soils are paid under single line item as per referred clause, here by we request to provide the soil strata up to 3m depth of proposed substations. | Soil Investigation Report will be made available during detailed engineering. Bidder to qoute as per BPS. | Soil Investigation Report will be made available during detailed engineering. Bidder to qoute as per BPS. | Soil Investigation Report will be made available during detailed engineering. Bidder to qoute as per BPS. | Soil Investigation Report will be made available during detailed engineering. Bidder to qoute as per BPS.
80 | Excavation -Different types of soil | Price Schedule Bhadla Si.No -81 & Sikar Si.No-90 Excavation | In absence of soil strata, we kindly request to split the excvation in to different line items such as Excvation in normal soil, Excvation in soft rock etc. | Bidder to qoute as per BPS. | Bidder to qoute as per BPS. | Bidder to qoute as per BPS. | Bidder to qoute as per BPS.
81 | Excavtion/cutting in hard rock | Price Schedule Bhadla Si.No -81 & Sikar Si.No-90 Excavation | We understand from the referred clauses that during land development if we met any hard rock excavation, it will be paid seperately to the contracor as per mutually agreed rates, please confirm. | Excavation in hard rock (requried blasting) is not envisaged. If during site execution, hard rock (requried blasting) is encountered, the same shall be paid separately. Refer cl 20.1 (b) of Technical Specification: Section: Civil Works, Rev 11A. Bidder to qoute as per BPS. | Excavation in hard rock (requried blasting) is not envisaged. If during site execution, hard rock (requried blasting) is encountered, the same shall be paid separately. Refer cl 20.1 (b) of Technical Specification: Section: Civil Works, Rev 11A. Bidder to qoute as per BPS. | Excavation in hard rock (requried blasting) is not envisaged. If during site execution, hard rock (requried blasting) is encountered, the same shall be paid separately. Refer cl 20.1 (b) of Technical Specification: Section: Civil Works, Rev 11A. Bidder to qoute as per BPS. | Excavation in hard rock (requried blasting) is not envisaged. If during site execution, hard rock (requried blasting) is encountered, the same shall be paid separately. Refer cl 20.1 (b) of Technical Specification: Section: Civil Works, Rev 11A. Bidder to qoute as per BPS.
82 | Drawings |  | The switchyard GA Drawing is avilable only for Bhadla SS. Please provide Sikar SS GA drawing. | Refer Cl. No. 6.2 of section project- "Sikar II PS, is under parallel development and the drawings shall be provided during detailed engineering"
83 | Approach road to proposed site |  | 1). We presume that the construction of approach road leading to allotted site is excluded from bidders scope. Please confirm. 2). Any strengthening / modification required in the existing culverts, road, bridges etc. for transportation of material / Items / equipment up to proposed site shall be carried out by the PGCIL. Please confirm. | 1) Please refer clause no. Specific exclusions of Section Project. 2) Please refer to the Clause 11.1 of GTR. Bidders to quote as per provision of the bidding documents.
84 | Construction Power & Water |  | Kindly confirm availability of the sources for 415V constructional power and water near the proposed site. | Please refer to the Clause 14.3.1 & 14.3.2 of GTR. Bidders to quote as per provision of the bidding documents.
85 | Order of Precedence |  | Please describe the order of precedence of price schedule (BPS), section project and technical specification. | Please refer to Clause 7 of Section-Project. In case of any discrepancy between BPS and other sections, BPS shall prevail over the other sections of the technical specifications. However, for rating of the BPS items, associated technical specification shall be referred to.