Appendix-8-Rev-01

GUARANTEES, LIQUIDATED DAMAGES FOR NON – PERFORMANCE

1.0	The equipment offered shall meet the rating and performance requirement indicated in Data requirement.

2.0	The ratings and performance figures of the below mentioned equipment are guaranteed by you.

| Sl. No. | Description | Guaranteed Loss (kW) | Rate of Liquidated Damages in Indian Rupees per kW of differential loss (applicable fo each item/unit of the facilities) |
| --- | --- | --- | --- |
| A | 25MVAR, 220kV, 3-Phase Reactor |  |  |
|  | Differential loss (KW) |  | INR 369,960/- (Indian Rupees Three Hundred Sixty Nine Thousand Nine Hundred Sixty only)only) per kW. |

3.0	If the aforementioned guarantees are not established at factory tests, then the Employer at his discretion may reject or accept the equipment after assessing the liquidated damages as follows against the Contract:

- Measured losses exceeding Guaranteed value by 0 to +5%: rates of LD mentioned above

- Measured losses exceeding guaranteed value by > +5% to +10%: Twice the rates of LD mentioned above.

- Measured losses exceeding Guaranteed value by > +10% to +15%: Four times the  rates of LD mentioned above

3.1   Such Liquidated damages shall be deducted from the Contract Price or otherwise recovered from the Contractor. However, the equipment under no circumstances shall be accepted if the measured losses are more than +15 percent of the guaranteed losses at rated voltage indicated by you in your Bid.