| S N | Clause Reference | Text as per TS/BDS | Bidder's Queries | POWERGRID Reply |
| --- | --- | --- | --- | --- |
| 1 | ITB 24.1(b) of Bid Data Sheet | The maximum losses permissible for 25 MVAR, 220 kV, 3- phase Reactor offered by the bidder is stipulated in the Technical Specifications, Volume-II of the Bidding Document. Any bid with deviations to the above shall be considered non-responsive. | Please furnish the maximum loss or any Capitalization rate for the 25MVAr shunt reactor to prepare the offer, which is not mentioned anywhere in the tender documents. | Please refer S.N.- 10 of Amendment-01 |
| 2 | Clause No 11.2 Page 19 of 80 Spec SR-R10 TS of RTV Coating_Ammend-1 | "Bushing for voltage of 52 kV and above shall be RIP bushing with composite insulator. 36 kV bushing shall be solid porcelain or oil communicating type" "Technical Specification for RTV Silicone high voltage insulation coating (HVIC)" | It may kindly be noted that as per Clause No 11.2 of Spec SR-R10 it is mentioned that Bushing for voltage of 52 kV and above shall be RIP bushing with composite insulator. 36 kV bushing shall be solid porcelain or oil communicating type. However, in this project Technical Specification for RTV Silicone high voltage insulation coating (HVIC) is attached also. But in section project there is no mention of RTV coating. Therefore, we understand that RTV Coating is not required. And if it is required then kindly specify on which bushing it is to be applied. | Bidders understanding is correct. RTV coating is not required |