Contents

1.0	GENERAL	2

2.0 	SCOPE OF WORK	3

3.0	SPECIFIC EXCLUSIONS:	7

4.0	PHYSICAL AND OTHER PARAMETERS	7

5.0	SCHEDULE OF QUANTITIES	8

6.0	BASIC REFERENCE DRAWINGS	8

7.0	DIFFERENT SECTIONS OF TECHNICAL SPECIFICATION	8

8.0	MANDATORY SPARES	9

9.0	SPECIFIC REQUIREMENT	10

|  | List of Annexures: |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Annexure-I |  | LIST OF DRAWINGS |  |  |  |  |  |  |  |  |
|  | Annexure-II |  | SPECIFIC REQUIREMENTS (Section-Project) - C/ENGG/SPEC/SEC-PROJECT/SPECIFIC REQUIREMENT Rev. No. 10 |  |  |  |  |  |  |  |  |

# GENERAL

  - Preamble:

Power Grid Corporation of India Ltd. (POWERGRID), A Govt. of India Enterprise is responsible for Bulk Power Transmission of electrical energy from various central Govt. Power Projects to various utilities/ beneficiaries and interconnecting regional grids, operating and maintaining the National Electrical Grid of India. It is established with the mission of “We will become a Global Transmission Company with Dominant Leadership in Emerging Power Markets with World Class Capabilities by:

- World Class: Setting superior standards in capital project management and operations for the industry and ourselves.

- Global: Leveraging capabilities to consistently generate maximum value for all stakeholders in India and in emerging and growing economies.

- Inspiring, nurturing and empowering the next generation of professionals.

- Achieving continuous improvements through innovation and state of the art technology.

- Committing to highest standards in health, safety, security and environment.”

  - POWERGRID is implementing the following Transmission Schemes on DCW basis

- Construction of Two Nos 230kV bays for TANTRANSCO at 400kV Pugalur POWERGRID Substation

  - It is the intent of this specification to describe primary features, materials, and design & performance requirements and to establish minimum standards for the work. The specification is not intended to specify the complete details of various practices of manufactures/ bidders, but to specify the requirements with regard to performance, durability and satisfactory operation under the specified site conditions.

  - The work to be done under this specification shall include all labour, plant, equipment, material and performance of all work necessary for the complete installation and commissioning of the switchyard. All apparatus, appliances, material and labour etc. not specifically mentioned or included, but are necessary to complete the entire work or any portion of the work in compliance with the requirements implied in this specification is deemed to be included in the scope of contractor.

  - Before proceeding with the construction work, the Contractor shall fully familiarize himself with the site conditions and General arrangements & scheme etc. Though the Employer shall endeavor to provide the information, it shall not be binding for the Employer to provide the same. The bidders are advised to visit the substation sites and acquaint themselves with the topography and infrastructure. The contractor shall be fully responsible for providing all equipment, materials, system and services specified or otherwise which are required to complete the construction and successful commissioning, operation & maintenance of the substation in all respects. All materials required for the Civil and construction/installation work including cement and steel shall be supplied by the Contractor. Complete design and detailed engineering shall be done by Contractor.

# 2.0 	SCOPE OF WORK

The scope of this specification covers following:

| Sl. No. | Scope of work |
| --- | --- |
| 1 | Construction of Two Nos 230kV bays for TANTRANSCO at 400kV Pugalur POWERGRID Substation. Present scope: - Switching Scheme: Double Main Transfer Scheme for 230kV - Fault Level: 50kA for 1 sec for 230kV - 230kV Line Bay: 2 no. - 230kv Bay-211 & 212 |

The detailed scope of works of the substation package is brought out in subsequent clauses of this section.

  - Construction of Two Nos 230kV bays for TANTRANSCO at 400kV Pugalur POWERGRID Substation:

Design, basic engineering, manufacture, testing at manufacture’s works, Supply including Transportation &   Insurance, unloading, Storage, Erection, Testing and Commissioning at the site (including all necessary deployment of OEM engineers) the following equipment/items, complete in all respects: -

  - 230 kV Circuit Breakers, Isolators, Current Transformers, CVTs, BPIs, Surge Arresters, Bus post Insulators, Wave traps, equipment support structures etc.

  - Complete Relay and Protection system for the 230kV bays under present scope as per Section: Control & relay panels. Existing 230kV Busbar protection scheme is of GE make (central unit-P741 & Peripheral Unit-P743) . Augmentation of Busbar protection scheme including new PU for bays under present scope must be provided. Necessary wiring for connection of bus bar protection for bays under present scope has to be carried out by the contractor. Any other hardware required for augmentation of the bus bar protection (FO cards, DI/DO cards, etc as may be required in central Unit apart from PU to be supplied, etc) is also deemed included in work scope. Necessary extension of station DC supply as per Cl. 2.1 (h) below is also included in work scope.

  - SUBSTATION AUTOMATION SYSTEM:

Substation automation system: 230kV Pugalur substation is equipped with substation automation system of GE make (software used is DS-AGILE) based on IEC 61850 protocols. Bidder shall include BCU required for 230kV bays (Bay as defined in technical specification, Section - Substation Automation) as listed below including all necessary hardware (ethernet switches, LIU's, patch chords. OFC etc) and software to integrate IEDs offered under present scope with the existing Substation Automation System as indicated above.

- 230kV bay – 02 Nos.

Existing network architecture of 400kV Pugalur substation is attached with the BID documents. It shall be the responsibility of the contractor to successfully integrate the BCUs and protection IEDs with existing substation automation system (which is based on IEC 61850) including updating of system database, displays, and development of additional displays and reports as per requirement for the bays covered under present scope. Data points to be integrated, as per standard NTAMC and RLDC list for the new bays shall be provided during detailed engineering.

Necessary interface equipment and integration work at existing substation for transferring data to NTAMC, Backup NTAMC, RTAMC for Remote operation and to RLDC (RSCC) /NLDC (for supervision) through optical fibre based SDH communication link is also under present scope. However, no work is envisaged at remote end (RLDC/NLDC/NTAMC/RTAMC etc) under the present scope. Network architecture of the station is attached with the BID documents.

  - CABLES:

1.1kV grade Power & Control cables along with complete accessories: 1.1kV grade Power & Control cables (and special cables, if any) along with complete accessories. Methodology for supply, installation & sizing of 1.1kV Power & Control cables shall be as per Specific Requirement attached.

  - ERECTION HARDWARE:

Hardware, conductor, Al tube, bus-bar materials, cable trays, Bay MB, clamps, spacers, connectors including equipment connectors, Junction box, earthwire, earthing material risers, auxiliary earthmat (excluding main earth mat) buried cable trenches/pipe equipment & lighting, all accessories etc. Insulator strings and associated hardware fittings, Erection hardware such as conductor(s), cable supporting angles/channels, insulating mats, cable sealing arrangement all accessories etc. as required (both bus side as well as line side for both the bays). New BMK for 220kV bays shall be provided under present scope. Necessary modification in ACDB/DCDB as per Cl. 2.1(h) below is also included in work scope. Insulator string along with hardware for line gantry shall be as per BPS line item.

  - MAIN EARTHMAT:

The Main Earthmat in the present scope switchyard area is already existing and existing outdoor Earthmat Layout of substation is enclosed along with tender drawings. However, all the equipment’s, structures, cable trenches, etc. are to be earthed by risers connecting them to the existing Main Earthmat and the same shall be deemed to be included in respective BPS items of Erection Hardware. However, extension of main earthmat, if required during execution, is included in scope of work.

  - ILLUMINATION SYSTEM:

LED based lighting and illumination system for Extension portion of 220kV Switchyard area under present scope shall be provided by the contractor. Illumination system shall be provided using the fixture types as specified in Technical Specification Section-Lighting System. Further, contractor shall submit lighting design calculation for finalizing the number of fixtures, in line with (Specific Requirements).

  - EXTENSION OF ACDB, DCDB and MLDB

MCBs, Connectors, Cables etc to be provided for extension of Supply from ACDB, DCDB and ELDB as part of the present scope of works. Any cutting out, MCB installation, looping of supply to installed MCB’s, minor modification/fabrication work required in the DBs for extension of supply to the new bays are also included in the present scope.

  - Augmentation of existing Visual Monitoring System (VMS) for area under present scope as per BPS. Make and Model of Existing VMS shall be shared to successful bidder during detailed engineering. The bidder shall provide sufficient nos. IP camera with PAN, Tilt & Zoom facility suitably located in Outdoor switchyard in the present scope area, so that entire bay area equipment’s are covered in the VMS system. The scope of bidder shall include providing all Items, Accessories, Line Interface units, Fiber patch cords, Power supply units, Junction Boxes, Cables, Fiber Optic Cables, Hardware and Software, etc. as applicable to the product design, to meet functional requirements & compatibility with existing VMS system. The cameras are to be integrated to the existing VMS system. Capability enhancement is not envisaged under the present scope. Specifications of VMS system are available in Specific Requirements- Annexure 10 attached with the BID documents.

  - Any other equipment/material required to complete the specified scope.

  - Mandatory Spares:

Manufacture, testing and supply including transportation & insurance, storage of mandatory spares at site as per BPS.

  - The PLCC, DTPC & Telecom related items / quantities envisaged for other end (TANTRANSCO end) are tentative only, and their actual requirement/execution (if required) is to be decided during detailed engineering as per direction of Engineer in charge. Installation of the above devices and commissioning is included in the work scope.

    - LATTICE AND PIPE STRUCTURES (GALVANIZED):

- All required galvanized Lattice Equipment support structures SLD/ Fabrication (except support structures for Circuit Breaker) shall be provided as per Employer during detailed engineering.

- The support structure for Circuit Breaker shall be as per manufacturer’s design & shall be deemed to be included in the cost of respective CB.

- Fabrication, proto-assembly, supply including transportation & insurance, unloading, storage, erection and commissioning of equipment support structures including nuts, bolts, fasteners and foundation bolts complete in all respect shall be in the scope of contractor.

- In the bid price schedule, the equipment support structures, nuts, bolts and fasteners & foundation bolts are indicated in Metric Ton (MT) and shall be paid as per respective items of BPS.

- The civil works shall be payable as per relevant item of BPS.

- Proto-corrected drawings and Bill of Materials of all equipment support structures etc. shall be in the scope of Contractor.

- The proto corrected drawings along with BOM are to be witnessed and certified by the contractor. Certified proto corrected drawings along with BOM shall be submitted to POWERGRID for information only. Contractor shall provide editable soft copies of design & drawings during detailed engineering.

    - CIVIL WORKS:

- The design of foundation shall be based on the soil investigation report and other parameters as per relevant IS codes & technical specification.

- The scope of civil work shall include but shall not be limited to the following based on drawings developed by the contractor:

- Structure and Foundation of non-Standard structures (if any) envisaged during detailed engineering. The design of foundation shall be based on the soil investigation report and other parameters as per relevant IS code & technical specification.

- Site levelling work:

- The item site levelling works includes Contouring of whole plot area within the boundary as per technical specification. The final area of levelling may be less than the whole plot area, which will be decided during detailed engineering.

- The Quantity of earthwork cutting & filling borrowed earth and FGL shall be proposed by vendor for approval of POWERGRID based on the approved contour level drawing and site HFL data.

- Mode of measurement of this item is in Cum of earthwork as per BOQ and technical specification.  The contouring of the plot area in scope as per technical specification is also deemed to be included in quoted rates of this item.

- HFL data duly verified by POWERGRID Site is required to be arranged by contractor for finalization of FGL (Finished Ground Level).

- Other miscellaneous requirements & scope:

- Stone spreading and anti-weed treatment including laying of PCC 1:5:10 (as per TS) in the switchyard for area under present scope. Layout for the same shall be developed by the contractor. This will supersede the clause 4.10 of Technical Specification : Civil works - Rev 12.

- Slope protection works/Retaining wall (if any)

- The work of Diversion of existing Nallah/ Surface runoff from external catchment area (including design & drawing), if required.

- Foundation for lighting poles, bay marshalling boxes, panels and control cubicles wherever required. The cost of these foundations shall deemed to be included in erection/installation of corresponding item/ equipment of BPS.

- Any other item/design/drawing required for successful completion of the scope of works.

- The scope of civil work shall include but not limited to the following based on POWERGRID drawings:

- Cable Trenches:

Cable trenches shall be constructed as per POWERGRID standard drawings provided in tender. However, Cable trench layout shall be prepared by vendor for approval of POWERGRID based on the standard sections.

- Foundations of Equipment Support Structure:

- 220 kV Equipment support structure foundations including 220 kV CB foundation, LT Transformer Foundation, DG Set Foundation, Foundation for Double pole structure.

- The foundations of these structures are including of embedment/grouting of foundation bolts.

- Gantry tower and beam, LM Structure:

220 kV Gantry tower and beam, LM Structure (If any).

- Foundations of 220 kV Towers and LM :

- Foundations of 220 kV Towers and LM (If any).

- The foundations of these structures are including of embedment/grouting of foundation bolts.

- Switchyard Panel Room:

The drawings pertaining to Switchyard Panel Room are attached as a part of tender drawings. Structural drawings shall be provided to the successful bidder during detailed engineering.

- For buildings, the complete civil works including internal and external finishing, stone soling for flooring, plinth protection, drain along plinth protection, electrical conduit and junction boxes, fan boxes, cable transit system etc. required to complete the building in all respect as per the drawing shall be payable in the plinth area rate. However, the quantity of the earthwork (excavation, backfilling, disposal etc.), concrete (all types), reinforcement steel, shall be measured and paid under respective items under BPS.

  - The work to be done under this specification shall include all labour, plant, equipment, material and performance of all work necessary for the complete installation and commissioning of switchyard. All apparatus, appliances, material and labour etc. not specifically mentioned or included, but are necessary to complete the entire work or any portion of the work in compliance with the requirements implied in this specification is deemed to be included in the scope of contractor.

  - Before proceeding with the construction work, the Contractor shall fully familiarize himself with the site conditions and General arrangements & scheme etc. Though the Employer shall endeavor to provide the information, it shall not be binding for the Employer to provide the same. The bidders are advised to visit the substation sites and acquaint themselves with the topography, infrastructure and also the design philosophy. The contractor shall be fully responsible for providing all equipment, materials, system and services specified or otherwise which are required to complete the construction and successful commissioning, operation & maintenance of the substation in all respects. All materials required for the Civil and construction/installation work including cement and steel shall be supplied by the Contractor.

  - Any other items not specifically mentioned in the specification, but which are required for erection, testing and commissioning and satisfactory operation of the substation are deemed to be included in the scope of the specification unless specifically excluded.

  - The Contractor shall also be responsible for the overall co-ordination with internal/external agencies, project management, loading, unloading, handling, moving to final destination for successful erection, testing and commissioning of the substation/switchyard.

  - Employer has standardized the technical specification for various equipment and works for different voltage levels. Items, which are not applicable for the scope of this package as per schedule of quantities described in BPS, the technical specification for the items should not be referred to.

  - The Contractor shall also be responsible for the overall co-ordination with internal/external agencies, project management, loading, unloading, handling, moving to final destination for successful erection, testing and commissioning of the substation/switchyard.

# SPECIFIC EXCLUSIONS:

The following items of work are specifically excluded from the scope of the specifications:

- Soil Investigation

# PHYSICAL AND OTHER PARAMETERS

4.1   Location of the Substation – The location of substation is indicated below:

| S. No | Name of Substation | Name of State | Nearest Rail Head |
| --- | --- | --- | --- |
| 1. | Pugalur (Karur) Substation | Tamil Nadu | Pugalur Railway Station |

4.2   Meteorological data - The meteorological data are as below:

| Station Name | Pugalur HVAC (Karur) Substation |
| --- | --- |
| Altitude | Less than 1000 meter above mean sea level (MSL) |
| Snow fall | NIL |
| Seismic Zone | As per NBC 2016 |
| Wind Zone | As per NBC 2016 |
| Min./Max. Ambient Temperature | 0 / 50 degree centigrade |
| Coastal Area Consideration | No |

4.3   Fault Level shall be considered as mentioned below:-

| Sr. No. | Name of Substation | 400kV | 220kV | 230kV |
| --- | --- | --- | --- | --- |
| 1. | Pugalur (Karur) Substation | - | - | 50kA for 1sec |

# SCHEDULE OF QUANTITIES

The requirement of various items/equipments and civil works are indicated in Bid price Schedules.

All equipments/items, Structures and civil works for which quantities has been given in the BPS shall be payable on unit rate basis. During actual execution, any variation in such quantities shall be paid based on the unit rate under each item incorporated in Letter of award. Actual execution of quantities/items in BPS are to be decided during detailed engineering and as per direction of engineer in charge.

Wherever the quantities of items/works are indicated in Set/LOT/LS, the bidder is required to estimate the quantity required for entire execution and completion of works and incorporate their price in respective Bid price schedules. For erection hardware items, Bidders shall estimate the total requirement of the works and indicate module-wise lump sum price bay wise and include the same in relevant Bid price schedules. Any material/works for the modules not specifically mentioned in the description in BPS, as may be required shall be deemed to be included in the module itself.

No cost compensation shall be considered on account of “Set/LOT/LS” items in any case if number of bays specified in section project remains unchanged.

Bidder should include all such items in the bid proposal sheets, which are not specifically mentioned but are essential for the execution of the contract. Item which explicitly may not appear in various schedules and required for successful commissioning of substation shall be included in the bid price and shall be provided at no extra cost to Employer.

# BASIC REFERENCE DRAWINGS

# The reference drawings, which form a part of the specifications, are given at Annexure-I  The enclosed drawings give the basic scheme and associated services etc. In case of any         discrepancy between the drawings and text of specification, the requirements of text shall prevail in general. However, the Bidder is advised to get these clarified from Employer.

          - Standard drawings shall be provided by POWERGRID. However, as per site requirement, while execution, contractor can change and shall develop single line drawing, general arrangement drawing, layout drawings, foundation & cable trench layout, erection key diagram & all other layout drawings as needed for successful execution of work in line with Cl. 6.1 above.

          - Layout drawings shall be finalized during detailed engineering based on best engineering practices and meeting the requirements of bidding documents

# DIFFERENT SECTIONS OF TECHNICAL SPECIFICATION

Employer has standardized its technical specification for various equipment and works for different voltage levels.  Items which are not applicable for the scope of this package, the technical specification for the items should not be referred to.

For the purpose of present scope of work, technical specification (Vol. II) shall consist of following sections, and they should be read in conjunction with each other.

| Sl. No. | Description | Revision |
| --- | --- | --- |
| 1. | Section - Project | Rev 00 |
| 2. | Section - General Technical Requirement | Rev 15 |
| 3. | Section-Switchgear | [(Rev.11 for CB, Rev.12 for CT & CVT) & (Rev.13 for ISO & LA/SA)] |
| 4. | Section - Power & Control Cable | Rev 06 |
| 5. | Section - Lighting System | Rev 07 |
| 6. | Section - Fire Protection System | Rev 06 |
| 7. | Section- Air conditioning | Rev. 04 |
| 8. | Section - Switchyard Erection | Rev 10 |
| 9. | Section – Structure | Rev 07 |
| 10. | Section - Civil Works | Rev 12 |
| 11. | Section - Control & Relay Panel | Rev 09 |
| 12. | Section - Substation Automation System | Rev 04 |
| 13. | Section - PLCC | Rev 05 |
| 14. | Section Telecommunication System | Rev 05 |
| 15. | Section – LT Switchgear | Rev 05 |
| 16. | Section – Lighting Specification | Rev 07 |

For Field Quality Standards, FQP document, attached with BID documents is to be referred to.

In case of any discrepancy between Section-PROJECT, Section-GTR and other technical specifications on scope of works, Section-PROJECT shall prevail over all other sections.

In case of any discrepancy between Section-GTR and individual sections for various equipments, requirement of individual equipment section shall prevail. In case of any discrepancy between Main body of Section-Project and Annexure(s) of Section-Project, provisions specified in Main body of Section-Project shall prevail.

# MANDATORY SPARES

The prices of mandatory spares shall be given by the Bidder in the relevant schedule of BPS and shall be considered for evaluation of bid. It shall not be binding on the Employer to procure all of these mandatory spares. The bidder is clarified that no mandatory spares shall be used during the commissioning of the equipment. Any spares required for commissioning purpose shall be arranged by the Contractor. The unutilized spares if any brought for commissioning purpose shall be taken back by the contractor.

Wherever spares in BPS/Technical Specification has been specified as “each type/each rating/each type & rating”: If the offered spare/spares are sufficient to replace the respective main equipment of all types/ratings, then such offered spare/spares shall be acceptable. It implies that common spare/spare set fulfilling the spare requirement of all types/ratings shall also be acceptable, provided it is configurable at site itself without special assistance of OEM.

Mandatory Spares, wherever mentioned, are envisaged for the equipment/items being supplied under the main equipment heads under present scope meeting the requirements of Technical Specifications. The component/sub-component of an equipment/item specified in BPS under Mandatory Spare, which is not applicable as per the offered design of respective main equipment, shall not be referred to.

# SPECIFIC REQUIREMENT

  - Relevant/applicable clauses of Specific Requirements as mentioned at C/ENGG/SPEC/SEC-PROJECT/SPECIFIC REQUIREMENT Rev. no. 10 shall also be referred for specified scope of work.

  - In Section-GTR and other technical specifications, the term ‘Employer and/or ‘Purchaser may be read as Employer.