|  |  |  |  |  |
| --- | --- | --- | --- | --- |
| **S​l. No.** | **Clause ref** | **Description as per bid document** | **Queries asked by the bidder** | **POWERGRID’s  clarification** |
|  | TS, Sec-II(Vol-II), Clause 1.1.5 | Dimensional Tolerance of Composite Insulators.The tolerances on all dimensions e.g. diameter, length shall be allowed as follows: ± (0.04d+1.5) mm when d≤300 mm. ± (0.025d+6) mm when d>300 mm with a maximum tolerance of +10 mm Where, d being the dimensions in millimetres for diameter, length as the case may be. | To maintain the tolerance of +/-50 mm as per previous technical specification and issue the amendment. | Provisions of Technical specifications provided in bidding document shall prevail |