| Sl. No. | Volume/Section/ Clause No. | Description | Bidders' Query | POWERGRID Reply |
| --- | --- | --- | --- | --- |
| 1. | Volume-II of Bidding Documents- Technical Specifications | Existing 220kV GIS details at Vadodara SS | For designing 220kV GIS adapter module/extn module for extension of existing ABB (Xiamen) make GIS, kindly Provide existing 220kV GIS SLD, Plan, Section view in cad or PDF format. | The existing 220kV GIS SLD, 220kV GIS Layout Plan and section drawings have already been provided as part of Tender drawings. Bidder to design and manufacture the offered GIS accordingly, meeting other requirement specified in the bidding document. |
| 2. |  | Existing 220kV GIS details at Vadodara SS | For designing 220kV GIS adapter module/extn module for extension of existing ABB (Xiamen) make GIS, kindly Provide existing 220kV GIS end module dimensional details and gas pressure details. | The existing available 220kV GIS end module drawing with all required details along with Gas pressure details have already been provided as part of Tender drawings. Bidder to design and manufacture the offered GIS accordingly, meeting other requirement specified in the bidding document. |
| 3. |  | Existing 220kV GIS details at Vadodara SS | For designing 220kV GIS adapter module/extn module for extension of existing ABB (Xiamen) make GIS, kindly Provide existing GIS data sheet which gives clear information about GIS pressure, CT -VT and other technical parameter. | GIS Gas pressure details of existing GIS end Piece module has already been specified under the tender drawings provided as part of bidding document. Further, other technical parameters of existing VT, CT is not required for extension of existing GIS. |
| 4. |  | Existing 220kV GIS details at Vadodara SS | Provide Existing GIS’s Available spare items on site. | Query is irrelevant. However, Bidders are advised to visit the substation sites as per clause no 1.5 of section project and acquaint themselves with the topography, infrastructure and the design philosophy. |
| 5. |  | Existing 220kV GIS details at Vadodara SS | For designing 220kV GIS adapter module/extn module for extension of existing ABB (Xiamen) make GIS, kindly Provide details in line with IEEE C37. | The existing 220kV GIS Interface module drawing of ABB make has already been part of Tender drawings and all the available required details are mentioned in the provided drawing. Bidder to design and manufacture the offered GIS accordingly, meeting all other requirement specified in the bidding document. |