| S. No. | Volume/Section/ Clause No./Page | Description | Bidder’s Query | POWERGRID Reply |
| --- | --- | --- | --- | --- |
| A. | Section Project SS-147_Rev-00.PDF |  |  |  |
| 1. | Pg 30 | GIS Extension piece (Interface) module: Extension of Three isolated phase/Three Phase, SF6 gas-insulated metal enclosed bus bar/duct module, each set comprising of the following: i. Extension piece (Interface) module, as required to extend existing bus bar/duct. ii. Gas monitoring devices, barriers, pressure switches, UHF PD Sensors, Support structures etc., as required. iii. All associated consumable items i.e., O-ring, adsorbents etc. with supervision of existing OEM. | Request kindly to note that item no. i) and ii) shall be designed and supplied by the OEM who is extending the bus bar/bus duct. Item iii) all associated consumables required for the existing GIS to be provided by the respective OEM or from spares already supplied by OEM. Hence, Item iii) is excluded from present GIS supplier’s scope. | It is the responsibility of bidder to design the extension interface module for successful extension of GIS as per the requirement of bidding documents. Further, all associated consumable items i.e., O-ring, adsorbents etc. with supervision of existing OEM is covered under the present scope of work and bidder to quote for the same under the respective BPS item for GIS Extension piece (Interface) module. Bidder to quote accordingly. |
| B. | Annexure-III_Specific_Requirement_Rev 10 |  |  |  |
| 2. | Annexure-S10 & Annexure-13 of GIS Rev 5A pg 74 | This dedicated copper grounding mesh is laid at the top of GIS floor and shall also be connected with dedicated grounding rod electrodes provided at a regular interval of not more than 12 meters around periphery of GIS building. This copper grounding mesh shall be laid after the GIS bays are place on the floor and shall be suitably covered with non-electrostatic rubber mats to avoid damage to mesh and to avoid hinderance in regular operation of equipment. | Earthing material of GIS shall be of adequate size of Aluminium flats. GEV scope of supply for earthing material shall be from the GIS equipment to the substation earth mat riser. Connection of earth mat riser and GIS earthing shall be in customer scope. Copper grounding mesh for GIS on FFL as per end customer specification is not recommended as this may cause hindrance in operations & Dilo movements even with rubber mats on the mesh. We recommend to have the same under the floor and is excluded from scope. Will take connections from riser as per this clause. | Bidder to comply the requirement as per Technical Specification. |
| 3. | Pg 90 | 420 kV Gas Insulated Switchgear (Double Main Busbar Scheme) ii) GIS Bus bar Module Extension (Make of Existing GIS: As per Section-Project): Extension of Three isolated phase, SF6 gas-insulated metal enclosed bus bar module, each set comprising of the following: | Being an extension as per Section-project, we have considered GIS equipment under this clause ii). | Bidder to quote as per BPS and the provisions of bidding document. |
| 4. | Pg 93 | vii) GIS ICT bay module (For 400kV HV side of 400/220kV ICT): i. One (1) number 3-phase, SF6 insulated circuit breaker without PIR, complete with operating mechanism. iv. Three (3) numbers 3-phase, single pole, group operated isolator switches, complete with manual and motor driven operating mechanisms. v. Three (3) numbers 3-phase, single pole, group operated safety grounding switches, complete with manual and motor driven operating mechanisms. | Offered GIS is single phase encapsulated. Hence, for CB, 3 Nos. single phase poles shall be provided with individual operating mechanism for each pole. Offered disconnector and earthing switches are single phase group operated type. | Acceptable in case other requirements of Technical Specifications are fulfilled for offered design of GIS. |
| C. | GIS Rev-5A.pdf |  |  |  |
| 5. | 5.28 pg 4 and 5.27 pg 18 | In addition to above suitable portable scissor lift shall be provided for access of distant portion of GIS installation. | Excluded from GIS scope. | Bidder to comply the requirement as per Technical Specification. |
| 6. | 5.41 9) pg 22 | GIS manufacturer as per their design shall preferably use maximum three standard straight horizontal outdoor busduct lengths for entire GIS installation to optimize the spare requirement. | As per specific requirement added to this clause, fifteen standard straight horizontal outdoor busduct lengths for entire GIS installation to optimize the spare requirement.” Depending on layout requirements, quantity of standard lengths is estimated. We confirm to maintain as minimum as practicable standard lengths discussing with you. | Bidder to refer sl. No. B.8 of Specific Requirement (Rev-10) attached at Annexure-III of Section Project (Rev-00) of Technical Specification. Bidder to quote accordingly. |
| 7. | 27.1, 27.2, 27.3, 27.4, 27.5 pg 60-67 | SF6 Gas Leak detector Gas filling and evacuating plant SF6 gas analyzer Portable PD monitoring system (generally applicable for 220kV & 132kV) On-line PD monitoring system | Excluded from GIS scope. We have not considered any gas handling tools and monitoring systems as per specification or as per BOQ. | Bidder to quote as per BPS and the provisions of bidding document. |
| D. | GTR Rev 15 |  |  |  |
| 8. | 4.6 pg 4 | System Parameters: Full wave impulse with stand voltage (1.2/50 micro sec.) – (for 400kV system) 1550kVp | For 400kV system, Impulse withstand voltage shall be 1425kVp. | For 400kV GIS, bidder to follow the impulse withstand test as per IEC 62271-203 and for other equipment’s, bidder to follow the values specified in Section-GTR. |
| 9. | 6.2.1.2 pg 10 | Space heaters: One or more adequately rated thermostatically connected heaters shall be supplied to prevent condensation in any compartment. The heaters shall be installed in the compartment and electrical connections shall be made sufficiently away from below the heaters to minimize deterioration of supply wire insulation. | Space heaters shall be provided in LCC and operating mechanism. | Acceptable in case other requirements of Technical Specifications are fulfilled for offered design of GIS. |
| 10. | Annexure B pg 46 | Seismic Calculations certified by NABL Labs shall also be acceptable | Seismic calculations prepared in-house shall be submitted for customer verification and acceptance. | Bidder to comply the requirement as per Technical Specification. |
| E. | Price Schedule |  |  |  |
| 11. | I) Sl.No. 3 | 420KV, 3150A, 63KA SF6 TO AIR BUSHING including support structure – 3 set | We presume set as 1 No. single phase bushing with support structure. | 01 Set consists of complete 420KV, 3150A, 63KA single phase SF6 TO AIR BUSHING including support structure, etc. Bidder to quote accordingly. |
| 12. | I) Sl. No. 4. | 420kV, 3150A, 63kA, Single phase, SF6Gas Insulated Bus Duct (GIB) outside GIS Hall along with associated support structure, etc, as pet technical specification – 275 Mtrs. | We quote GIB as per quantity in this item. If there is any increase in quantity, actuals may please be paid. | Any change in the quantity shall be dealt in line with provisions of bidding documents/contracts. |
| 13. | Sl.No. C 79, 80 | GIS : Spares – Single phase maintenance earthing switch NOTE 2 - IN CASE, DIS-CONNECTOR SWITCH (DS) & EARTH SWITCH (ES) IS PROVIDED IN A SAMEENCLOSURE WITH SEPARATE OPERATING MECHANISM, THEN THE MODULE COMPRISING OF DIS-CONNECTOR & EARTH SWITCH IN SINGLE ENCLOSURE WITHSEPARATE OPERATING MECHANISM IS TO BE PROVIDED UNDER THE HEAD OF SPAREDIS-CONNECTOR ONLY.) | As per Note 2; item no. 80 is included in item no. 79 in respective Disconnector enclosure. | The detailed requirements of applicability of Mandatory Spares shall be decided during detailed engineering considering offered GIS design and meeting the requirements of Technical Specifications. |
| 14. | Sl.No. 80 & 81 | Open / Close contactor assembly, timers, key interlock, interlocking coils…. & drive control cards for one complete MOM box for disconnector – 400kV GIS, for MES and for HES – 1 set | Proposed interlocks are all electrical with pad locking arrangement. Key interlock, drive control cards is not applicable. Spares applicable for the offered scope shall be considered. | The detailed requirements of applicability of Mandatory Spares shall be decided during detailed engineering considering offered GIS design and meeting the requirements of Technical Specifications. |
| F. | General Queries |  |  |  |
| 15. | General | Supply of H-beams/base plates Supply of Earthing between the earthing terminals and main earth grid Supply of Control & Power cables including accessories between LCC and CRP/SAS Civil Foundation work of GIS and GIB Submit the study report of VFTO generated for GIS installation. | Out of GIS scope, shall remain in Main contractor’s scope.. VFTO study is not applicable for 220kV GIS as per IEC.. | Bidder to comply the requirement of bidding documents. VFTO study is applicable for 400kV & above Voltage Level. |
| 16. | General | Type test | Type tests are performed once for the design. Type test validity shall be complied as per latest CEA guidelines. We do not include repetition of any type tests in our offer. Repetition of type test if any requested will be at extra cost & time. | Provisions of bidding documents shall prevail. Bidder to quote accordingly. |
| G. | BOQ given |  |  |  |
| 17. | Sl.no:9 | Magarwada Extn: 245kV,1600A, 50kA, 3 Single phase / 3Phase, SF6 Gas Insulated Bus Duct (GIB) outside GIS Hall along with associated support structure (Quantity mentioned here is for 3 Phase type) – 60m Vadodara Extn: 245kV,1600A, 50kA, 3 Single phase / 3Phase, SF6 Gas Insulated Bus Duct (GIB) outside GIS Hall along with associated support structure (Quantity mentioned here is for 3 Phase type) – 250m Rajgarh Extn: 245kV,1600A, 50kA, 3 Single phase / 3Phase, SF6 Gas Insulated Bus Duct (GIB) outside GIS Hall along with associated support structure (Quantity mentioned here is for 3 Phase type) – 100m | Quantity of Outdoor GIB shall be quoted as per BOQ given. Any increase in GIB quantity will have to be paid at unit rate for actual quantity. | Any change in the quantity shall be dealt in line with provisions of bidding documents/contracts. |
| H. | BOQ given: Mandatory spares-220kV GIS |  |  |  |
| 18. | Sl.no: I 125,126 & II 64,65,66 & III 40,41 | OPEN/CLOSE CONTACTOR ASSEMBLY, TIMERS, KEY INTERLOCK, INTERLOCKINGCOILS, RELAYS, PUSH BUTTONS, INDICATING LAMPS, POWER CONTACTORS, RESISTORS, FUSES, MCBS & DRIVE CONTROL CARDS ETC. (AS APPLICABLE) ONEOF EACH TYPE FOR ONE COMPLETE MOM BOX FOR 220KV GIS DISCONNECTORSWITCH, MAINTENANCE EARTHING SWITCH & FAST ACTING EARTHING SWITH- 1 SET | Offered interlocks are electrical with pad locking arrangement. Key interlock, interlocking coil and Drive control card are not applicable. Spares applicable for the offered scope shall be considered. | The detailed requirements of applicability of Mandatory Spares shall be decided during detailed engineering considering offered GIS design and meeting the requirements of Technical Specifications. |
| 19. | Sl.no:I 124,130,132 & II 62,71,74 & III 39,45,47 | 220kV GIS-Three phase Maintenance earthing switch including Main circuit, Enclosure, Driving mechanism and support insulator…. Drive Mechanism for 220kV GIS Maintenance Earth switch Motor for Drive Mechanism for 220kV GIS Maintenance Earth switch | As per type tested design Maintenance earthing switch is combined with disconnector with common operating mechanism. Hence these items shall not be quoted as separate, as this item is integral part of Disconnector spare item itself. | The detailed requirements of applicability of Mandatory Spares shall be decided during detailed engineering considering offered GIS design and meeting the requirements of Technical Specifications. |
| I. | GIS Rev-5A Technical specification |  |  |  |
| 20. | Cl 9.8 (for Cl 5.27 of GIS Rev 5A) | Portable Scissor Lift | Excluded from GIS Scope of Supply | Bidder to comply the requirement as per Technical Specification. |
| 21. | Cl 9.11 ( for Cl 5.41(9) of GIS Rev 5A) | .. fifteen standard straight horizontal busduct lengths… | Shall be firmed during detailed engineering stage. We shall try for least variations | Bidder to comply the requirement as per Technical Specification. |
| 22. | Annexure III | 245 kV Gas Insulated Switchgear (Double Main Busbar Scheme): 3-phase, group operated isolator switches, complete with manual and motor driven operating mechanisms. 3-phases, group operated safety grounding switches, complete with manual and motor driven operating mechanisms. | For 245kV as per type tested design, we offer three single phase group operated disconnector with combined safety earthing switch for one of the BB disconnector and outgoing feeder disconnector. | Acceptable in case other requirements of Technical Specifications are fulfilled for offered design of GIS. |
| J. | General Queries |  |  |  |
| 23. | General | Supply of H-beams/base plates Supply of Earthing between the earthing terminals and main earth grid Supply of Control & Power cables including accessories between LCC and CRP/SAS Civil Foundation work of GIS and GIB Study for Insulation co-ordination and selection of surge arrester Submit the study report of VFTO generated for GIS installation Responsible for any failure of the existing switchgear while the mentioned activities are in progress and Coordination with existing make vendor in presence of PGCIL representative for successful operation. | Out of GIS scope, shall remain in Main contractor’s scope. VFTO study is not applicable for 220kV GIS as per IEC. | Bidder to comply the requirement of bidding documents. VFTO study is applicable for 400kV & above Voltage Level. |
| 24. | General | Type test | Type tests are performed once for the design. Type test validity shall be complied as per latest CEA guidelines. We do not include repetition of type test in our offer. Repetition of type test if any requested will be at extra cost & time. | Provisions of bidding documents shall prevail. Bidder to quote accordingly. |
| 25. | General | Specific comment for Extension project | - End customer to authorize GE to do the necessary X ray / measurements (including associated de-gassing if needed) on existing GIS to allow design of interface. - We shall do degassing / open existing GIS Bus enclosure for measuring the interface requirement (if required) and during interface. We shall carryout HV test on our GIS only and shall not carry out HV Test on existing GIS. | - It is the responsibility of bidder to design the extension interface module for successful extension of GIS as per the requirement of bidding documents. Necessary required Shutdown for necessary X ray/measurements shall be arranged by the employer in coordination with appropriate regulatory authority. However, all associated works, items/materials, supervision of existing GIS OEM (if required) etc. required for the measurement works shall be in the scope of bidder. - It is the responsibility of bidder to design the extension interface module for successful extension of GIS as per the requirement of bidding documents. Further, site HV test on present scope GIS after installation shall be carried out by the bidder meeting the requirement of bidding document. |