| Sl. No | Ref Section | Provision in bidding document | Bidders Queries | POWERGRID Reply |
| --- | --- | --- | --- | --- |
| 1. | Vol. II, TS section project, Cl. 2.1.4. d | Dismantling & re-erection of Lightning Mast (LM): Existing LM, along with all lighting fixtures, cameras (if present), shall be dismantled, shifted and re-erected at suitable location to be decided during detailed engineering as per layout requirement. | 1) Please provide type of lighting Fixtures 2) Please provide the make and specification of the earlier installed cameras in the LM | Details of cameras and Lighting fixtures shall be provided during detailed engineering. However, bidder is advised to visit site as per cl. 2.5 of section Project |
| 2. | Vol. II, TS section project, Cl. 2.1.4. e | Control panel for Dia 410-411-412 is existing with bay no. 412 configured for 420kV Bus Reactor. Under present scope, control panel shall be modified for revised configuration of diameter mentioned at sl. no. b) above. The control panel shall be modified and augmented such that bay no. 410 shall be associated with 420kV, 63MVAR Bus Reactor and 412 bay shall be associated with present scope 400/230/33kV ICT. The augmentation and modification of control panel shall be done under item “400KV CONTROL PANEL AUGMENTATION” of BPS. | 1)Please provide the details of current configuration of Bay 410. 2) Also provide the existing protection SLD. 3) We understand that the existing control panels and control panels under current scope are placed at respective Switchyard Panel Room (SPRs) | 1) Presently 410 bay is spare. 2) Protection SLD shall be shared during detailed engineering. However, bidder is advised to visit site as per cl. 2.5 of section Project 3) Existing control panels are placed in control room building. No new control panel is envisaged under present scope. Only augmentation of the existing control panel is envisaged under present scope. |
| 3. | Vol. II, TS section project, Cl. 2.1.4. e | Provision for 1 no. bay is available in one of the existing 230kV control panel. Augmentation of same for the 230kV ICT bay is under present scope. Digital voltmeters, Ammeters, MW meters, Mvar Meters along with transducers to be included in control panel. | Please confirm the existing 230kV Control Panel is loose unused panel available for ICT 220kV Side protection. Please provide the scheme and OGA drawing of the existing panel. | Existing 230kV control panel has provision for 2 bays, out of which one bay is already in service. The provision for other bay, presently spare, shall be augmented for present 230kV ICT bay. |
| 4. | Vol. II, TS section project, Cl. 2.1.4. b | Dismantling, shifting and re-erection of 63MVAR Shunt reactors: Dismantling, shifting, & re-erection of 1 nos. 420 kV Shunt Reactors, 63MVAR (M/s BHEL make) from bay no. 412 to 410 bay in the same substation. The contractor shall also arrange the services of OEM representative (M/s BHEL) for dismantling and re-erection of the Bus Reactors. Present scope 400/230/33kV ICT shall be installed in the vacated 412 bay | 1) We understand the current 410 bay is Line bay, and clear levelled space will be available in 410 bay to erect the 63MVAR 420kV Bus Reactor. No other dismantling work is involved in 410 bay. In case of 410 Bay, the scope is only re-erection of 63MVAR shunt reactor. ETC(Erection, Testing and Commissioning) of CB, Isolator, Post Insulator, LA for bay 410 is not in current scope 2) We understand Testing commissioning of the Reactor is not in current scope. | 1) Presently 410 bay is spare bay, which shall be used under present scope for 420kV 63MVar, reactor being shifted from 412 bay. Fairly levelled land is available for placing 420kV reactor and 410 bay equipment. Kindly refer to GA drawing enclosed along with tender for various levels present in the present scope area. Erection testing and commissioning of 420kV Reactor, 400kV CB, Isolator, BPI , LA for 410 bay is included under present scope. Kindly refer SLD attached along with tender drawings. 2)Erection, testing and commissioning of 400kV Reactor is included under present scope under supervision of OEM as per referred clause of TS |
| 5. | Vol. II, TS section project, Cl. 2.2.4. c | Shifting of earthing pit, FF pipeline etc. for laying of the 245kV EHV cable is deemed to be included in this item of BPS | Please provide the existing piping layout. | Please find the attached drawing herewith for ready reference. |
| 6. | Vol. II, TS section project, Clause no.2.1.4.ii, Clause 2.2.4.a.ii and Clause 2.3.5.a | Digital RTCC panel with 5 no. of relays for 3ph. 400/2230kV Transformers. Existing 3 Nos. of 400/230/33kV 3-ph autotransformers at this substation are commissioned with parallel operation using Analogue RTCC Panels. The RTCC panels under present scope shall comprise of 5 Nos. of Digital RTCC Relays {One(1) as spare, One (1) for present scope transformers & Three(3) for existing transformers}. The Present Scope shall include required cabling between existing transformer RTCC panels/OLTC MB/Transformer MB and the Digital RTCC panels, wiring modifications in existing panels as per RTCC scheme requirement so as to enable parallel operation of transformer under present scope with existing transformers through Digital RTCC relays. | Please provide the rating and make of the existing Transformers. | For rating of existing Transformer, please refer tender SLD of respective substations. Make of the ICT shall be intimated during detailed engineering. |
| 7. | General | General Arasur | We understand that Spare feeder in ACBD & DCDB panels are available at site. Same shall be utilized for present scope of work. Please confirm. | Confirmed |
| 8. | Vol. III, BPS-SCH-1 Sl no. 155 SCH-3 sl no. 178 | Controlled Switching Device for 420 kV, 3-ph Circuit Breaker Service-Controlled Switching Device for 420 kV, 3-ph Circuit Breaker | As per the general practice CSD is procured through CB OEM to avoid interface issues during commissioning, hence it is requested to please delete the item from BPS as procurement of CB is not in current scope. If same is to be procured, please inform the make and model of CB. | CB is being procured under separate package, accordingly make & model of the CB to be supplied by Employer shall be provided during detailed engineering. |
| 9. | Vol. III, BPS-SCH-3 sl no. 45 | Dismantling of existing 400 kV tower including transportation and stacking of dismantled material at specified location | Please mark the location in the layout where stacking of dismantled material is envisaged. | After dismantling the 400kV towers shall be stacked in Raigarh Substation store as per space allocated by site in-charge. |
| 10. | Vol. II, TS section project, Cl .2.1.4.l and Cl 2.2.4.m | Contractor shall provide editable soft copies of design & drawings during detailed engineering. | We understand that the Towers, Beams & Equipment structures will be supplied as per the standard drawings available in the technical spec. So please remove Designing of the Towers, Beams & Equipment structures (as equipments are not in current scope) from the current scope. | Contractor shall provide editable soft copies of design & drawings during detailed engineering for non-standard structure, if any, in contractor scope. |
| 11. | Vol II, TS, Section Project, Cl. no. 2.1.4.a.ii) | The Present Scope shall include required cabling between existing transformer RTCC panels/OLTC MB/Transformer MB and the Digital RTCC panels, wiring modifications in existing panels as per RTCC scheme requirement so as to enable parallel operation of transformer under present scope with existing transformers through Digital RTCC relays. | As cabling between existing transformer RTCC panels included in scope, please provide the locations of RTCC panels of existing 3 nos transformers. | Existing RTCC panels are placed in control room building. However kindly note that the cable shall be paid as per actual quantity executed based on unit rate quoted by the bidder. |
| 12. | Vol II, TS, Section Project, Cl. no. 2.1.4.e) | The augmentation and modification of control panel shall be done under item “400KV CONTROL PANEL AUGMENTATION” of BPS | Please provide the as built schematics of 400kV & 220kV Control Panels that need to be modified. | Shall be Provided during detailed engineering. However, bidder is advised to visit site as per cl. 2.5 of section Project. |
| 13. | Vol II, TS, Section Project, Cl. no. 2.1.4.e) | Required modification in existing protection panel including wiring modification to suit new diameter configuration is included under present scope and shall be quoted under item or new protection panel | Please provide the as built schematics of 400kV Protection Panels that need to be modified. | Shall be Provided during detailed engineering. However, bidder is advised to visit site as per cl. 2.5 of section Project. |
| 14. | Vol II, TS, Section Project, Cl. no. 2.1.4.f) | …....The piping for fire protection system shall be extended from nearest available header. | Existing HVWS layout required to identify the requirement. | Shall be Provided during detailed engineering. However, bidder is advised to visit site as per cl. 2.5 of section Project. |
| 15. | Vol II, TS, Section Project, Cl. no. 2.1.4.g) | Augmentation of Visual monitoring system (VMS) for bays under present scope and their integration with existing Substation VMS system. | Please confirm the existing VMS softwate for integration | VMS software is NiceVision make version Net 3.1 |
| 16. | General | SLD, Existing Layout Hosur S/s | Bays nos & Bay names in SLD does not match with existing layouts provided with tender. | Bay no. and name of present scope bays are in order. |
| 17. | Vol. II TS, Section Project, Cl. no. 2.2.4.a.ii) | The Present Scope shall include required cabling between existing transformer RTCC panels/OLTC MB/Transformer MB and the Digital RTCC panels, wiring modifications in existing panels as per RTCC scheme requirement so as to enable parallel operation of transformer under present scope with existing transformers through Digital RTCC relays. | As cabling between existing transformer RTCC panels included in scope, please provide the locations of RTCC panels of existing 3 nos transformers. | The RTCC for existing ICT is placed in respective SPR or the bay. However kindly note that the cable shall be paid as per actual quantity executed based on unit rate quoted by the bidder. |
| 18. | Vol. II TS , Section Project, Cl. no. 2.2.4.d) | The necessary required modification in wiring, configuration etc. shall be in the scope of the contractor. | We understood no modification required in panel. Modification in wiring only required. Please confirm. | Modification as per scheme requirement mentioned in referred clause is in present scope of work |
| 19. | Vol. II TS , Section Project, Cl. no. 2.2.4.g) | The piping for fire protection system shall be extended from nearest existing header. | Existing HVWS layout required to identify the requirement. | Attached herewith for ready reference. |
| 20. | Section Project, Cl. no. 2.2.4.l) | Augmentation of Visual monitoring system (VMS) for bays under present scope and their integration with existing Substation VMS system. | Please confirm the existing VMS software for integration | VMS software is NiceVision make version Net 3.1 |
| 21. | Vol. II, TS section project, Clause no.2.1.4b | Dismantling, shifting and re-erection of 63MVAR Shunt reactors: The contractor shall also arrange the services of OEM representative (M/s BHEL) for dismantling and re-erection of the Bus Reactors | - We request PGCIL to kindly arrange the services of OEM i.e M/s. BHEL as the equipment has been purchased PGCIL. Or - Provide contact details of M/s. BHEL representative to coordinate with them regarding the same. | Bidder to quote as per bidding document. |
| 22. | Section Project, Cl. no. 2.3.5.a) | The Present Scope shall include required cabling (supply & installation) between existing transformer RTCC panels/OLTC MB/Transformer MB and the Digital RTCC panels, wiring modifications in existing panels as per RTCC scheme requirement so as to enable parallel operation of transformer under present scope with existing transformers through Digital RTCC relays. | As cabling between existing transformer RTCC panels included in scope, please provide the locations of RTCC panels of existing 3 nos transformers. | Location of existing RTCC panel shall be in 400kV Kiosk-1 for ICT-1& Kiosk-3 for ICT-2. Bidder may also visit the site and collect the required details. |
| 23. | Section Project, Cl. no. 2.3.5.c) | ........existing substation automation of Make: ABB, Microscada 9.3 (which is based on IEC 61850) and capability enhancement of substation and same as required including up-dating of system database, displays, development of additional displays and reports as per requirement. | SAS Architecture of the existing substation required to decide exact requirement. | Details shall be provided to successful bidder during detailed engineering. |
| 24. |  | …...necessary interface equipment (Router, Firewall, Ethernet Switches etc.) and integration work for transferring data to RLDC (RSCC)/NLDC/National Transmission Asset Management Centre (NTAMC) at Manesar through optical fiber based SDH communication link is also under present scope |  |  |
| 25. |  | …...any additional items (including supply of PU) required for completion of busbar scheme shall deemed to be included in the service item of 400kV and 220kV Bus bar protection augmentation of BPS. | Details of existing Busbar ring & CU & PU model nos. required. | Please refer clause 2.3.5 b of section project of technical specification. |
| 26. | Section Project, Cl. no. 2.3.5.d) | ….....Piping for fire protection system shall be extended from nearest existing Main Header existing in the switchyard. | Existing HVWS layout required to identify the requirement. | The main header for Firefighting shall be extended from nearest ICT main header pipe. Further any other details required, bidder may visit the site. |
| 27. | Section Project, Cl. no. 2.3.5.j) | ….... All the Gantry support structures, equipment’s (including owner supplied equipment), structures, cable trenches, auxiliary earthmat for isolators etc. shall be earthed by connecting them to the main Earthmat by the contractor. | Existing Earthmat Layout along with Earthmat spacing required to work out the quantity of Risers | Please consider earthmat spacing as 12m*12m for estimation of riser's quantity. The details of existing Earthmat shall be provided to successful bidder during detailed engineering. |
| 28. | Price Schedule_Schedule III-Civil Works_Item No.53 | Removing,cleaning and washing of existing stones and respreading of stones in switchyard excluding PCC | For Raigarh, there is no item for stone spreading, only item for Re-spreading is there. PGCIL will paid separetly if additional stone required during execution. Please confirm | The Gravel is existing in the area of switchyard under present scope. |
| 29. | Vol II BPS | Price Schedule_Schedule III-Civil Works_Construction of drain | It is understood that, for Raigarh we need to quote all complete basis (for excavation,RCC,PCC,Steel etc) for all drain section(whichever applicable) but for Arasur & Hosur Excavation, PCC, RCC, Steel will be paid extra under respective line items. Please confirm. | Bidder to quote as per BPS. |
| 30 | Vol III BPS Schedule III-Item No. 46 | Excavation in all kind of soil including Rock | As all the substation are existing substation, please share existing Soil investigation report to envisaged the actual soil type. | Soil report, if required, shall be provided to successful bidder during detailed engineering. |
| 31 | Vol III, BPS, Sch. III | General | It is understood that, Outdoor cable trench is required but no separate line item is there on BPS for the same. It will be paid component wise under respective line items. Please confirm. | Confirmed |
| 32 | Vol III BPS, Sch III, Civil Works- Item No. 10 | Construction of Buried trench | Please share a drawing for Buried cable trench | A general section drawing of Buried cable trench section is already attached along with the tender drawings. Refer drawing no. C/ENGG/SR-II/ARASUR EXTN./AUG/CABLE SECTION/01 titled “EHV Cable section” attached along with tender drawings. However kindly note that Section drawings for trench crossing, road crossing, drain crossing etc. shall be submitted by bidder during detailed engineering as per provision of standard Technical specification as mentioned at cl. no. 2.2.4 c) of TS section project. |
| 33. | Vol II, TS section: 400kV Transformer Specification_Rev 13 Page No. 68 of 69 | Page No. 68 of 69 Dynamic Short circuit withstand test (If specified in BPS) | BPS does not mention to carry out Dynamic Short circuit Test on 500MVA, 400KV/230/33 KV, 3-phase Autotransformer. Hence, we understand that there is no requirement of carrying out Dynamic Short circuit Test on 500MVA, 400KV/230/33 KV, 3-phase Autotransformer. Please confirm our understanding. | Requirement of Dynamic short circuit test is clearly specified in Cl. No. 3.14.1 of Tech. Specification: Section- Transformer (Upto 400kV Class) Rev 13. Bidder to comply the TS requirement. In case bidder does not have short circuit test report of 315MVA or above rating 400/220/33kV or 400/230/33kV, 3-Phase Auto transformer, it’s bid shall be treated as NON-RESPONSIVE. Design review of offered 400kV Class Auto transformer shall be carried out based on the design of short circuit tested 315MVA or above rating 400/220/33kV or 400/230/33kV, 3-Phase Auto transformer. Dynamic Short circuit test on offered transformer as per IEC 60076-5, may be carried out on request of bidder, without impacting the delivery schedule and at no extra cost to employer. |
| 34. | Vol III, BPS, Sch I, Sl. no. 77 and Vol. II, TS section: EHV XLPE Cable Rev01 | 220KV HV POWER CABLE ALONG WITH ACCESSORIES | It is mentioned in Technical specifications of 220kV EHV Cable that radial sealing (Metal sheath of Lead alloy ‘E’ / Corrugated Aluminum, (unless otherwise specified in Section Project). Section project does not mention anything about the cable corrugation. Further there is huge price difference between 220kV Cable with Lead sheath corrugation & 220kV Cable with aluminum corrugation. Request you to specify the Metal sheath is of Lead alloy ‘E’ or Corrugated Aluminum. | Sheath of Lead alloy ‘E’ or corrugated aluminum is acceptable. |
| 35. | Vol III, BPS, Sch I, Sl. no. 77 and Vol. II | 220KV HV POWER CABLE ALONG WITH ACCESSORIES | Please confirm if we need to consider the straight through joints for 220kV HV Power Cable. If yes then there is no separate line item in Price schedule for quoting straight through joints. | Kindly refer to clause 2.2.4 c of TS section project wherein it is specified that “The Item “220KV HV POWER CABLE ALONG WITH ACCESSORIES” of BPS includes all the Cable joint (if required), bonding cable, earth continuity cables, Link boxes, Sheath Voltage Limiters (SVLs) etc. as per requirement for entire cable route” |
| 37. | General | General | Please provide Google coordinates of all substations. | Bidder is advised to visit site as per cl. 2.5 of section Project |
| 38. | General | General | Please Provide the Contour Drawing & SBC for proposed Bay extensions as the same is out of the bidder scope. | Site levelling is not envisaged presently. However, in case it is to be executed during detailed engineering contouring shall be in scope of contractor. Soil report, if required, shall be provided to successful bidder during detailed engineering. |
| 39. | Vol. III BPS | Annexure III -Mandatory spare, Price Schedule -BOQ 400/220 kV RAIGARH Extn. | As per Annexure - III Mandatory spares, it is required to include spares for all 3 substations i.e Raigarh, Arasur & Hosur. However, there is no line item of mandatory spares in price schedule for Raigarh SS, whereas for Arasur & Hosur line item for respective spares is given. Please clarify. whether to consider or not. If yes, please provide revised price schedule. | Please refer Amendment-I |
| 40. | Vol II, TS Section: EHV XLPE POWER CABLE Rev 01, clause 1.2 | The EHV grade cable shall be single core, unarmoured, stranded, compacted/ Segmental Aluminium/Copper (as specified in BPS) ..........radial sealing (Metal sheath of Lead alloy ‘E’ / Corrugated Aluminium, (unless otherwise specified in Section Project), | The EHV grade cable shall be single core, unarmoured, stranded, compacted/ Segmental Aluminium/Copper (as specified in BPS) ..........radial sealing (Metal sheath of Lead alloy ‘E’ / Corrugated Aluminium, (unless otherwise specified in Section Project), 1.Please clarify whether lead alloy sheath or Corrugated aluminium sheath is required. 2. Please confirm that SCC rating is 40kA for 1 Sec. | - Sheath of Lead alloy ‘E’ or corrugated aluminum is acceptable - Confirmed |
| 41. | Vol II, TS Section Transformer (Upto 400kV Class) Annexure M | On-line insulating oil drying system (Cartridge type) | On-line insulating oil drying system (Cartridge type) is not mentioned in BPS nor it is clearly indicated in specification and/or exclusions in section project, whether it is mandatory or not to supply along with transformer. Please clarify if it is required to be considered. | On line insulating oil drying system is part of standard fitting and accessories as specified in cl. 20 of TS section – Transformer (Upto 400kV Class) and included under present scope |
| 42. | Vol II TS Section Project | TS of Visual Monitoring System | Technical specifications are not available for the "Video Monitoring System". | Technical Specification for Visual monitoring system (VMS) is available at Vol II TS Section Project Annexure II (Specific requirement rev. 07), Annexure-S9 |