| Sl. No. | # Volume/ Section/ Description | # Clauses | # Bidder’s Query | # POWERGRID Reply |
| --- | --- | --- | --- | --- |
| Volume-II: Technical Specifications |  |  |  |  |
|  | Clause-6 of Section project | Basic reference drawings (List of drawing as per-Annexure-I) | Please provide following details related to - Pandibili S/s (Hyosung Make) 1)Drawing of the End Flange which will be extended. 2)Pressure details in the gas compartments of the GIS | 1)Please refer Sr. No. 01 of Amendment No-04 for details of Bus Extension Module 400kV Pandibili S/s. 2) Please refer Sr. No. 02 of Amendment No-04 for GSLD - 400kV Pandibili S/s showing Pressure details in GIS Compartment. |
|  |  |  | Please provide following details related to -MISA S/s (ABB Make) 1)Drawing of the End Flange which will be extended. 2)Pressure details in the gas compartments of the GIS | 1)End Flange details are not available with POWERGRID. For clarity of scope of work, please refer clause no. 2.2.2 A of TS: Section Project 2)Bidder to refer attached SLD of Misa S/s in tender documents for the SF6 gas pressure of gas compartments. |
|  |  |  | Please provide following details related to -Rangpo S/s (Make: Hyosung) 1)Type of GIB to be extended 2)Drawing of the End Flange which will be extended. 3)Pressure details in the gas compartments of the GIS | 1) Bidder to quote as per provision of contract documents. 2) Bus Extension Module details shall be provided to successful bidder during detailed engineering. 3) Please refer Sr. No. 03 of Amendment No-04 for GSLD - 132kV Rangpo S/s showing Pressure details in GIS Compartment. |