| Volume-II: Technical Specifications |  |  |  |  |
| --- | --- | --- | --- | --- |
| Extension of 400/220kV Pandiabill GIS Substation- Eastern Region Bay Scheme-I (ERBSI) |  |  |  |  |
|  | Section project as per Clause no 2.2.1 | “Existing 400kV GIS bay no-410 shall be used for termination of one circuit of Pandiabili-Talchar -III D/C Line. For this termination, the existing GIB duct inside the existing GIS shall shall be re-oriented to the opposite direction from the existing 400KV Bay#410. | We need the following documents check the clearance and feasibility to carry out this works- 1)The location where this Line Bay -410 shall be terminated in the exiting Outdoor S/s. | 1)For termination of outdoor GIB for Bay#410, please refer Drg no: C/ENGG/OD/ERBS-I/PANDIABIL/GA/01 already enclosed with tender drawings. |
|  |  |  | 2)Existing Outdoor & Inside Hall Layout along with Foundation details, civil structural i.e. columns, beams etc. | 2)For details of positioning of column of existing GIS building, please refer Drg no: 014133-E-IS—GB-EL-4001 already enclosed with tender drawings. The foundation & civil structural details of existing 400KV GIS hall of Pandiabili S/s shall be shared with successful bidder during detailed engineering. Bidder to quote accordingly. |