| Sl. No. | Clause ref. | Existing Provision of the Bidding Document | Query asked by the bidders | POWERGRID’s Clarification |
| --- | --- | --- | --- | --- |
| 1 | Volume II, Section IA, Clause 1.4 | Technical Requirements of High Temperature Low Sag (HTLS) Conductor ………………………….. ………………………… Note: 1. In case more than one sag tension conditions are specified in the above table, Bidder shall offer only one design of HTLS conductor, which shall comply with all the above sag-tension requirements. | Pls. clarify as mentioned below, Note: 1. In case more than one sag tension conditions are specified in the above table for specified packages, Bidder shall offer only one design of HTLS conductor, which shall comply with all the above sag-tension requirements with respect to packages specified above. | It is clarified that the bidder shall offer the HTLS conductor meeting all the requirements specified under a package. Accordingly, different designs of HTLS conductor may be offered under different packages provided the offered HTLS conductor meets all the requirements specified under a particular package. |
| 2 | Volume II, Section IA, Clause 1.1 | Line Length (Approx.) | As per our survey report line length is 129.787 KM and 126.076 KM for OH02 & OH03 respectively but in tender its mention 177.5 KM & 173 KM respectively. Line length calculation sheet required from client | It is to clarify that the line length of 177.5 KM & 173 KM specified for OH02 & OH03 respectively is the specified route length which consists of line length of D/C & S/C (either on D/C or M/C Tower). A schematic diagram indicating arrangement of all four circuits of 400 Rourkela – Sundargarh TL is enclosed with the bidding documents, the same may be referred for more clarity. |
| 3 | Volume II, Section VIIB, Clause 2.11 | Packing ……………………. …………………… | Returnable or non-returnable conductor drum for all tenders. | As per the provisions of Technical Specification, conductor shall be supplied in non-returnable, strong, wooden drums. As an alternative to wooden drum, Supplier may also supply the conductors in returnable/ non-returnable painted steel drums. Based on the provisions of the bidding documents, Bidders may decide the choice of drum to be offered for the proposed HTLS conductor. |
| 4 | Volume II, Section IA, Clause 1.3.3 | ………………………….. Appropriate safety measures along with necessary safety tools and equipment to carry out de-stringing and stringing operations under the above conditions, including mechanical/ structural safety of the towers, shall be the responsibility of the contractor. This shall include inspecting the tower to ascertain quantity of missing members and bolts & nuts and erection of assorted tower members to be supplied under the scope of the package. ………………………… | Detail scope required against 200MT tower erection work. | As per the provisions of Technical Specification, Inspecting the tower to ascertain quantity of missing members and bolts & nuts and supply, erection of assorted tower members is included under the scope of the package. Accordingly, Bidders may carry out the inspection of existing towers to ascertain detailed scope of erection work. |
| 5. | Volume II, Part B, Section Project, Annexure-II List of drawings | SLD of substation for upgradation part in OH02 tender | SLD of substation for upgradation part in OH02 tender | It is to clarify that substation upgradation part in OH02 at 400/220kV Rourkela Sub Station; the Single Line Diagram (Drg No. C/ENGG-SS/ER/Rourkela/SLD/01) is already attached along-with tender documents. Bidders are requested to refer the same. |
| 6. | 1.1 of Appendix-1 (Terms and Procedures of Payment), Sample Forms and Procedures, Section-VI | I) Transmission Line Works Portion I(a) Interest bearing Option Advance 10% as interest bearing optional advance against 110% ABG (Ex- works value of tower/tower parts including nuts & bolts and all other material) Ib.1) Ex- works value of tower/tower parts (including nuts & bolts) - 60% of Ex works value of tower/tower parts against dispatch on completed tower basis. …………………………………….. | Please amend payment term to ‘’ tower parts delivered quantity basis’’ instead of ‘’completed tower basis’’. | Please refer Amendment No-I |
| 7. | 1.1 of Appendix-1 (Terms and Procedures of Payment), Sample Forms and Procedures, Section-VI | 1.4 Supply of Services Portion: Price Component for Installation (including Civil Works) - Tower Portion D Progressive Payment D1. Sixty Eight percent (68%)^^^^ (excluding the price component for survey) shall be paid on completion of the each of the items of Erection activity and on successful completion of quality check point involved in Installation, submission of the details of items, components, raw materials, services etc procured/availed from MSEs, if any, for the preceding 6 months, in respect of all the contracts in the respective executing Region of POWERGRID as per format enclosed at Section VI, Forms, VolumeI of the bidding documents and certification by Employer’s representative and on submission of GST invoice. ……………… | We request to amend the clause - monthly payment on pro-rata progress basis especially for civil works instead of completion of each items of erection activity. | Please refer Amendment No-I |