| **Sl. No.** | **Clause Reference** | **Existing Provision** | **Amended Provision** |
| --- | --- | --- | --- |
| 1 | Volume II, Section I,  Clause 3, Sl. No. C 4 ii) | |  |  | | --- | --- | | Sag for ruling span at minimum temp ( 0 deg C) and no wind condition (m) | ≥9.663 | | |  |  | | --- | --- | | Sag for ruling span at minimum temp **( 2.5 deg C)** and no wind condition (m) | **≥9.65** | |
| 2 | Volume II, Section I,  Clause 3, Sl. No. C 4 iv) | |  |  | | --- | --- | | Tension at 0°C and 2/3 wind condition  (32 kg/m2 wind pressure) | ≤ 4523 kg & not exceeding 70% of UTS of proposed conductor | | |  |  | | --- | --- | | Tension at **2.5°C** and 2/3 wind condition  (32 kg/m2 wind pressure) | **≤ 4474 kg** & not exceeding 70% of UTS of proposed conductor | |
| 3 | Volume II, Section I,  Clause 13, | **Service Condition**  ………………..   |  |  | | --- | --- | | Minimum ambient temperature (Degree Celsius) | 0 |   ……………………………. | **Service Condition**  ………………..   |  |  | | --- | --- | | Minimum ambient temperature (Degree Celsius) | **2.5** |   ……………………………. |