| Sl. No | Clause No | Document Name | Clause Description | Bidder Query | PGCIL Reply |
| --- | --- | --- | --- | --- | --- |
|  | 2.6 | Vol-II Part-I of III Section -I Introduction and General Technical Requirement | 33/11KV Power Transformer shall be of “Off Load Tap Changer” type. On LV side, the connection will be done with armoured XLPE cable. Therefore cable box arrangement shall be provided on LV side Transformer. | Kindly Clarify the same | Refer clause No. 2.6 of section – I of Vol-II part 1 of 3 which states as below: “33/11KV Power Transformers shall be of “Off Load Tap Changer” type. On LV side, the connections will be done with armoured XLPE cable. Therefore, cable box arrangement shall be provided on LV side Transformer.” |
|  |  | Section – IV Chapter -1 (Transformer) Annexure-II | On load Tap changer for 33/11KV Power Transformer |  |  |
|  | Steel Tubular Pole PKG ARP-DMS-05 A BOQ PR Line item No. |  |  |  |  |
|  | 20 |  | Galvenised Steel tubular Pole 540 MPA, SP64, 12 Meter | As per IS:2713, Steel Tubular Pole of 540MPA grade is no more exist as the same has been deleted (IS:2713 amendment attached). Kindly clarify and revised the same. | Refer Clause No. 2.4 of Section – I of Vol-II- part 1 of 3 which is reproduced herein below: Tubular poles shall be designed and manufactured as per IS 2713 (Part-I&II) 1980 with up to date. The pole shall be manufactured by HR coils of Grade E410 with minimum guaranteed Yst 410, UTS 540 Mpa as per IS 2062. Further, Roll Electric Resistance Welded (ERW) pipes will have with mechanical properties of 410 Yst, UTS 540 Mpa and % Elongation of 10 minimum. |
|  | 30 |  | Galvenised Steel tubular 12 of 3 Meters, 540, SP64 Pole Made from Steel Grade E410C |  |  |
|  | 50 |  | Galvenised Steel tubular 14.5 Meters, 540, SP76 Pole Made from Steel Grade E410C |  |  |
|  | 280 |  | Galvenised Steel tubular Pole 540 MPA, SP64, 12 Meter |  |  |
|  | 290 |  | Galvenised Steel tubular 12 Meters 540, SP-64 pole, Made from Steel Grade E410C |  |  |
|  | 4.3.6 | Vol-II-Part 2-Section IV Chapter 2 -SECTION 4 | 4.3.6. All the high voltage compartments must have pressure discharge flap for the exit of gas due to internal are to insure operator safety. All the HV compartment design ensures conformity to IEC-60298 and must be type tasted for Internal Arc Test`. | We would Like to inform that IAC classification is silent on this referred clause. We once again request you to consider as per IEC 62271-200 clause A. 4.5 (AFLR) all the HV compartment design shall ensure conformity to IEC- 60298 and must be type tasted at 25 kA (Full SC) for 1 second for IAC classification and duration considering human and equipment safety. We would also like to inform that here in North East requirement if 1 sec Internal Arc is mandatory for state Utilities. Specification of APDCL (IPDS Project- MV Switchgear) attached for reference. | Refer clause no. 4.3.6 of Section – IV Chapter -2 of Vol. II Part 2 of 3. |
|  | 4.17 | Vol-II-Part 2-Section IV Chapter 2 -SECTION 4 | Type Test | The referred clause calls for 7 years validity of TTR i.e. The test-reports submitted shall be of the tests conducted within last 7 (seven) years prior to the date of bid opening. In case the test reports are of the test conducted earlier than 7 (seven) years prior to the date of bid opening, the contractor shall repeat these test(s) at no extra cost to the Employer. This supersedes all other clauses mention elsewhere regarding date of type test for which type test reports are to be submitted. But as per attached CEA guideline – refer Clause 2 of Broad Guideline – Serial No. h – Serial No. XII which states that the validity of MV switchgear shall be 10 years from the date of bid opening. Hence request PGCIL to accept the validity accordingly. Guideline attached for reference. | Refer clause no. 1.7.1 of Section – V Vol. II Part 2 of 3. |