| Sl. No. | Ref Section | Provision in bidding document | Bidders Queries | POWERGRID Reply |
| --- | --- | --- | --- | --- |
| 1. | Vol II – Annexure II of section project (Specific requirement) Clause No. - 65 | Transmission line side insulator string along with hardware for line termination shall be in the scope of substation contractor. | We shall include Transmission Lines side insulator string for line termination and tension clamp for earth wire termination in present scope of work. Kindly confirm. | As specified in referred clause, line side insulator string for line termination is included under present scope. However, tension clamp for earthwire termination is not included under present scope. |
| 2. | Vol II – TS Vol. III, BPS | General | We understand that there is no PLCC & FOTE equipment included in present scope of works. Kindly confirm. | As per bidding document FOTE & PLCC terminal Equipment are not included under present scope of work, however, new wave traps specified under present scope for Kolar & NP Kunta substations shall be supplied as per TS Section-PLCC, Rev.5. Refer Amendment no. 2 sl.no. 4 for inclusion of Section:PLCC in TS |
| 3. | Vol II –Tender drawings and TS - Cl. no. 2.1.2.3 a) of Section Project Vol. III, BPS | Reconductoring of the NP Kunta-Kolar 400kV S/C Line (twin Moose) section with high capacity conductors (like twin HTLS equivalent or Quad Moose) is being carried out under separate package. Accordingly following modifications are under present scope: Existing 400kV Isolators, and Wavetrap with current rating of 2000A shall be dismantled and replaced with new equipment of 3150A current rating as per BPS. Dismantled equipment shall be handed over POWERGRID site incharge and kept in store area within substation as per direction of POWERGRID site I/c | We understand that supply of equipment as mentioned in the BPS is only included in present scope of works. Other equipment required to complete the bay works shall be free issued items. Kindly confirm. | Only Existing isolators and Wave traps of the bays shown in tender SLD & General arrangement drawing of NP Kunta shall be replaced under present scope as specified in referred clause of TS and BPS. Other equipment i.e. CB, CT, LA, BPI and CVT are already existing and are suitable to carry 3000A/3150A current and hence replacement of same not included under present scope. However, connectors of all existing equipment shall be changed to suit new conductor configuration and to carry 3000A/3150A current rating as specified in tender drawings, TS Section-Project and also refer NP Kunta s/s Section drawing Rev1 attached with Amendment sl.no.6. |
| 4. | Vol II – TS & tender drawings - Cl. no. 2.1.2.3 b) Vol. III, BPS | b) Erection Hardware: All conductor in current carrying path of Kolar Line shall be replaced by conductor of higher current rating. It includes replacement of conductors for Kolar Line Jackbus, Equipment interconnections along with associated dropper & jumpers as indicated in GA and sections drawing attached at Annexure-I. Accordingly, all associated clamps and connectors shall be replaced by clamps and connectors of 3000A/3150A current rating. Further Insulator strings and associated hardware fittings, cable trays & covers, spacers, junction box, earthwire, earthing material risers, auxiliary earthmat (excluding main earth mat), buried cable trenches/pipes for equipment & lighting, cable supporting angles/channels, insulating mats, cable sealing arrangement, all accessories etc. as required is covered under present scope. Line side Hardware fittings shall be suitable for Twin HTLS conductor. | Kindly note that we shall consider the EKD hardware scope for Kunta SS as per tender provided layout plan & section only. Kindly confirm. | Scope of Erection hardware is clearly specified in Tender documents. Please, refer to revised section drawings of NP Kunta S/s attached herewith as per amendment no.2 sl. no. 6. Bidder to quote as per bidding documents. |
| 5. | Vol II – TS & tender drawings Vol. III, BPS | General | We understand that augmentation of CRP for Kunta & Kolar SS is not included in present scope of works. Kindly confirm. | Confirmed. Augmentation of CRP for NP Kunta & Kolar SS is not envisaged under present scope |
| 6. | Vol II – TS Section project – Cl. no. 2.1.3.1 r), 2.1.4.1l), 2.1.4.1e) and Vol. III – BPS Sl. no. 80, 133,201of Schedule 1 | Augmentation of Visual monitoring system (VMS) for bays under present scope and their integration with existing Substation VMS system. The existing VMS drawing shall be provided to the contractor during detailed engineering. The bidder shall provide color IP camera (quantity as per BPS), with PAN, TILT and ZOOM facilities, suitably located in the switchyard for monitoring of bays and equipments. The scope of bidder shall include providing all Items, Accessories, Line Interface units, Fiber patch cords, Power supply units, Junction Boxes, Cables, Fiber Optic Cables, Hardware and Software, etc., as are applicable to the product design, to meet functional requirements. Compatibility enhancement of exiting VMS system, as needed, shall be done to integrate visual monitoring for bays under present scope with existing Visual monitoring system of the station. A copy of specification for Visual Monitoring system is enclosed at Annexure-S7 of Annexure – II with this specification, which shall, be read only for the Augmentation scope of existing VMS system. | Please let us know the existing make of VMS equipment for all the existing substations. | For Hiriyur, Kochi and Tuticorin substations - Existing NVR (VMS Software) is of Qognify(Nice vision) make. |
| 7. | Vol. II – Tender drawings |  | Please provide following drawings for all the existing substations lies under SS-82 package scope.: 1) Existing VMS layout drawing 2) Existing Outdoor Lighting Layout & Distribution diagram 3) Existing DSLP Layout 4) Existing Panel arrangement layout of SPR/Control Room building 5) Existing SAS Architecture diagram 6) Existing LT Board drawings (ACDB, DCDB, MLDB & ELDB) 7) Existing SS SAS architecture drawing 8) Existing SS Busbar protection scheme | 1) Existing VMS architecture of Kochi and Hiriyur S/s is already attached along with tender drawings. VMS architecture for Tuticorin is attached herewith. Existing Drawings as requested from sl.nos 2) to 8) shall be provided to successful bidder during detailed engineering, if required. |
| 8. | General | General | Request PGCIL to provide soil investigation reports for existing substations. | Soil investigation report for substations under present scope may be provided during detailed engineering, if required |
| 9. | General | General | Request to furnish the approx. soil resistivity to be considered for all the existing substations. | Existing Earthmat layout drawings for all substations is attached along with tender drawings for ready reference and hence requirement of soil resistivity details is not applicable. |
| 10. | Vol. II TS Section project – Cl. 3.0 | # SPECIFIC EXCLUSIONS The following items of work are specifically excluded from the scope of the specifications of A) At Kolar substation - Extension of LT Switchgear B) At NP Kunta S/s - Extension of LT Switchgear E) At Tuticorin-II GIS PS - Extension of LT Switchgear. | Please confirm whether there is Extension scope for MSB/ACDB/DCDB/MLDB/ELDB other than Hiriyur SS & Cochin SS in present scope of works since same is not specified in Section Project & Bid price schedule. Also confirm on sufficient spare feeders availability in MSB/ACDB/DCDB/MLDB/ELDB for present scope of Extn. works. | Extension of MSB/ACDB/DCDB/ MLDB/ELDB is not envisaged for Kolar, NP Kunta and Tuticorin S/s under present scope. Also, extension of MCB/MLDB/ELDB is not envisage for Kochi and Hiriyur S/s. Only extension of DCDB and ACDB for Kochi and Hiriyur S/s is kept under present scope. |
| 11. | General | General | We presume that New Control & protection panels for present scope of work as per section project will be placed in Switchyard Panel Room only for all the existing substations. Any panel shall not required to be placed in the control building. Please confirm. | New control and protection panels to be supplied under present scope shall be placed in Switchyard panel room. |
| 12. | General | General | Please let us know the creepage distance to be considered for all the existing substations. | Provision of bidding document is amply clear. Bidder to quote as per bidding document. |
| 13. | Vol. II Tender Drawings Vol. III – Sl. no. 37 | III Bay Works at Hiriyur SS. Erection Hardware for 400kV I type layout-Bus Work (For one diameter)as per technical specification; SET; 1. | Kindly note that as per tender SLD for Hiriyur SS, main bus bar extension for two 400kV diameters shall be included in the present scope of work. However, same is mismatching with BPS & layout. Kindly clarify. | Bus extension works for 400kV Main bus I and II for one diameter is envisaged under present scope. Bidder to quote as per BPS and GA drawing. For better clarity, refer sl. no.6 of amendment no. 2, for revised SLD for Hiriyur s/s. |
| 14. | Vol. II Tender Drawings and TS Section project Cl. 2.1.3.1 b) | 220kV, EHV XLPE cable along with cable termination kit (4 Run for R,Y, B and spare Phase for ICT#3) shall be supplied and laid in buried cable trench from 220kV side of ICT#3 up to 220kV ICT -3bay for work under present scope. | Kindly note that as per tender SLD provided for Hiriyur SS, we understand that the supply and laying of four runs of 220kV EHV cable run including one no. of spare run shall be included in the present scope of works. Kindly confirm. | Confirmed. |
| 15. | Vol. II TS Section project Cl. 2.1.5.3 c) | C. The scope of civil work shall include but shall not be limited to the following based on drawings developed by POWERGRID: Structure and foundation of standard lattice and pipe structures for standard equipment. iii) Switchyard Panel Room | From the Civil BPS we understand that Switchyard Panel room is in the scope of works and whereas there is no requirement mentioned in the supply BPS for the Fire Detection and Alarm system, Air Conditioning system and Illumination system for Switchyard Panel room. Request you to please add the system required for Switchyard panel room | Refer amendment no. 2, Sl. no.2&3 |
| 16 | - Vol-III_BPS Sch1. Sl. No. 6, 7, Sch2. Sl. No. 6,7 and Sch3. Sl. No.11,12 ii)Vol-II-Tender Drawings - Drg. No. C/ENGG/SR/OVL/ KOLAR/GA/01,Rev.0 and Drg. No. C/ENGG/SR/OVL/ KOLAR/SECTION/01,Rev.0 iii) Vol. II TS Section-Project – Cl. 2.1.1 Extension of 400/220kV Kolar substation (2.1.1.1, (b)) | - Supply & Erection of Erection Hardware for 400kV D type layout-Line bay and Spare bay of half dia) - Kolar GA and SLD - Accordingly, all associated clamps and connectors shall be replaced by clamps and connectors of 3000A/3150A current rating. Connector for new LA shall also be supplied. Further Insulator strings & associated hardware fittings, cable trays & covers, spacers, junction box, earthing material risers, auxiliary earthmat (excluding main earth mat), buried cable trenches/pipes for equipment & lighting, cable supporting angles/channels, insulating mats, cable sealing arrangement, all accessories etc. as required is covered under present scope. Line side Hardware fittings shall be suitable for Twin HTLS conductor. | As per GA Drawing it is given that “2. Existing conductor shown in red shall be replaced with new conductor as per following. a) Jack Bus-Twin HTLS, b) Droppers-Quad Bersimis, c) Equipment interconnection:4.5" AL. IPS Tube and d) Dropper for LA-Twin Bersimis ACSR and associated Hardware shall be replaced to suit above new conductor configuration. - Query:-We understand that after dismantling of existing IPS Al Tube, it can be reused in present scope kindly confirm As per Section Project Insulator strings & associated hardware fittings, cable trays & covers, spacers, junction box, earthing material risers, auxiliary earthmat (excluding main earth mat), buried cable trenches/pipes for equipment & lighting, cable supporting angles/channels, insulating mats, cable sealing arrangement, all accessories etc. as required is covered under present scope. - Query: -Please confirm whether the aforesaid dismantled materials shall be reused or bidder will consider fresh material for present scope | Reply for Query i): Dismantled IPS Al tube/conductor at Kolar substation shall not be used elsewhere under present scope and shall be handed over to POWERGRID Site I/C at Kolar S/s for storage/disposal. Reply to Query ii): The existing dismantled erection hardware & associated items at Kolar substation for present scope works shall not be re-used and shall be replaced by new items. All dismantled materials shall be handed over to POWERGRID Site I/C at Kolar S/s for storage/disposal. |
| 17 | Vol. II TS Section-Project – Cl. 2.1.1 Extension of 400/220kV Kolar substation (2.1.1.2) and Annexure III of Section Project: Breakup of mandatory spares | Sl No.; Description; Unit; Qty. 400/ 220 kV Kolar SS. 10; Spares-Substation Automation System. a); Bay Control Unit (IED) of each type; Set; 1. b); Ethernet switch of each type; Set; 1. | As per Section Project it is mentioned that "Design, engineering, manufacturing, testing and supply including transportation & insurance, storage of mandatory spares at site as per BPS. Detailed break-up of Mandatory spares shall be as per Annexure-III." Query:-In BPS there are no provision of supply of Spares-Substation Automation System where as in Annexure-III Break-up of Mandatory Spares, there are provision of 1 set Bay Control Unit (IED) of each type and 1 set Ethernet switch of each type are to be supplied as Spare for Kolar SS, kindly clarify | Bidder to quote as per BPS. SAS spares not applicable for Kolar Substation as there is no scope for SAS augmentation at Kolar S/s. Refer Amendment no.2 Sl.no. 5 for deletion of SAS mandatory spare breakup for Kolar S/s |
| 18 | i) Vol-III_BPS-Sch1. sl. No.13,14, Sch2.sl. No.13,14 and Sch.3. sl.no. 26,27) ii) Vol. II of TS section project - 2.1.1 Extension of 400/220kV Kolar substation (a. POWER & CONTROL CABLES:) | 1.1kV grade Power & Control cables along with complete accessories. All existing cables associated with NP Kunta Line-Tie-Future dia. shall be replaced. Old cables shall be handed over to POWERGRID site I/C | As per Section Project it is mentioned that "1.1kV grade Power & Control cables along with complete accessories. All existing cables associated with NP Kunta Line-Tie-Future dia. shall be replaced. Old cables shall be handed over to POWERGRID site I/C" Query:- All existing cable to be replaced with new cables. Please confirm whether the existing BMK and S/Y Panel room can be used in present scope and there are no need of supply and erection of BMK and also construction of SPR is not in the present scope. | Existing BMKs at Kolar S/s shall be replaced. Switchyard panel room is not present at Kolar S/s. Please note that existing Control and protection panels are placed at existing control room building at Kolar S/s. Construction of new switchyard panel room is not envisaged in present scope work. |
| 19 | - Vol.II BPS - Sch1. Sl. No. 20,21, Sch2. Sl. No. 20,21 and Sch3. Sl. No.30,31. ii) Vol II – Tender Drg. No. C/ENGG-SS/SR/NP KUNTA/OVL/GA/01,Rev.00 and Drg. No. C/ENGG-SS/SR/NP KUNTA/OVL/SECTION/01,Rev.00 iii) Vol.II-TS section project Cl. no. 2.1.2 b) | i) Supply & Erection of Erection Hardware for 400kV I type layout-Bus Reactor bay and Line Bay ii) General Arrangement Drawing for 400KV NP Kunta Substation (Extn.) under regional system strengthening scheme to mitigate the overloading of NP Kunta-Kolar S/C Line iii) Erection Hardware: All conductor in current carrying path of Kolar Line shall be replaced by conductor of higher current rating. It includes replacement of conductors for Kolar Line Jackbus, Equipment interconnections along with associated dropper & jumpers as indicated in GA and sections drawing attached at Annexure-I. Accordingly, all associated clamps and connectors shall be replaced by clamps and connectors of 3000A/3150A current rating. Further Insulator strings and associated hardware fittings, cable trays & covers, spacers, junction box, earthwire, earthing material risers, auxiliary earthmat (excluding main earth mat), buried cable trenches/pipes for equipment & lighting, cable supporting angles/channels, insulating mats, cable sealing arrangement, all accessories etc. as required is covered under present scope. Line side Hardware fittings shall be suitable for Twin HTLS conductor. | As per GA Drawing it is given that Twin Moose conductors for Jack Bus and associated jumpers, Twin Moose Droppers for Main Bus-I and Main Bus-II shall be changed to Quad Bersimis ACSR Conductor and 4" IPS Al Tube used for the interconnection of the Equipments in Kolar-Tie-Reactor dia to be changed to 4.5" IPS Al Tube Query i) We understand that supply and erection of new conductor, Hardware and total required 4.5" IPS Tube for Kolar-Tie-Reactor dia are in present scope kindly confirm As per Section Project Insulator strings and associated hardware fittings, cable trays & covers, spacers, junction box, earthwire, earthing material risers, auxiliary earthmat (excluding main earth mat), buried cable trenches/pipes for equipment & lighting, cable supporting angles/channels, insulating mats, cable sealing arrangement, all accessories etc. as required is covered under present scope. Query ii) Please confirm whether the aforesaid dismantled materials are reused or bidder will consider fresh material for present scope | Reply to query i): Confirmed Reply to Query ii): The existing dismantled erection hardware & associated items at NP Kunta substation for present scope work shall not be re-used and shall be replaced by new items. All dismantled materials shall be handed over to POWERGRID Site I/C at NP Kunta S/s for storage/disposal. |
| 20 | Vol. II TS section project – Cl. no. 2.1.2.3 e) Extension of 400/220kV NP Kunta substation | Existing Cable shall be retained for wiring of new equipment under present scope. Termination of all the Existing cables including termination of interpole cabling is covered under present scope. | As per Section Project it is mentioned that "Existing Cable shall be retained for wiring of new equipment under present scope. Termination of all the Existing cables including termination of interpole cabling is covered under present scope." Query:- We understand that existing cables are reused in present scope and Termination work of all existing cables and interpole cabling with supply of necessary required termination material will be in present scope. But in BPS Sch.3 there is no provision of Cable termination work, please clarify where the bidder will consider the said activity. | Cable termination works shall be deemed to be included in erection works of associated equipment. Further, it is to clarify that existing cables shall be reused for the new Isolators to be installed under present scope. However, in case any of the existing cables falls short for new Isolator connections then those cables shall be replaced with new cables along with its accessories. Cost of the same shall be deemed included in erection works of associated equipment. Any joints in existing cables is not acceptable. |
| 21 | Vol. III BPS schedule Sl. No. 11 and 23 | I Bay Works at Kolar SS. 400kV,3150A,0.5mH, 40kA Line Trap; EA; 2. II Bay Works at NP Kunta SS. 400kV,3150A,0.5mH, 50kA Line Trap; EA; 2. | Technical Specification for supply of 400kV,3150A,0.5mH ,40kA Line Trap and 400kV,3150A,0.5mH,50kA Line Trap are not available in tender documents. Kindly provide the same | Refer amendment no. 2, Sl. no.4 for TS section PLCC, Rev.05 to be referred for supply of 400kV Wave trap under present scope. |
| 22 | - Vol-III_BPS Sch1. Sl. No. 6, 7, Sch2. Sl. No. 6,7 and Sch3. Sl. No.11,12 ii)Vol-II-Tender Drawings - Drg. No. C/ENGG/SR/OVL/ KOLAR/GA/01,Rev.0 and Drg. No. C/ENGG/SR/OVL/ KOLAR/SECTION/01,Rev.0 iii) Vol. II TS Section-Project – Cl. 2.1.1 Extension of 400/220kV Kolar substation (2.1.1.1, (b)) | - Supply & Erection of Erection Hardware for 400kV D type layout-Line bay and Spare bay of half dia) - Kolar GA and SLD - Accordingly, all associated clamps and connectors shall be replaced by clamps and connectors of 3000A/3150A current rating. Connector for new LA shall also be supplied. Further Insulator strings & associated hardware fittings, cable trays & covers, spacers, junction box, earthing material risers, auxiliary earthmat (excluding main earth mat), buried cable trenches/pipes for equipment & lighting, cable supporting angles/channels, insulating mats, cable sealing arrangement, all accessories etc. as required is covered under present scope. Line side Hardware fittings shall be suitable for Twin HTLS conductor. | Technical Specification for supply of HTLS Conductor is not available in tender documents. Kindly provide the same. | Refer amendment no. 2, Sl. no.1 & 6 Accordingly, HTLS conductor shall be supplied by Owner. Hence, TS for HTLS is not applicable. |
| 23. | Vol. II TS Section EHV XLPE POWER Cable rev. 01, Cl. 1.8 and Section project Cl. 2.1.3.1 b) | Cl. 1.8 of section EHV XLPE power cable: Conductor The conductor shall be of Copper/Aluminium wires as specified in the Bid Price Schedule (BPS). The shape of conductor shall be compacted /segmental having high compactness and smooth surface finish. Cl. 2.1.3.1 b) of section project …………… The conductor and size of cable shall be copper and 2500Sq.mm. respectively | As per Technical Specification of EHV XLPE Cable – Rev-01. The Size of 220kV XLPE Cable Size should be as per BPS. But, in BPS the Size of 220kV EHV XLPE Cable is not mentioned in BPS. The Size of Cable 220kV, EHV XLPE Cable, 2500Sqmm mentioned in Section Project. Kindly confirms the Supply of Cable as per Section Project or not. Kindly provide the Size of 220kV EHV XLPE Cable. | Size and material of 220kV EHV XLPE cable shall be 2500Sq.mm copper as per referred clause of TS section-project. |
| 4. | Vol. II TS Section EHV XLPE POWER Cable rev. 01, Cl. 1.12 | Radial Moisture Barrier: This shall be of extruded Lead alloy “E” sheath or Corrugated Aluminium sheath unless otherwise specified in Section Project. In case Corrugated Aluminium sheath is used, suitable anti-corrosive layer shall be applied over the Aluminium sheath. | As per Technical Specification of EHV XLPE Cable – Rev-01, this shall be of extruded Lead alloy “E” sheath or Corrugated Aluminium sheath unless otherwise specified in Section Project. In Section Project the Specified Radial Moisture Barrier details are not mentioned. Kindly Confirm whether the Radial Moisture Barrier required with extruded Lead alloy “E” sheath or Corrugated Aluminium sheath. | Bidder may provide either Extruded Lead alloy “E” sheath or Corrugated Aluminium sheath as radial moisture barrier as mentioned in referred clause of TS. |
| 25. | Vol. II TS Section EHV XLPE POWER Cable rev. 01, Cl. 34 | 34. DISTRIBUTED TEMPERATURE MONITORING SYSTEM (DTS) The bidder shall include and provide separate “Distributed Temperature Monitoring System (DTS)” for entire route for EHV cables complete in all respects along with terminal coupling equipment, workstation and all required hardware & software for real time monitoring of conductor temperature profile and to provide load predictions………………………………………………………………………………………………………… | As per Tender Specification of 220kV XLPE Cable (23.0 EHV XLPE cable Rev01) the “Distributed Temperature Monitoring System” is mentioned. However in BPS no Items available for “Distributed Temperature Monitoring System”. As per the general practice the DTMS is required in Long Route Length of the UG Cables Systems. Hence, here the Route Length is very short (0.3 km Approx.). So, Kindly confirm the “Distributed Temperature Monitoring System” required or Not. | DTS is not envisaged under present scope as clearly specified at Cl. 2.1.3.1 b) of TS section Project. |