RECTIFICATION WORKS ON PILE AT LOC.NO.46

OF

132KV PASIGHAT- ROING TRANSMISSION LINE

TECHNICAL SPECIFICATIONS

SECTION – 1 CIVIL WORKS

# Introduction:

    - The intent of this technical specification covers all construction of all civil works as covered in the scope of contract as per drawings supplied by Owner.

    - All civil work shall be carried out as per design/drawings standardized by the Consultant / Owner and this specification provided by the Consultant / Owner. All standard drawings are enclosed with the tender documents. In case any item is not covered under specification then the same shall be carried out as per CPWD specification and applicable Standards and IS Codes. Any item for which specification is not provided herein and is not covered under CPWD specification shall be executed as per manufacturer guidelines. All materials shall be of best quality conforming to relevant Indian Standards and Codes.

    - The Contractor shall furnish all labour, tools, equipment, materials, temporary works, constructional plant and machinery, fuel supply, transportation and all other incidental items not shown or specified but as may be required for complete performance of the Works in accordance with drawings, specifications and direction of Owner.

    - All materials including cement, reinforcement steel and structural steel etc. shall be arranged by the Contractor. All testing required shall be arranged by the Contractor at his own cost. The contractor shall execute the work as per the Field Quality Plan (FQP) attached with this document.

    - The bidder shall fully appraise himself of the prevailing conditions at the proposed site. Climatic conditions including monsoon patterns, local conditions and site specific parameters and shall include for all such conditions and contingent measures in the bid, including those which may not have been specifically brought out in the specifications.

# GENERAL:

    - The work shall be executed in accordance with the specification stipulated in the Bill of Quantity and other bidding documents read along with CPWD (Central Public Works Department) specifications-2021 for civil works and IS codes with up-to-date corrections. For non-schedule items specification as given along with tender document and similar items of CPWD shall be applicable.

    - The list of references for civil works are BOQ, DRAWING ATTACHED WITH TENDER, CPWD specifications, relevant IS codes and best practices.

    - The works shall include:

- Removing loose concrete from the concrete pile surface at the location of crack or spalling to expose the rusted steel from all sides and cutting of concrete of about 20-25mm beyond the reinforcement in the vicinity of rusted steel to expose the re-bars completely The R.F. Steel shall be cleaned by sand blasting, scrubbing or wire brushing to remove the rust completely. To avoid anode formation an anti-corrosive coating of SikaTop® Armatec®-108 or Nitozinc Primer or equivalent product shall be applied to minimum 40-50 micron thick on the surface of the clean re-bars.

- Providing suitable bonding treatment over the old substrate concrete after cleaning the whole surface of the pile with Sikadur®-32 of Sika®, Nitobond EP of Fosroc or equivalent for bonding of fresh concrete with old pile surface. The bonding agent shall have bond strength of 11MPa & compressive strength 40 MPa

- Structural steel work riveted, bolted, welded in built up sections, trusses and framed work of 2000mm dia for a height of minimum 1000mm or as per site condition of 8mm thick MS Plate in two halves just 200mm above the existing MS Liner up to minimum of 1000mm or as per site condition depth may increase with all necessary bolts & nuts surrounding the piles bolting/welding and sealing the joints properly to make it water tight including dewater for making for dry working condition inside the MS Liners, including cutting, hoisting, fixing in position and applying a priming coat of approved steel primer all complete after completion of concrete it should use as permanent structure with pile like MS Liner which is in continue of existing MS Liner and as per direction of Engineer-In-Charge. All Liner Joints (both vertical & horizontal) shall be permanently welded as per relevant IS Codes and Lugs of 16mm Dia bars 9nos @1mc/c shall be provided on the inside the part of MS Liners for anchorages as per the approved drawings.

- Grouting the annular area between steel lining & existing pile concrete surface with fresh non shrink, free flowing, cementitious micro concrete of SikaRep® Microcrete-3 of Sika® or Renderoc LA of Fosroc or equivalent having a strength of 30 MPa in 3 days & 50 MPa in 28 days.

# Field Quality Plan

  - The work shall be executed as per the Standard Field Quality Document pertaining to building civil works along with the other quality plans indicated in the Technical specifications. All tests on materials and finished products as required in the field quality plan shall be carried out by the Contractor at his own cost.

  - The material testing shall be carried out in any of the NABL accredited laboratories/ Approved TPL of POWERGRID NERTS:

  - The contractor shall arrange at his own cost, packing, forwarding and other incidentals for conducting the tests.

  - The Contractor shall bring samples of all materials; finished or raw to the site and shall get them approved from the Engineer-in-Charge before using them in the work. Any material not conforming to approved samples shall be removed within 48 hours of the Engineer-in-Charge’s instruction to the Contractor to do so, failing which it shall be removed by the Engineer-in- Charge or his representative from the site at the risk and cost of the Contractor.

  - Samples of materials to be used with original/colour catalogue with specification shall be brought by contractor well in advance and shall be displayed and kept in separate sample rooms

on site. Samples of all kinds of materials to be used shall require approval of the Owner.

  - Materials shall be of approved quality and the best of their kind available and shall generally conform to I.S. Specifications. The Contractor shall order all the materials required for the execution of work as early as necessary and ensure that such materials are on site well ahead of requirement for use in the work. The work involved calls for high standard of workmanship combined with speed and to the entire satisfaction of the Engineer in Charge.

  - Before the placement of an award for supply & installation of equipment’s, materials. The contractor shall submit a proposal furnishing all the catalogs & specifications for approval of the Engineer in charge, well in advance.

****