| Sl. No | Item No./ Clause ref. | Existing provision | Amended Provision |
| --- | --- | --- | --- |
|  | 2.4.2.5 of Section Project [New Clause] | NIL | The Losses of 66/11 kV Power Transformer at 75 deg Celsius at rated voltage shall be not higher than the values indicated below (IS2026 along with latest amendments if any): Transformer Rating (in MVA); No-load losses (Fixed loss) KW; Load losses at 75°C KW. 6.3; 5.5; 45. |
|  | Item Description, BOQ Sch-1, Loss Reduction Works under RDSS Leh District, Sub-schedule – 66/11 kV Substation works: Sl. No- 288 | Item; Unit; Qnty. Control, relay and protection panel for 66kV Line (Bus Scheme as per SLD)-Duplex Panel Existing SAP code 1000009698; EA; 12. | Item; Unit; Qnty. Control, relay and protection panel for 66kV Line (Bus Scheme as per SLD)- Simplex Panel SAP code - 1000068938; EA; 12. |
|  | Item Description, BOQ Sch-1, Loss Reduction Works under RDSS Leh District, Sub-schedule – 66/11 kV Substation works: Sl. No- 287 | Item; Unit; Qnty. Control, relay, and protection panel for 66/11kV Transformer Protection Panel (For both HV & MV side)-Duplex panel Existing SAP code 1000009700; EA; 8. | Item; Unit; Qnty. Control, relay, and protection panel for 66/11kV Transformer Protection Panel (For both HV & MV side)-Simplex panel SAP code - 1000068939; EA; 8. |
|  | Item Description, BOQ Sch-1, Loss Reduction Works under RDSS Leh District, Sub-schedule – 66/11 kV Substation works: Sl. No- 290 | Item; Unit; Qnty. 66KV, 630A, 31.5KA, 3-Ph double break centre rotating type(DBCR)without earthing switch, gang operated, isolator along with support insulators, operating mechanism, base channel down pipe and all required accessories complete as per TS. Existing SAP code 1000056495; SET; 23. | Item; Unit; Qnty. 66KV, 630A, 31.5KA, 3-Ph double break centre rotating type (DBCR)without earthing switch, gang operated, isolator along with support insulators, operating mechanism, base channel down pipe and all required accessories complete as per TS. SAP code - 1000056495; SET; 25. |
|  | Item Description, BOQ Sch-1, Loss Reduction Works under RDSS Leh District, Sub-schedule – 66/11 kV Substation works: Sl. No- 326 | Item; Unit; Qnty. 72.5 KV, 1-PHASE, 25KA, 300-150/5-5 AMPS OUTDOOR TYPE CURRENT TRANSFORMER ALONG WITH JUNCTION BOX (1 NO JUNCTION BOX FOR 3 NOS OF 1-PHASE CTS) ETC, COMPLETE AS PER TECHNICAL SPECIFICATIONS. Existing SAP code 1000068464; SET; 1. | Item; Unit; Qnty. 72.5 KV, 1-Phase, 300-150/1-1 Amps outdoor type current transformer along with junction box (1 no junction box for 3 nos of 1-Phase cts) etc complete. SAP code - 1000068965; EA; 3. |
|  | Item Description, BOQ Sch-1, Loss Reduction Works under RDSS Leh District, Sub-schedule – 66/11 kV Substation works: Sl. No- 327 | Item; Unit; Qnty. 72.5 KV, 1-PHASE, 25KA, 200-100/5-5 AMPS OUTDOOR TYPE CURRENT TRANSFORMER ALONG WITH JUNCTION BOX (1 NO JUNCTION BOX FOR 3 NOS OF 1-PHASE CTS) ETC, COMPLETE AS PER TECHNICAL SPECIFICATIONS.. Existing SAP code 1000068462; SET; 19. | Item; Unit; Qnty. 200-100/1-1-1 A, 66KV, 1-PHASE, 31.5KA OUTDOR TYPE CURRENT TRANSFORMER ALONG WITH JUNCTION BOX (1 NO JUNCTION BOX FOR 3 NOS OF 1-PHASE CTS) ETC., COMPLETE AS PER TECHNICAL SPECIFICATIONS. SAP code - 1000041087; EA; 57. |
|  | Item Description, BOQ Sch-1, Loss Reduction Works under RDSS Leh District, Sub-schedule – 66/11 kV Substation works: Sl. No- 293 | Item; Unit; Qnty. 72.5 KV, 1-PHASE, 66KV/110 VOLT, SINGLE CORE OUTDOOR TYPE POTENTIAL TRANSFORMER ALONG WITH JUNCTION BOX (1 NO JUNCTION BOX FOR 3 NOS OF 1-PHASE PTS) AND REQUIRED ACCESSORIES ETC, COMPLETE AS PER TECHNICAL SPECIFICATIONS. Existing SAP code 1000041207; EA; 36. | Item; Unit; Qnty. 72.5 KV, 1-Phase, 66KV/110 Volt, Outdoor type potential transformer along with junction box (1 no junction box for 3 nos of 1-phase PT's) and required accessories etc, complete. SAP code - 1000068966; EA; 36. |
|  | Item Description, BOQ Sch-2, Loss Reduction Works under RDSS Leh District, Sub-schedule – 66/11 kV Substation works Sl. No- 03 | Item; Unit; Qnty. Control, relay and protection panel for 66kV Feeder Protection Panel - Duplex panel Existing SAP code 100042675; EA; 12. | Item; Unit; Qnty. Control, relay and protection panel for 66kV Feeder - Simplex panel SAP code - 100043188; EA; 12.. |
|  | Item Description, BOQ Sch-2, Loss Reduction Works under RDSS Leh District, Sub-schedule – 66/11 kV Substation works: Sl. No- 04 | Item; Unit; Qnty. Control, relay and protection panel for 66/11kV Transformer Protection Panel (For both HV & MV side)-Duplex panel Existing SAP code 100000857; EA; 8. | Item; Unit; Qnty. Control, relay and protection panel for 66/11kV Transformer (For both HV & MV side)-Simplex panel SAP code - 100043189; EA; 8. |
|  | Item Description, BOQ Sch-2, Loss Reduction Works under RDSS Leh District, Sub-schedule – 66/11 kV Substation works: Sl. No- 07 | Item; Unit; Qnty. Installation of 72.5KV, 25KA, 300-150/5-5 AMPS, 3-Phase outdoor type Current Transformer along with junction box etc (1 no junction box for 3 nos of 1-phase CTs) etc along with structure complete as per Technical Specifications. SAP code 100043970; SET; 1. | Item; Unit; Qnty. Installation of 72.5kV, 1-Phase outdoor type Current Transformer along with junction box (1 no junction box for 3 nos CT) etc along with structure complete as per Technical Specifications. SAP code - 100043981; EA; 60. |
|  | Item Description, BOQ Sch-2, Loss Reduction Works under RDSS Leh District, Sub-schedule – 66/11 kV Substation works: Sl. No- 08 | Item; Unit; Qnty. Installation of 72.5KV, 25KA, 200-100/5-5 AMPS, 3-Phase outdoor type Current Transformer along with junction box etc (1 no junction box for 3 nos of 1-phase CTs) etc along with structure complete as per Technical Specifications. Existing SAP code 100043971; SET; 19. | To be deleted |
|  | Item Description, BOQ Sch-2, Loss Reduction Works under RDSS Leh District, Sub-schedule – 66/11 kV Substation works: Sl. No- 011 | Item; Unit; Qnty. Installation of 9kV, 10kA, 1-ph LA with porcelain bushing on Pedestal structure including installation of structure complete with terminal connectors etc. Existing SAP code 150000525; EA; 24. | Item; Unit; Qnty. Installation of 9kV, 10kA LA, 3-Phase with porcelain bushing including structure complete SAP code - 100043204; SET; 8. |
|  | Item Description, BOQ Sch-2, Loss Reduction Works under RDSS Leh District, Sub-schedule – 66/11 kV Substation works: Sl. No- 39 | Item; Unit; Qnty. 66 kV Solid Core Bus Post Insulator fittings and accessories. Existing SAP code 100005688; SET; 60. | Item; Unit; Qnty. Erection of 66kV Solid core Bus Post Insulator assembly along with structure, SAP code - 100043191; SET; 60. |
|  | Item Description, BOQ Sch-2, Loss Reduction Works under RDSS Leh District, Sub-schedule – 66/11 kV Substation works: Sl. No- 05 | Item; Unit; Qnty. 72.5 kV, 630A, 25 KA, 3-Phase Double Break Isolator with one E/S Existing SAP code 100000625; EA; 10. | Item; Unit; Qnty. 72.5 kV, 630A, 25 KA, 3-Phase Double Break Isolator with one E/S SAP code - 100000625; EA; 12. |
|  | Item Description, BOQ Sch-2, Loss Reduction Works under RDSS Leh District, Sub-schedule – 66/11 kV Substation works: Sl. No- 47 | Item; Unit; Qnty. Design, engineering, supply of labour, material and construction of RCC foundation for 6.3 MVA, 66/11 KV, 3-phase Power Transformer per approved drawing and TS; EA; 8.000. | Deleted |
|  | Item Description, BOQ Sch-2, Loss Reduction Works under RDSS Leh District, Sub-schedule – 66/11 kV Substation works: Sl. No- 48 | Item; Unit; Qnty. Design, engineering, supply of labour, material and construction of RCC foundation as per approved drawing and TS for 66 KV Circuit Breaker; EA; 20.000. | Deleted |
|  | Item Description, BOQ Sch-2, Loss Reduction Works under RDSS Leh District, Sub-schedule – 66/11 kV Substation works: Sl. No- 49 | Item; Unit; Qnty. Design, engineering, supply of labour, material and construction of RCC foundation as per approved drawing and TS for 66 KV CT for3phase; EA; 60.000. | Deleted |
|  | Item Description, BOQ Sch-2, Loss Reduction Works under RDSS Leh District, Sub-schedule – 66/11 kV Substation works: Sl. No- 50 | Item; Unit; Qnty. Design, engineering, supply of labour, material and construction of RCC foundation as per approved drawing and TS for 66 KV Isolator for 3 phases; EA; 37.000. | Deleted |
|  | Item Description, BOQ Sch-2, Loss Reduction Works under RDSS Leh District, Sub-schedule – 66/11 kV Substation works: Sl. No- 51 | Item; Unit; Qnty. Design, engineering, supply of labour, material and construction of RCC foundation as per approved drawing and TS for66 kV Bus Post Insulator for single phase; EA; 60.000. | Deleted |
|  | Item Description, BOQ Sch-2, Loss Reduction Works under RDSS Leh District, Sub-schedule – 66/11 kV Substation works: Sl. No- 52 | Item; Unit; Qnty. Design, engineering, supply of labour, material and construction of RCC foundation as per approved drawing and TS for 66 kV Tower [Incomer Gantry / Bus Gantry]; EA; 49.000. | Deleted |
|  | Item Description, BOQ Sch-2, Loss Reduction Works under RDSS Leh District, Sub-schedule – 66/11 kV Substation works: Sl. No- 53 | Item; Unit; Qnty. Design, engineering, supply of labour, material and construction of RCC foundation as per approved drawing and TS for 60kV, 10kA,LA with porcelain for Transformer for three phase; EA; 60.000. | Deleted |
|  | Item Description, BOQ Sch-2, Loss Reduction Works under RDSS Leh District, Sub-schedule – 66/11 kV Substation works: Sl. No- 54 | Item; Unit; Qnty. Design, engineering, supply of labour, material and construction of RCC foundation as per approved drawing and TS for9kV, 10kA, LA with porcelain for Transformer for three phase; EA; 8.000. | Deleted |
|  | Item Description, BOQ Sch-2, Loss Reduction Works under RDSS Leh District, Sub-schedule – 66/11 kV Substation works: Sl. No- 60 | Item; Unit; Qnty. Design, engineering and construction of Control Room Building including supply of T&P, Labour, Cement, Reinforcement Steel, Formwork, Excavation, RCC (M30 Grade) including Double Wall in panelling over plaster Etc., all complete as per Technical Specification and drgs in 66/11 KV new sub-stations.; M2; 840.00. | Deleted |
|  | Item Description, BOQ Sch-2, Loss Reduction Works under RDSS Leh District, Sub-schedule – 66/11 kV Substation works: New Item (service code | NIL | Item; Unit; Qnty. Earth work in Excavation for foundations in all types of soil and rock including backfilling disposal etc. for all leads and lifts. (SAP code 100001324); M3; 7057.50. |
|  | Item Description, BOQ Sch-2, Loss Reduction Works under RDSS Leh District, Sub-schedule – 66/11 kV Substation works: New Item | NIL | Item; Unit; Qnty. Providing and laying of Plain Cement Concrete (PCC) (1:4:8) ( SAP code 100001325); M3; 351.25. |
|  | Item Description, BOQ Sch-2, Loss Reduction Works under RDSS Leh District, Sub-schedule – 66/11 kV Substation works: New Item | NIL | Item; Unit; Qnty. Providing and laying of Plain Cement Concrete (PCC) (1:2:4) ( SAP code 100001326); M3; 34.72. |
|  | Item Description, BOQ Sch-2, Loss Reduction Works under RDSS Leh District, Sub-schedule – 66/11 kV Substation works: New Item | NIL | Item; Unit; Qnty. Providing and laying of Reinforced Cement Concrete of Grade M25 Mix including precast, shuttering, grouting of pockets & underpinning but excluding steel reinforcement ( SAP code 100001327); M3; 1660.60. |
|  | Item Description, BOQ Sch-2, Loss Reduction Works under RDSS Leh District, Sub-schedule – 66/11 kV Substation works: New Item | NIL | Item; Unit; Qnty. Steel Reinforcement for RCC work including straightening, cutting, bending, placing in position and binding all complete in foundation and in superstructure at all levels. ( SAP code 100001329); MT; 110.19. |
|  | Item Description, BOQ Sch-2, Loss Reduction Works under RDSS Leh District, Sub-schedule – 66/11 kV Substation works: New Item | NIL | Item; Unit; Qnty. Supply & Fixing in position of Misc. Structural steel including rails, embedment's, edge protection angles, gratings etc. as per approved drawing but excluding the reinforcement steel and steel for lattice and pipe structures. ( SAP code 100001331); MT; 2.12. |
|  | Item Description, BOQ Sch-2, Loss Reduction Works under RDSS Leh District, Sub-schedule – 66/11 kV Substation works: New Item | NIL | Item; Unit; Qnty. Design, engineering and construction of New Control Room Building including indoor cable trench - All civil works as per approved drawing and technical specifications complete EXCEPT for Excavation, PCC, RCC and reinforcement which shall be paid separately as per BPS. (SAP code 100007101); M2; 840.00. |
|  | Item Description, BOQ Sch-2, Loss Reduction Works under RDSS Leh District, Sub-schedule – 66/11 kV Substation works: New Item | NIL | Item; Unit; Qnty. Construction of Septic tank and soak pit for CRB as per approved drawing and technical specifications. (SAP code 100001740); EA; 7. |
|  | Clause no 2.3, Section - Project | Substation; Altitude (in meter). 66/11 kV Tangste; 5669. 66/11 kV Chushul; 4350. 66/11 kV Mudh Nyoma; 4180. 66/11 kV Phobrang; 4420. 66/11 kV Hanle; 5290. 66/11 kV Koyul; 4660. 66/11 kV Korzok; 4595. The service condition mentioned above are indicative only. The contractor shall finalize the design of the equipment/system as per the actual service condition of the installations. | Substation; Altitude (in meter); GPS coordinates of four corners. 66/11 kV Tangste; 4107; N34º01.031’ E078º07.575’; N34º01.040’ E078º07.621’; N34º01.006’ E078º07.634’; N34º00.987’ E078º07.589’. 66/11 kV Chushul; 4422; N33º36.367’ E078º37.699’; N33º36.340’ E078º37.698’; N33º36.351’ E078º37.641’; N33º36.387’ E078º37.655’. 66/11 kV Mudh Nyoma; 4157; N33º10.937’ E078º40.864’; N33º10.985’ E078º40.906’; N33º10.925’ E078º40.954’; N33º10.907’ E078º40.914’. 66/11 kV Phobrang; 4371; N34º01.875’ E078º25.740’; N34º01.910’ E078º25.743’; N34º01.893’ E078º25.807’; N34º01.863’ E078º25.792’. 66/11 kV Hanle; 4277; N32º47.148’ E079º00.235’; N32º47.118’ E079º00.278’; N32º47.115’ E079º00.226’; N32º47.146’ E079º00.235’. 66/11 kV Koyul; 4214; N32º55.251’ E079º12.580’; N32º55.216’ E079º12.568’; N32º55.227’ E079º12.571’; N32º55.260’ E079º12.543’. 66/11 kV Korzok; 4566; N33º01.984’ E078º16.329’; N33º01.956’ E078º16.298’; N33º01.976’ E078º16.253’; N33º02.003’ E078º16.286’. The contractor shall finalize the design of the equipment/system as per the above service condition of the installations. |
|  | Clause 2.4.7.2, Section - Projects | In finishing schedule of the Control Room Building, “Precast Terrazo Tiles” shall be read as “Vitrified Tiles”. | In finishing schedule of the Control Room Building, “Precast Terrazo Tiles” shall be read as “Vitrified Tiles”. However for control room & Sub-Station Incharge room wooden flooring shall be provided. |
|  | Clause 2.4.7.9, Section - Projects | New Clause | Wooden paneling with polish shall be provided in control room & In-charge room. Accordingly, item of “Oil bound washable distemper on smooth surface applied with 2mm thick POP putty” for control room & In-charge room stands deleted from finishing schedule of the Control Room Building. |
|  | Clause 2.4.1.3, Section - Projects | Potential based control and protection has not been envisaged in the system. Supply from Potential Transformer shall be used for metering and indication only. | 66 kV Potential Transformer (electromagnetic type) shall have two cores which shall be used for metering and protection purpose. |
|  | Clause 2.4.1.10, Section - Projects | New Clause | All the protective relays to be provided under the contract shall be Numerical type and conform to IEC-61850. In all numerical protections, 20% spare DI/DO shall be provided. |
|  | Clause 2.4.1.11, Section - Projects | New Clause | 66 kV line feeders shall have Distance Protection and Non-Directional Over Current & Earth Fault protection. The Over Current & Earth Fault protection shall be in the Bay Control Unit (BCU) to be provided for 66 kV line bay. The BCU shall also have 3-phase auto reclosure facility. |
|  | Clause 2.4.1.12, Section - Projects | New Clause | For each 66 KV Line & 66/11 KV power transformer, Bay Control Unit (BCU) shall be provided in control panel. Same shall be used for monitoring parameters, synchronization, interlocking for all bays and Auto Reclosure feature for line feeders. For breaker control, control switch shall be provided in the panel. |
|  | Clause 2.4.2.3, Section - Projects | Over current and earth fault protection shall be provided for Power transformer and 66 kV & 11 kV feeders | For Power transformers, Directional Overcurrent shall be provided on HV side and Over current & Earth fault protection shall be provided on LV side. For 11 KV feeders, Over current & Earth fault protection shall be provided. |
|  | Clause 2.4.2.4, Section - Projects | Additionally, Differential relay Protection & REF Protection shall be provided for 66 kV class transformers. Power Transformer shall have necessary CTs’ (Bushing CTs). | Additionally, Differential Protection and High impedance REF Protection on LV side shall be provided for 66 kV class transformers. Power Transformer shall have necessary CTs’ (Bushing CTs) for REF protection. |

Corresponding to the above changes in BOQ existing “Price_schedule” stands replaced with “Price_schedule_Rev1” and is attached herewith.

Note- Bidders are requested to consider the revised excel ‘Price_schedule_Rev1’ for bid preparation/submission. It may be noted that while submitting the bid, Bidders are required to change the excel file name from ‘Price_schedule_Rev1’ to ‘Price_schedule’. As per the provisions of the portal, it is mandatory to upload excel file with titled ‘Price_schedule’ (Bidders may refer user manuals at the portal https://etender.powergrid.in regarding submission of bid).