| Sr. No. | Clause No. & Reference | Tender Description | Bidders Query | POWERGRID Reply |
| --- | --- | --- | --- | --- |
|  | Part-1, Section-3, Bid Data Sheet (BDS), ITB Clause No. 44.1 | The Performance Security amount is 10% of Contract Price | We request you to consider for submission of 3% value of performance bank guarantee instead of 10% as per circular released by ministry of Finance Government of India vide office memorandum no. F.9/42020-PPD dated 12.11.2020, Procurement policy division, | Provisions of Bidding documents remain unchanged. |
|  | SBD Part-1 |  | Please clarify in whose favour the EMD BG will be prepared, as "In favour of" is not mentioned in the tender document. And also detailed address is required. | Bidders are requested to refer Format of Bank Guarantee for Bid security in Part-1 which is amply clear |
|  | SBD Part-1 | Section-2 Page-20 | In Clause no. 1.5, it is mentioned that "in case of price reduction during e-Reverse Auction, if envisaged as per Section 3 of RFB document, or for any other reason including matching L1 price pursuant to the purchase preference extended, the revised prices shall be so as to ensure that classification of the bidder ‘Class –I local supplier’ remains unchanged" Please clarify whether e-Reverse Auction will be done or not. | e-Reverse Auction is not applicable for subject package |
|  | 6.3 MVA, 66/11 KV, 3 PH, 50 HZ, ONAN, CU WOUND, OUTDOOR CONVENTIONALTYPE POWER TRANSFORMER ALONG WITH TRANSFORMER OIL & ALL ACCESSORIESCOMPLETE | BOQ Sl no- 283, 66/11kV Power transformer | BOQ is mentioned for 66/11KV 6.3 MVA Power transformer. However in TS SBD part-2 Technical Specification Appendix-A, The Power transformer Technical Particulars are of 12.5 & 15 MVA 66/11kV PTR. Please provide the TS for 6.3MVA, 66/11kV PTR. | For General construction refer the technical specification of 66/11 KV Sub-station in the SBD-Part-2 technical specification. Refer Amendment No-1 for No load loss and Full load loss of the transformer |
|  | ACSR Conductor | SBD Part-2, employers requirement page 60 | As per SBD Part-2, employers requirement page 60, it is mentioned that 66KV Bus bar shall be of ACSR Zebra. However as per BOQ of 66/11kV Substation, ACSR Panther conductor provided for substation. We are proceeding with ACSR Panther conductor for Bus Bar also. Please confirm. | Bidder understanding is in order. ACSR Panther conductor shall be used for 66 kV Bus as per BoQ. |
|  | Earth Grid System | SBD Part-2 , employers requirement page 786 | As per TS, Employer's requirement " EARTH GRID SYSTEM" mentioned as 75x8 mm MS flat. However in BOQ, it is mentioned as 32mm MS Rod for earthmat. We are proceeding with 32mm MS rod as per BOQ. Please confirm. | 32mm MS Rod shall be used for Earth mat as per BoQ. |
|  | Tubular Steel Pole: Swaged type | SBD Part-2 , employers requirement page 413 " Annexure-A" | As per SBD Part-2, employers requirement page 413 "Annexure-A", Tubular Steel Pole: Swaged type 9 Mtr long mentioned as 540 SP 28 type designation. However in BOQ 66/11Kv Substation Sl.no-285, It is mentioned as " 9M STP 410 SP33". Please confirm. | As per Clause 2.4.6 of Section-Project of Bidding documents: STP shall be of SP 410 grade as per IS 2713 Part-I. |
|  | 66KV Isolator | SBD Part-2 , employers requirement page 870 " | As per SBD Part-2 , employers requirement page 870 cl.no-9.2 b), Rated continuous current is 800A minimum. However in BOQ 66/11Kv Substation Sl.no-289, The rated current mentioned as 630A. Please confirm. | 66 kV isolator continuous current shall be 630 A as per BOQ |
|  | Control & Protection System For 66kv Sub-Station | SBD Part-2 , employers requirement page 888 " | As per SBD Part-2 , employers requirement page 888 cl.no-2.1, It is mentioned that " The Simplex panel shall be vertical and freestanding". However in BOQ 66/11Kv Substation Sl.no-287 & 288, the panel mentioned as Duplex Panel. Please confirm. | Refer Amendment no -1 |
|  | Control & Protection System For 66kv Sub-Station | BoQ Sl.no-288 | Control & Relay panel with all protections for 66kV Line (Bus Scheme As per SLD) Panel as Per TS. However SLD drawing for Bus scheme not available. Kindly confirm. | The bus scheme of 66 kV system shall be Single strung Busbar system. |
|  | 415 V AC Distribution Board | BoQ Sl.no-301 | As per BOQ , it is mentioned as " 415V AC Distribution Board (ACDB) as per Technical Specification". However there is no specific TS for the same in SBD Part-2. Please confirm. | Refer section – 6, Cl no 13.3 of SBD Part-2 Scope of Work for TS of ACDB and DCDB. |
|  | Requirement of pole for Augmentation work of DT 63 & 100KVA | SECTION PROJECT - Page 3 out of 45 | In BOQ, there is not mentioned of requirement of new pole for replacement of existing damaged pole for augmentation work of 63 & 100KVA DTR. According to TS or employers requirement same is not required. If the new pole is required for replacement of existing pole for the above work whether new pole shall be considered as line item. Kindly confirm. | Presently new pole is not envisaged for this work. If new pole is required for such work same shall be provided as per the applicable line item. |
|  | Augmentation of existing DT except 400 kVA & 630 kVA | Section Project | As per Section Project Cl.no- 2.2.5. " Augmentation of existing DT except 400 kVA & 630 kVA" , it is mentioned that DTs under augmentation shall be installed on existing DP. The same to be finalised based on the survey and if possible new DP shall be installed for Augmentation of existing DT. Please confirm. | Bidder understanding is in order. Presently new pole is not envisaged for this work. If new pole is required for such work same shall be provided as per the applicable line item. |
|  | Civil works | General observations | There is no specific TS available for Civil works under the package. Request to kindly provide the same. | Refer section -6, 13.9 of SBD Part-2 Scope of Work for TS of Civil Works. |
|  | 11kV HG Fuse | Technical Specification | 11kV HG Fuse TS not available. please provide the same | For technical specification of 11 kV HG fuse refer Clause 3.3 of Section -Project of Bidding documents which is reproduced below: In case specification of any equipment /material is not included in this volume, the same shall be supplied as per relevant standards. Latest REC specification & Construction Standards may also be referred to. |
|  | - | General observations | Overhead water tank size not specified. Please Confirm. | Refer section-6, cl no 13.9 of SBD Part-2 Scope of Work for TS of Civil Works. |
|  | - | BOQ | In LT AB cable, the BOQ has not street light wire, whereas in AB cable TS the same is given (Insulated Street light wire). Please clarify whether the insulated street light wire is required or not in AB cable. | Bidder understanding is in order. LT AB cable shall be used as per BoQ without street light wire provision. |