VOLUME- II

TECHNICAL SPECIFICATION

FOR

Supply of 220 KV XLPE cable along with termination module & accessories including laying and termination at POWERGRID 400/220 kV Raipur  substation

Table of Contents

1. General

2. SCOPE OF WORK

3. SPECIFIC EXCLUSIONS

4. PHYSICAL AND OTHER PARAMETERS OF THE SUBSTATION

5. SCHEDULE OF QUANTITIES

6. DRAWINGS

7. INTERPRETTING DIFFERENT SECTIONS OF TECHNICAL SPECIFICATIONS

8. MANDATORY SPARES

9. SPECIAL TOOLS AND TACKLES

10. SPECIFIC REQUIREMENT

# 1. GENERAL

1.1 Preamble:

Power Grid Corporation of India Ltd. (POWERGRID), A Govt. of India Enterprise is responsible for Bulk Power Transmission of electrical energy from various central  Govt. Power Projects to various utilities/ beneficiaries and interconnecting regional grids, operating and maintaining the National Electrical Grid of India. It is established with the mission of “We will become a Global Transmission Company with Dominant Leadership in Emerging Power Markets with World Class

Capabilities by:

- World Class: Setting superior standards in capital project management and operations for the industry and ourselves.

- Global: Leveraging capabilities to consistently generate maximum value for all stakeholders in India and in emerging and growing economies.

- Inspiring, nurturing and empowering the next generation of professionals.

- Achieving continuous improvements through innovation and state of the art technology.

- Committing to highest standards in health, safety, security and environment.”

1.2 POWERGRID is implementing the following transmission systems through RTM route

Augmentation of Transformation capacity by 400/220Kv, 1x500MVA (4th) ICT at Raipur (PG) S/s in Chhattisgarh.

# 400kV

- Switching Scheme: One and Half Breaker Scheme.

- Fault Level: 63 kA for 1 sec.

# 220kV

- Switching Scheme: Double Main and Transfer Scheme

- Fault Level: 50 kA for 1 sec.

The existing 400/220 kV Raipur substation is of AIS type.

- The proposed extension of 400 kV Bay and 220 kV bay is to be done through AIS

- However, 220 kV Interconnection of 400/220 kV ICT is envisaged through 220 kV Cable and includes supply & laying under present scope.

# 2. SCOPE OF WORK

The scope of this specification covers following:

Supply, Installation, Testing & Commissioning of 220kV EHV XLPE cable from 220KV side of the 400/220kV ICT 4 along with cable termination (2X04 Nos) at both ends for interconnection of ICT to proposed 220 KV ICT Bay.

- Supply: -

  - 220kV, Single Core (1C) EHV XLPE cable along with cable termination kit (4 Runs i.e R-Ph, Y-Ph, B-Ph and one cable as spare) shall be supplied and laid in buried cable trench from 220kV side of ICT#4 up to 220kV bay under present scope.

    - The conductor and size of cable shall be copper and 2500Sq.mm. respectively.

    - The Item “220KV HV POWER CABLE” of BPS includes all the bonding cable, earth continuity cables, Link boxes, Sheath Voltage Limiters (SVLs) etc. (but excluding jointing kit) as per requirement for entire cable route.

    - Cable joint as per BPS, shall be under the present scope and the Joint location shall be decided during detailed engineering, if required.

    - Tentative route of buried cable trench for 220kV cable is marked in the General Arrangement drawing.

    - Cable shall be laid in Flat formation. A general section drawing is attached herewith.

    - The BPS item “Laying of 220KV XLPE Power Cable as per technical specification” includes excavation, backfilling, cover etc & crossing of roads, cable trenches,  drains etc  and restoration of the same as far as possible.

    - All the drawings/ design i.r.o. cable laying i.e. section drawings for buried cable, road crossing etc. shall be under the scope of the bidder and bidder shall be required to submit the same for approval of the Employer during detailed engineering immediately after the award of contract duly meeting the requirements specified in the standard technical specification.

    - Distributed temperature monitoring system for above 220kV cable is not envisaged for present scope.

- Services: -

  - The scope of work for underground power cable laying typically includes trench excavation, cable installation, jointing, termination, and backfilling, as well as testing and commissioning of the cable system. It also encompasses activities like site preparation, material procurement, and ensuring proper safety measures throughout the process.

Detailed Scope of Work:

- Site Preparation:

- Survey and Mapping: Determining the cable route, ensuring it avoids existing utilities, and marking the trench location.

- Excavation: Digging trenches to the specified depth and width, using appropriate methods like open-cut or horizontal directional drilling (HDD).

- Barricading and Protection: Protecting the excavated areas and ensuring the safety of workers.

- Cable Installation:

- Cable Laying: Carefully laying the cable in the trench, using rollers to minimize strain, and ensuring proper bending radii at changes in direction. Laying of 220 kV grade XLPE cables through buried cable trench inside the Sub-Station premises under scope as per specification/ drawings approved by the Employer.

- Cable Jointing: Connecting the cable ends using approved methods and materials to ensure a reliable and secure connection.

- Cable Termination: Securing the cable ends at the starting and ending points (e.g., transformer, switchgear) to ensure proper electrical connections.

- Backfilling and Restoration:

- Backfilling: Carefully filling the trench with suitable materials, compacting them to ensure proper compaction, and levelling the surface.

- Protection: Installing warning tape or tiles to indicate the cable route and prevent accidental damage. All other accessories and items like supply and installation of warning tape, providing layer of Bricks  as per drawing enroute (if required), construction of jointing bays & restoration as per specification shall be under the scope.

- Testing and Commissioning:

- Cable Testing: Performing necessary tests to verify the cable's integrity and proper functioning.

- System Commissioning: Ensuring the cable system is properly connected to the electrical grid and ready for operation.

- Documentation:

- As-Built Drawings: Creating detailed records of the cable route and installation details.

- Testing Records: Maintaining records of all cable testing and commissioning results.

- Safety and Quality Control:

- Safety Measures: Implementing safety protocols to protect workers and the public, including the use of personal protective equipment (PPE).

- Quality Control: Inspecting the work at various stages to ensure it meets the required standards and specifications.

- General requirements of work:

  - Cable marker “220kV EHV Cable” as per statutory requirements shall be provided all along the route at an interval of 50 meters.

  - Supply and installation of straight through joints for complete route.

  - Supply and installation of all critical installation materials like trefoil clamps, neoprene cushions, support brackets etc. as required for complete route to avoid damage of the cable. Neoprene cushions shall be provided at road crossings to avoid damage of cable due to vibrations during movement of vehicles.

  - Bonding of screen/sheath to the earth station through disconnecting type link boxes and SVL (sheath voltage limiter). Bidder shall adopt cross bonding for route under scope. Earthing stations /Earthing pits, earthing materials and earthing conductors wherever applicable for complete route including cable termination and earth link box at ends of cable shall be in contractors’ scope.

  - The mounting of outdoor termination kit including end termination shall be in the scope of the contractor. Termination of spare cable shall be made such that it can be used for any phase in case of fault or maintenance of any of the three phase cables.

  - Testing & Commissioning as per IS: 62067 after installation of cable section shall be under scope of contractor. There is no requirement of do test using AC voltages i.e AC voltage test of insulation and Partial Discharge test” as mentioned in IS:62067.

  - Cable Route, Buried Cable Trench etc. tentative drawings are attached. On award of work, agency shall submit the final route after site visit jointly with the site representative of the Employer and shall submit to the Employer final route, buried cable trench, crossing, etc. drawings for approval.

| Design guidelines and parameter for cable laying |  |
| --- | --- |
| Design Parameter | Details |
| Method of laying | Direct laying of cable in ground is to be done. This method involves digging a trench in ground and laying cables on a bedding of minimum 100mm sand at the bottom of the trench and covering it with additional sand of minimum 100mm and protecting it by means of bricks. ( as per drawing). The desired minimum clearances are as -Power to Power cable-0.45m ( drawing attached for reference purpose). The desired minimum depth of laying from ground surface to the top of cable shall be : 220kV grade XLPE Cables: 1.2M Spacing shall be maintained uniformly between the cables all along the length including the bends. To maintain the spacing, suitable non-metallic spacer shall be placed uniformly . No separate payment shall be done for the spacer. Laying of the cables and handling of the same shall be undertaken, at all times, by adequate staff suitably trained and supplied with all the necessary plant, equipment and tools. |
| Handling and storage of the cable drum | The cable drum shall be transported upright, so that the weight is distributed on both the flanges. Under no circumstances the cable drum may be laid on its side. During transportation the drum must be properly secured. The cable drum should never be dropped from Lorry or a trailer, so as to prevent damage to cable drum and also to the cable. Ramp may be used for unloading. The drum may be rolled over short distance, provided the correct direction of rolling as provided on the drum is observed. Alternatively, a mobile crane should be used for lifting and lowering the drum. A chain-pulley arrangement may also to be used to lift the drum and deposit the same on ground if required. In case the drum are to be stored prior to cable laying, they should be arranged in such a way to leave some space between them for air circulation. It is desirable that the drums stand on battens placed directly under the flanges. Overhead covering is not essential except during monsoon. Cable should however be protected from direct rays of sun by leaving the battens on or by providing some form of sunshade. In no case the drums shall be stored in flat position with flanges horizontal. For transportation of the cable drums from storage site to work site, the drum should be mounted on a trailer or a open lorry and unloaded by mobile cranes. |
|  | After cable laying, empty cable drums shall be taken return back by vendor from site at their own risk and cost. |
| Cable laying | The ground over which the drum is positioned at site should be properly consolidated and jacks placed on both sizes of the drum to make the pay-off arrangement stable. Suitable arrangement be made to stop the drum rotation, during cable laying preferably by square wooden poles kept temporarily pivoted over cable roller under the flanges which when required can be applied on the flange as a brake by personnel manning the drum. The cable should always be paved off from the top of the drum. The drum must be positioned in such a way that the arrow on that drum points opposite to the direction of rotation marked on the drum. It must be ensured that the cable is not dragged over sharp object or on the road surface, so as to avoid damage to the outer sheath of the cable. Cable supplier's recommended maximum pulling tension shall not be exceeded. Rollers shall be placed at intervals and the cable shall be pulled over the rollers. The rollers shall be kept lubricated so that they rotate freely, minimize friction to the cable in motion. Rollers shall be positioned at the bends to minimize side wall frictions. The cable should not be pulled out from the drum by lifting of the coil while the drum is lying flat on the flange. This leads to twisting of the armour and cores resulting in permanent damage to the cable. To avoid ingress of moisture, it must be observed that the end capping of the cables is not damaged. Cut pieces of the cables must be capped immediately, before laying of the same is taken up. |
| Excavated Material | The excavated earth shall be so stored at site, that it shall not cause any hurdle. |

3. SPECIFIC EXCLUSIONS

The following items of work are specifically excluded from the scope of the specification:

- Supply of Cable termination Support Structure

- Foundation of Cable termination Support Structure

# 4. PHYSICAL AND OTHER PARAMETERS OF THE SUBSTATION

| i) | Name of Substation | 400/220KV Raipur S/s Kumhari |
| --- | --- | --- |
| ii) | Name of state | Chhattisgarh |
| iii) | Nearest Railway Station | Raipur Railway station |
| iv) | Co-ordinates | 21.24619262222047 N, 81.49048233271672 E |
| v) | Altitude | Less than 1000 meter above mean sea level (MSL) |
| vi) | Seismic zone | II as per IS 1893 |
| vii) | Wind Zone | II |
| viii) | Min./Max. Ambient Temperature | 0-50 deg celsius |

4.1 Fault Level shall be considered as mentioned below: -

| S.No | Name Substation | of | 400KV | 220KV |
| --- | --- | --- | --- | --- |
| 1 | 400/220KV Raipur S/s |  | 63kA | 50kA |

4.2 System Parameter

The brief particulars of 220 kV system parameters are given here under:

| i) | Nominal system voltage | 220KV rms |
| --- | --- | --- |
| ii) | Highest system voltage | 245Kv rms |
| iii) | Impulse withstand voltage 1.2/50 Microseconds wave of positive/ Negative polarity | 1050 kV peak |
| iv) | System rated Frequency | 50Hz |
| v) | No. of phase per circuit | 03 |
| vi) | Total nos. of circuit | One as per BPS |
| vii) | System Earthing | Effectively Grounded |
| viii) | Rated short time current | 50KA, for 1 second |
| ix) | One minute Power frequency withstand voltage | 460KV rms |
| x) | The cable should carry earth fault current of 50kA for 1 second. | (Symmetrical & asymmetrical faults both) |

# 5. SCHEDULE OF QUANTITIES

The requirement of various items/works are indicated in the Bid price Schedules. All  equipment’s/items for which BOQ has been indicated in BPS shall be payable on unit  rate basis. During actual execution, any variation in such quantities shall be paid based  on unit rate under each item incorporated in the Letter of award.

Wherever the quantities of items/works are indicated in lot/set, the bidder is required  to estimate the quantity required for entire execution and completion of works and incorporate their price in respective Bid price schedules. Any material/works not specifically mentioned in the description in BPS, but essential for successful commissioning of the specified scope shall be deemed to be included in the bid price and shall be provided at no extra cost to Employer.

In case of cable (i.e. Power cables & fiber optics cable), the actual quantity erected shall be considered for payment purpose. All wastages during installation, jointing, termination etc. shall be to Contractor’s account.

# 6. DRAWINGS

The successful bidder shall require developing the drawings based on proposed scheme of cable laying as discussed at Para-2.1 above. The enclosed tender drawings give the basic scheme, layout etc. In case of any discrepancy between the drawings and text of specification, the requirements of text shall prevail in general. However, the Bidder is advised to get these clarified from the Employer in case of any doubt. On completion of work, the bidder shall be required to submit 02 (Two) sets of final/ as built drawings to the Employer in soft copies.

# 7. INTERPRETTING 	DIFFERENT 	SECTIONS 	OF 	TECHNICAL SPECIFICATIONS

Employer has standardized its technical specification for various equipment and works  for different voltage levels. Items which are not applicable for the scope of this package  as per the schedule of quantities described in BPS, the technical specification for those  items shall not be referred.

For the purpose of present scope of work, technical specification (Vol II) shall consist  of following sections and they should be read in conjunction with each other.

- Section-Project, Rev. 00

- Section-General Technical Requirement (GTR), Rev. 15, Dec 2020 (Pages-134)  3. Section- Technical Specification EHV XLPE Power Cable, Rev. 01 (Pages-23)

4. Section-Civil Works (Pages-91).

In case of any discrepancy between Section-PROJECT and other technical specifications documents regarding scope of works, Section-PROJECT shall prevail over all other sections.

In case of any discrepancy between Section-GTR and individual sections for various equipment, the requirement of individual equipment section shall prevail.

In case of any discrepancy between the Main body of Section-Project and Annexure(s)  of Section-Project, provisions specified in Main body of Section-Project shall prevail.

# 8. SPECIAL TOOLS AND TACKLES

The bidder shall include in his proposal the deployment of all special tools and tackles required for erection, testing, commissioning and maintenance of equipment. The special tools and tackles shall only cover items which are specifically required for the equipment offered and are proprietary in nature. However, a list of all such devices should be indicated in the relevant schedule provided in the BPS. In addition to this the Contractor shall also furnish a list of special tools and tackles for the various equipment in a manner to be referred by the Employer during the operation of these equipment. The scope of special tools and tackles are to be decided during detail engineering and the list of special tools and tackles, if any shall be finalized.

# 9. SPECIFIC REQUIREMENT

The bidder shall be responsible for safety of human and equipment during the working. It will be the responsibility of the Contractor to co-ordinate and obtain Electrical Inspector's clearance before commissioning. Any additional items, modification due to observation of such statutory authorities shall be provided by the  Contractor at no extra cost to the Employer.

All necessary termination equipment for cable shall be in the scope of the bidder.

Electricity at one point will be provided by POWERGRID on chargeable basis.

In the Technical Specifications documents, the term “Purchaser” and/or “Owner” may  also be read as “Employer”.

# List of Tender Drawings: -

| S.No | Drawing No. | Description |
| --- | --- | --- |
| 1. | C/ENGG-SS/WR-1/ RAIPUR /EXTN/TR-202584/GA | General arrangement Drawing |
| 2. | C/ENGG-SS/WR-1/ RAIPUR /EXTN/TR-202584/SLD | Single Line Diagram |
| 3. | Buried cable trench Section | Buried Cable Trench Section |

| Codes & Standards |  |  |
| --- | --- | --- |
| Sr.no. | Reference no | Name of standard |
| 1 | IS 1255 | Code of practice of installation and maintenance of power cable up to and including 33KV rating |
| 2 | IS 7098 Part III | Crosslinked Polyethylene insulated PVC sheathed cables for working voltages from 66KV up to and including 220KV. |
| 3 | IEC 62067 | Power cable with extruded insulation and their accessories for rated voltages above 150kV and up to 500kV test methods and requirement. |