Annexure-1

Scope of Work for Transportation of 500 MVA, 400/220/33 kV, 3-Phase, spare ICT from Lucknow 400/220 kV Substation to Prayagraj Substation

The scope of work includes the following:

- Spare 400/220/33 kV, 500 MVA 3-Phase Transformer is erected with all bushings, conservator tank and Oil filled which need to be dismantle before loading. Radiator bank is in dismantled/ not erected state.

- The scope of work includes dismantling of 400/220/33 kV, 500 MVA Transformer including HV, IV, LV & Neutral bushings, turret, conservator tank etc. The contractor shall fix all necessary dummy plates and fill the dry air (up to -55 degree dew point) up to 0.2-0.5psi.

- The scope of work includes the transportation of Main Tank, Oil, bushings, conservator, Radiators, supporting structure, pipes, marshaling box and other accessories attached with main tank.

- The Transport dimension of main tank is 11550 mm x 5000 mm x 4600 mm . Transport mass of ICT (without Oil & With Dry Air) 260000 KGS. (OGA drawing is attached for reference)

- Total insulating oil for the Spare ICT at Lucknow 400/200 kV Substation is 114 kL  which need to be evacuated from Main Tank for transportation in Oil drums or Tanker (either of which to be arranged by Contractor) at site before transportation.

- Packing:

- Original Packings of Bushings are not available at site and vendor has to pack bushings properly before transportation.

- The other Transformer auxiliaries such as Radiator, cooling fans, pipes and other accessories removed from the Transformer are to be properly packed in wooded packing/steel frames or by other suitable means prior to the transportation.

- The packing of all items to be transported shall be as per the norms of POWERGRID.

- Loading of ICT and its accessories at POWERGRID Lucknow 400/220 kV Substation and unloading of ICT at Plinth and unloading of other accessories at Prayagraj Substation to be ensured by the contractor.

- Contractor shall arrange suitable material handling and transport equipment as may be necessary including labor, packing materials, cranes, trucks, trailers etc. and the T&P required for above works. The main tank shall be filled with dry air by POWERGRID before transportation however dry air cylinders which are available at site need to be top up before and during transportation to maintain the required pressure (shall be in the scope of party). The impact recorder (if required) shall be arranged by POWERGRID.

- Contractor shall make all arrangement of adequate size and capacity of cranes etc. for loading and unloading of materials and will ensure that overloading in vehicles in not done.

- All the clearances required from various authorities for transportation of transformer shall be in the scope of contractor.

- The contractor shall carry out the route survey along with the transporter and finalize the detail methodology for transportation of autotransformer and based on route survey; any modification/ extension/ improvement to existing road, bridges, culverts etc. if required, shall be in the scope of the contractor.

- If any damages to drainage, culverts etc. occurred due to dragging of ICT at source station or destination, the same shall be repaired by the contractor.

- The contractor shall be fully responsible and liable for payment of all demurrages of any kind whatsoever or other extra charges levied by the road authorities, by state Govt. municipal authority and any other agency for delay in clearances handling and forwarding of materials.

- All the toll taxes, entry taxes and any other levies shall be paid by the contractor.

- All the equipment and materials to be transported shall be kept insured by the contractor against any loss, damage, accident, pilferage, theft, fire etc. from the point of commencement of loading up to the time of taking over by the owner POWERGRID. The premium charges for above need to be quoted in BOQ. Approx value of ICT with oil and accessories: 14.96 Crore.

- The Contractor shall take the policy in the joint names of Employer and the Contractor. The policy shall indicate the Employer as the beneficiary. However, if the Contractor is having an open policy for its line of business, it should obtain an endorsement of the open cover policy from the insurance company indicating that the dispatches against this Contract are duly covered under its open policy and include the name of the Employer as jointly Insured in the endorsements to the open policy.

- The Contractor shall arrange necessary surveys and loading/settling of insurance claims for consignments landed in damaged conditions. Necessary surveys for the damaged materials/packing before repacking and dispatch.

- Proper coordination for smooth transportation and dispatch of materials is essential.

- Proper verification, checking and segregation of materials/packages before taking delivery from station and the time of dispatch shall be made by the contractor.

- Contractor shall mark the consignments with “indelible paints” clearly indicating the consignee’s address as per the dispatch instructions of the owner.

- Contractor shall be fully responsible for the safe handling of materials and shall indemnify and absolve owner of any consequences thereof by way of damage/loss of cargo, accidents, damages to vehicles and handling equipment either owned or hired by the contractor, public property as well as injuries or otherwise to the personnel under the contractor’s command or the public.

- Contractor shall properly maintain all registers and records in the prescribed manner as required by the regulations of the various authorities concerned and shall indemnify the consignee and the owner from any consequences due to any inaccurate and faulty documentation on contractor part.

- All the statutory requirement such as electrical license, Workman compensation policy, Erection all risk policy, Transit/Marine Cargo insurance (as applicable) etc. shall be in the scope of contractor/Bidder.

- POWERGRID shall arrange and provide necessary documents which are needed during transportation such as Gate pass, E-way bill, delivery chalan, GST invoices etc.

- The other related works which are not specifically mentioned above and required for completion of the works shall be in the scope of contractor.

- Contractor shall take proper supervision of entire operation till final dispatch/receipt of materials.

- Oil filtration plant, Dry air plant and temporary electrical connection shall be arranged by POWERGRID, free of cost.

- Deputation of OEM Representative for supervision of Dismantling work at Lucknow and Erection work at Prayagraj (if felt necessary by POWERGRID) shall be under scope of POWERGRID.

- Erection of ICT at Prayagraj S/s: The erection of ICT at Prayagraj S/s is also in the scope of vendor. The main activities to be carried out for erection shall be as below:

- Removal of impact recorder under the supervision of OEM representative, followed by erection of accessories including HV, IV, LV & Neutral bushings, Conservator, Tank to conservator pipes, Buchholz &  PNRV Relay, equalizer pipes, PRV, Turret, Radiator along with support structures and other accessories etc.

- Erection of the ICT BPI, 400 KV Connection with Jumper/Aluminum with Bushings & LA and Neutral Jumper/Aluminum Tube is in the scope of contactor.

- The scope of work also includes commissioning of the ICT as per POWERGRID norms such as activities related to dry-out with Vacuum Cycles, leakage identification and arresting, processing and filling of insulating oil in main tank and carrying out the Hot Oil Circulation (HOC) of the insulating oil inside Main Tank. Total quantity of Insulating oil is 114 KL in main tank.

- T&P such as dew point meter, online ppm kit, McLeod Guage, appropriate sling for lifting of bushing etc. shall be in the scope of contractor.

- Testing of the processed oil before filling & after HOC shall be in the scope of POWERGRID.

- Erection of all the auxiliary items such as IMB, ODS, FOTS, DGA etc. is in the scope of contactor. Cable termination at IMB, CMB, mechanical protection devices etc. will be in the scope of M/s POWERGRID.

- Contractor shall arrange suitable material for handling of equipment as may be necessary including labor, cranes, hydra etc. and the T&P required for above works.

- Contractor shall make all arrangement of adequate size and capacity of cranes/ hydra etc. for erection of the bushings and accessories such as conservator, radiator etc.

- Oil filtration plant, Dry air plant and temporary electrical connection shall be arranged by POWERGRID.

- Electrical Testing of the ICT (after the final settling of the Main tank post HOC) along with the Kits required for the same shall be in the scope of POWERGRID.