| Sl. No. | Clause/ Drg. No. | Existing provision | Amended provision |
| --- | --- | --- | --- |
| 1 | Clause No. 9.6 of Section-Project, Rev. 00 | New Clause added | Clause No. 9.6: Clause 2.1 (a) of Section GTR, Rev-15 is amended as below: "All equipment/materials/items, as per Annexure-K (Rev 01), as applicable under present scope of works, shall be procured and supplied from domestic manufacturers only with Minimum Local Content for individual items as listed in the above annexure. Any imported equipment/material/item/parts/component (comprising of embedded systems) to be supplied under the contract shall be tested in the certified laboratories to check for any kind of embedded malware/trojans/cyber threats and for adherence to Indian Standards as per the directions issued by Ministry of Power/Govt. of India from time to time. In case of such import from specified “prior reference” countries, the requirement of prior permission from the Govt. of India including protocol for testing in certified and designated laboratories by Ministry of Power/Govt. of India shall also be complied with by the contractor. The bidder/contractor shall list out the products and components producing Toxic e-waste under the contract and shall furnish to the Employer the procedure of safe disposal at the time of closing of the contract." |
| 02 | Clause No. 9.1 of Section-Project, Rev. 00 | Clause No. 9.1 Bushing of 420kV, 245kV and 52kV voltage level shall be Oil filled condenser type with composite polymer insulator (housing) or RIP (Resin Impregnated paper) condenser type with composite polymer insulator (housing) or RIS (Resin Impregnated Synthetic) condenser type with composite polymer insulator (housing). | Clause No. 9.1 VOID. |
| 03 | Clause No. 9.7 of Section-Project, Rev. 00 | New Clause added. | Clause No. 9.7: Clause No. 6.5.1 of Technical Specification, Section – Transformer (Upto 400kV Class), Rev. 13, is amended as below: Main conservator shall have air cell type constant oil pressure system to prevent oxidation and contamination of oil due to contact with moisture. Conservator Protection Relay (CPR)/Air cell puncture detection relay shall be installed to give alarm in the event of lowering of oil in the conservator due to puncture of air cell in service. Conservator shall be fitted with magnetic oil level gauge (Plug & socket type arrangement) with potential free high and low oil level alarm contacts and prismatic oil level gauge and Conservator Protection Relay. Plug & socket type arrangement with factory fitted cable of adequate length shall be supplied by OEM. Connection of plug and socket with cable at site is not acceptable. |
| 04 | Annexure-H of Section – Transformer (Upto 400kV Class), Rev. 13 of Technical Specification | Annexure-H 1.1 KV GRADE POWER & CONTROL CABLES … … STANDARD TECHNICAL DATA SHEET (1.1kV GRADE XLPE POWER CABLES) … … STANDARD TECHNICAL DATA SHEET (1.1kV GRADE PVC POWER CABLES) … … STANDARD TECHNICAL DATA SHEET (1.1kV GRADE PVC CONTROL CABLES) … … | Annexure-H 1.1 KV GRADE POWER & CONTROL CABLES … … STANDARD TECHNICAL DATA SHEET (1.1kV GRADE XLPE POWER CABLES) – VOID (Parameters of Standard Technical Data Sheet shall not be referred to) STANDARD TECHNICAL DATA SHEET (1.1kV GRADE PVC POWER CABLES) – VOID (Parameters of Standard Technical Data Sheet shall not be referred to) STANDARD TECHNICAL DATA SHEET (1.1kV GRADE PVC CONTROL CABLES) – VOID (Parameters of Standard Technical Data Sheet shall not be referred to) |