| Sl. no | Clause no w.r.t specification | Description as given in specification | Comments/ Clarifications | POWERGRID’s Reply |
| --- | --- | --- | --- | --- |
| 01 | Section-Project TR36 Clause No: 2.2.1 c) Page No – 3 Clause No:9.1 Page No – 7 | (400/220/33kV, 3-ph Autotransformer shall be suitable for connecting both HV side (400kV) & IV side (220kV), with GIS SF6/Oil Interface, as per IEC-62271-211. Bushing of 420kV, 245kV and 52kV voltage level shall be Oil filled condenser type with composite polymer insulator (housing) or RIP (Resin Impregnated paper) condenser type with composite polymer insulator (housing) or RIS (Resin Impregnated Synthetic) condenser type with composite polymer insulator (housing). | - Please confirm that whether HV & IV bushing of Transformer shall be of OIL to SF6 or RIP type/OIP/RISbushings. Kindly confirm - Please furnish technical requirements/ specification for OIL to SF6 bushing. - Please clarify the conflict between clause 2.2.1 & 9.1, i.e. as Oil to SF6 bushing shall be RIP type but without polymer insulator. - Please confirm that Bushing and transformer insulation level shall remain same. - Please confirm that Testing of Transformer shall be allowed with oil-air bushing due to testing/ layout limitation. | - HV & IV bushings of Transformer shall be suitable for Oil to SF6 termination only. - Bushing shall be in-line with IEC 60137-2017 & Technical specification. - Please refer clarification at sl.no.1 above and Clause No - 1 of Amendment No-1. - Bidding document is quite clear. Bidders to comply the requirement of Technical specification. - Acceptable. However, all required arrangements shall be in the scope of bidder. |