| POWER GRID CORPORATION OF INDIA LTD. (A Government of India Enterprise) |  |  |
| --- | --- | --- |
| TECHNICAL SPECIFICATION FOR Tower package tw-01 Diversion works of POWERGRID 400kV D/C 400kV DC Vadodara-Pirana TL & 400kV DC Pirana-Ranchhodpura & Pirana-Nicol TL |  |  |
|  | VOLUME-II |  |
| (This document is meant for the exclusive purpose of bidding against this specification and shall not be transferred, reproduced or otherwise used for purposes other than that for which it is specifically issued). |  |  |

TECHNICAL SPECIFICATION

(VOLUME-II)

CONTENTS

| SECTION-I A | SCOPE |
| --- | --- |
| SECTION-I B | GENERAL INFORMATION |
| SECTION-II | GENERAL TECHNICAL CONDITIONS |
| SECTION-III | SURVEY AND SOIL INVESTIGATION |
| SECTION-IV A | TOWER DESIGN |
| SECTION-IV B | TOWER TESTING |
| SECTION-IV C | FABRICATION, ERECTION AND STRINGING |
| SECTION-IV D | FOUNDATION (CONTRACTOR DESIGN) |
| SECTION-IV E | FOUNDATION (EMPLOYER DESIGN) |
| SECTION-IV F | MONOPOLE STRUCTURE, FOUNDATION AND ERECTION |
| SECTION-V | GALVANISED STEEL EARTHWIRE |
| SECTION-VI A | HARDWARE FITTINGS & ACCESSORIES |
| SECTION-VI B | CLAMP FITTINGS AND ACCESSORIES FOR HTLS CONDUCTOR |
| SECTION-VII A | CONDUCTOR |
| SECTION-VII B | HTLS CONDUCTOR |
| SECTION-VIII | COMPOSITE LONGROD INSULATOR |
| SECTION-IX A | PILE FOUNDATION |
| SECTION-IX B | STONE COLUMN |
| SECTION-X | OPGW |
| SECTION-XI | DRAWINGS |
| SECTION-XII | FAQ |
| SECTION-XIII | TOWER SCHEDULE OF EXISTING LINE (only applicable for Re-conductoring packages) |

SECTION-I A

SCOPE

TECHNICAL SPECIFICATIONS

SECTION-I A

# SCOPE

# Revision History

| # Revision No. | # Date | # Clause Ref | # Description |
| --- | --- | --- | --- |
| # Rev-0 | # June’2021 |  | # First Release |
| # Rev-1 | # Sept’2021 |  | # First Revision |
| # Rev-2 | # Oct’2021 |  | # Second Revision |
| # Rev-3 | # Jan’2022 |  | # Third Revision |
| # Rev-4 | # Apr’2022 |  | # Fourth Revision |
| # Rev-5 | # July’2022 |  | # Fifth Revision |
| # Rev-6 | # Feb’2023 |  | # Sixth Revision |
| # Rev-7 | # Sept’2023 | # 2.1.1.1 | # Seventh Revision |
| # Rev-8 | # Dec’2023 | # 3.4 (v) | # Eighth Revision |
| # Rev-9 | # March’2024 |  | # Ninth Revision |

TECHNICAL SPECIFICATIONS

SECTION-I A

# SCOPE

CONTENTS

| Clause No. | Description | Page No. |
| --- | --- | --- |
| 1.0 | Scope | 1 |
| 2.0 | Transmission towers & line data | 5 |
| 3.0 | Different Sections to Technical Specification | 7 |
| 4.0 | Service Condition | 8 |

# TECHNICAL SPECIFICATIONS

# SECTION- I A

SCOPE

  - Scope

  - The following transmission lines are included in the scope of the Contractor under various packages:

Tower Package – TW01

Diversion works of POWERGRID 400kV DC Vadodara-Pirana TL & 400kV DC Pirana-Ranchhodpura & Pirana-Nicol TL due to construction of new Railway line from Barajedi to Sanand District by Western Railway, Ahmedabad.

  - This Specification covers the following scope of works:

          - Detailed survey including route alignment, profiling, tower/ *pole structure spotting, optimization of tower/*pole structure locations, soil resistivity measurement & geotechnical investigation (including special foundation locations viz. pile/well foundation locations, whenever applicable & covered under BPS);

          - Check survey.

          - *Fabrication,supply and erection of assorted tower members for transmission line Towers as per Employer’s design/drawings including River crossing towers (wherever applicable) including fasteners, step bolts, hangers, D-shackles etc.; (applicable only for Re-conductoring packages)

          - De-stringing the existing conductor and EW/OPGW (wherever applicable) including inspection of insulator strings, hardware fittings, dismantling and replacement of the same (if required), dismantling of accessories for conductor, dismantling of existing insulators (if required) etc. (applicable only for Re-conductoring packages)

          - Design and Proto type testing of transmission line towers

          - Design and Proto type testing of pole structures

          - Fabrication and supply of all type of transmission line Towers as per Employer’s design/drawings including River crossing towers (wherever applicable) including fasteners, step bolts, hangers, D-shackles etc.;

          - Fabrication and supply of transmission line monopole structures alongwith cross arms, earth wire peaks, base plates and anchor bolts for foundations, as per Employer’s design/ drawings including required fasteners i.e. bolts, nuts, spring washers, etc., and other accessories including step bolts/ hooks/ ladder, hangers, D-shackles/ fixtures etc. as may be required for monopole structure

          - Supply of all types of tower accessories like phase plate, circuit plate (where ever applicable), number plate, pole plate (where ever applicable), danger plate, anti-climbing device, Bird guard, (where ever applicable);

          - Supply of

- Earth wire

- Hardware Fittings and accessories for Conductor/*Earth wire

- Conductor

- Insulators

- OPGW & associated fittings & accessories.

          - Classification of foundations for different type of towers and Casting of Foundations for tower/ *pole structure footings as per Employer’s foundation design/ drawing;

          - Supply & Installation of Tower/ *Pole structure Earthing.

          - Supply & installation of Insulated Conductor sleeve, (if required & covered under BPS);

          - Supply & installation of Bird Diverter, (if required & covered under BPS);

          - Erection of towers/ *pole structures by using crane (wherever feasible), tack welding of bolts and nuts including supply and application of zinc rich paint, fixing of insulator strings, stringing of conductors and earth wires/OPGW* along with all necessary line accessories. For transmission lines, to promote mechanization and safe working conditions, use of crane is being promoted.  However, where usage of crane is not possible, erection of towers has to be carried out by conventional method i.e using Gin pole, Derrick, Centre mast etc. through usage of Power Operated Winch Machines. No tractor shall be allowed for tower/ *pole structure erection.;

          - Installation of Insulator strings complete with Arcing Horns & Necessary Hardware, Installing & Stringing of conductor including fixing of Conductor Accessories, Installing & Stringing of Earthwire including fixing of Earthwire Accessories for the line

          - Destringing & dismantling of existing 765/400/220/132/66kV Transmission line. (whenever applicable & covered under BPS)

          - Stringing of Power line crossing section under Live Line Condition (where ever applicable & covered under BPS);

          - Painting of towers/ *pole structures & supply and erection of span markers, obstruction lights (wherever applicable) for aviation requirements (as required)

          - Testing and commissioning of the erected transmission lines and

          - Other items not specifically mentioned in this Specification and/or BPS but are required for the successful commissioning of the transmission line, unless specifically excluded in the Specification.

          - The installation/stringing of OPGW cable along with associated fittings & accessories shall be carried out by the contractor. The scope of installation/stringing shall include splicing, termination, testing, demonstration for acceptance & commissioning as well as documentation. Splicing is preferred to be carried out at Tension towers locations. However, it shall be permitted at Suspension Tower locations also as required due to site conditions. The installation/stringing and splicing shall be carried out as per owner guidelines (provided as part of TS). The FODP & Approach cable shall also be installed by the Contractor (where ever applicable as per BPS).

          - The casting of special pile/well foundations/Caisson Monopole foundation, wherever required, shall be in the scope of the Bidder. The design shall be provided by POWERGRID. If the bidder does not have necessary experience and is not meeting the qualifying requirements specified herein, some other agencies meeting the qualifying requirements may be engaged by the bidder for the casting of pile/well foundations.

or

In case of special type pile or well foundations or Caisson Monopole foundation, some other contractor may be engaged by the Employer for casting of foundations. However, the Bidder shall be responsible for all the necessary co-ordination with the special foundation Contractor including stub-setting/fixing of base plate with anchor bolt.

  - Destringing/ Dismantling

    - The scope of works includes destringing of conductor, earthwire & OPGW, removal of hardware fittings, insulators, conductor, earthwire & OPGW accessories, etc. and dismantling of tower from some sections of existing 400kV/ 765 kV/ +/-500kV HVDC/ +/-800kV HVDC line and transporting of dismantled materials to designated POWERGRID stores. The Employer shall arrange shut down of charged sections of existing transmission lines, if required, before carrying out destringing & dismantling works as per program finalized in co-ordination with site. Appropriate safety measures along with necessary safety tools and equipments to carry out destringing and stringing operations under the above conditions including mechanical/ structural safety of the towers shall be the responsibility of the contractor. The entire quantity of dismantled line materials viz. tower parts, conductor, earthwire, OPGW, hardware fittings, insulators and conductor, earthwire & OPGW accessories removed from the existing line shall be transported to the designated POWERGRID stores by the contractor at his own cost. The Bidder shall submit his offer taking into consideration transportation cost of the dismantled material.

    - The contractor shall inspect the affected stretch of transmission lines and shall accordingly devise appropriate methodology/procedure of carrying out the destringing/restringing works during detailed engineering & execution stage in consultation with the site-in-charge.

  - Details of Transmission Line Routes and Terrain

The detailed survey shall be carried out using Total stations along the approved route alignment. As an alternative, the contractor may also use ALTM (Airborne Laser Terrain Modeling) techniques of equal or better accuracy for the detailed survey.

Quantity of detailed survey including route alignment, profiling, tower/ *pole structure spotting, optimization of tower/ *pole structure locations, soil resistivity measurement & geotechnical investigation etc. of lines have been indicated in the BPS.

    - Bidders may visit the line route to acquaint themselves with terrain conditions and associated details of the proposed transmission lines. For this purpose they are requested to contact the following address:

POWER GRID CORPORATION OF INDIA LTD.

400/220kV POWERGRID Dehgam Substation,

Vasna- Rathod Road, Near

Ganeshpura Village, Dehgam,

District- Gandhinagar

Gujarat.

Pin- 382305.

  - Location Details and Terminal Points

    - Diversion and shifting of following transmission line:

- 400kV D/C Vadodara- Pirana TL (LOC 846-849) (Quad ACSR MOOSE WZ-III)

- 400kV D/C Pirana- Ranchhodpura & Pirana- Nicol TL (LOC 11-20) (Twin ACSR MOOSE WZ-III)

These transmission lines pass through Plain area and in state of Gujarat.

Vadodara- Pirana TL

| Existing Line |  |  |  |  | Proposed Line |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| S.No | Tower | Type of Tower | Deviation Angle | Span | S.No | Tower | Type of Tower | Deviation Angle | Span |
| 1 | EX T- No.846 | DA+3 |  |  | 1 | EX T- No.846 | DA+3 |  |  |
|  |  |  |  | 400 |  |  |  |  | 293 |
| 2 | EX T- No.847 | DC+0 | 23° 56' 00'' LT |  | 2 | AP-1/0 | DD+3 | 48°34'28" LT |  |
|  |  |  |  | 250 |  |  |  |  | 245 |
| 3 | EX T- No.848 | DA+0 |  |  | 3 | AP-2/0 | DD+6 | 57°52'38" RT |  |
|  |  |  |  | 370 |  |  |  |  | 259 |
| 4 | EX T- No.361 | DA+0 |  |  | 4 | AP-3/0 | DD+0. | 33°03'49" LT |  |
|  |  |  | Total Route KM | 1.02 |  |  |  |  | 266 |
|  |  |  |  |  | 5 | EX T- No.849 | DA+0 |  |  |
|  |  |  |  |  |  |  |  | Total Route Km | 1.063 |

Pirana- Ranchhodpura & Pirana- Nicol TL

| Existing Tower Schedule |  |  |  |  | Proposed Tower Schedule |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| SL. No. | Location No. | Tower Type | Angle of Deviation | Span Length (m) | SL. No. | Location No. | Tower Type | Angle of Deviation | Span Length (m) |
| 1 | EXIST TW-11 | DD+6 | 00°00'00" |  | 1 | EXIST TW-11 | DD+6 | 00°00'00" |  |  |
|  |  |  |  | 325 |  |  |  |  | 254 |  |
| 2 | EXIST TW-12 | DA+0 |  |  | 2 | PROP TW-12 | DD+3 | 25°36'21" LT |  |  |
|  |  |  |  | 290 |  |  |  |  | 349 |  |
| 3 | EXIST TW-13 | DD+0 | 59°00'00'' |  | 3 | PROP TW-13 | DD+0 | 42°41'24" LT |  |  |
|  |  |  |  | 340 |  |  |  |  | 325 |  |
| 4 | EXIST TW-14 | DA+0 |  |  | 4 | PROP TW-14 | DA+3 | 00°00'00" |  |  |
|  |  |  |  | 380 |  |  |  |  | 365 |  |
| 5 | EXIST TW-15 | DD+0 | 31°17'50'' |  | 5 | PROP TW-15 | DA+3 | 00°00'00" |  |  |
|  |  |  |  | 370 |  |  |  |  | 320 |  |
| 6 | EXIST TW-16 | DB+0 | 07°55'58'' |  | 6 | PROP TW-16 | PDD+9 | 08°44'13" LT |  |  |
|  |  |  |  | 291 |  |  |  |  | 248 |  |
| 7 | EXIST TW-17 | DA+0 |  |  | 7 | PROP TW-17 | PDD+9 | 34°12'30" RT |  |  |
|  |  |  |  | 282 |  |  |  |  | 205 |  |
| 8 | EXIST TW-18 | DB+0 | 03°39'00'' |  | 8 | PROP TW-18 | PDD+9 | 21°30'14" LT |  |  |
|  |  |  |  | 222 |  |  |  |  | 221 |  |
| 9 | EXIST TW-19 | DB+0 | 05°35'00'' |  | 9 | PROP TW-19 | PDD+9 | 07°48'50" LT |  |  |
|  |  |  |  | 286 |  |  |  |  | 262 |  |
| 10 | EXIST TW-20 | DC+0 | 17°44'20" |  | 10 | EXIST TW-20 | DC+0 | 17°44'20" |  |  |
|  |  | Route Length in KM |  | 2.786 |  |  | Route Length in KM |  | 2.549 |  |

Please Note, The tower schedule indicated above is subjected to change.

    - The Contractor shall have to construct the transmission line portions, covered under the tower package, completely up to suitable tower as per instruction of Engineer In-Charge. Stringing shall also be carried out for diverted portion of above transmission line so as to make it ready in all respect for power flow between the terminal stations.

- Transmission towers and Line data

  - General Description of the Tower*

    - The transmission towers covered under the package are of self-supporting hot dip galvanized lattice steel type, designed to carry the line conductors with necessary insulators, earth wire*, OPGW*(If applicable) and all fittings under all loading conditions.  Outline diagram of towers are enclosed with the Specification.

    - The towers shall have mild steel or/and high tensile steel sections and shall be fully galvanized as specified in relevant clauses in section-IV. Bolts and nuts with spring washer are to be used for connections.

    - The towers are of the following types:

A)	Double Circuit

B)	Monopole (D/C Tower)

  - Classification of Towers

The tower for 400kV line shall be vertical configuration and are classified as below:

| Sl No | Type of Tower |  | Deviation Limit | Typical Use |
| --- | --- | --- | --- | --- |
| 1 | DA |  | 0 – 2 deg. | To be used as Tangent tower. |
| 2 | DB |  | 0 deg. | To be used as Section Tower. |
|  |  |  | 0 - 15 deg. | - Angle towers with tension Insulator string. |
|  |  |  |  | - Also to be used for uplift force resulting from an uplift span up to 200m under broken wire conditions. |
|  |  |  |  | - Also to be used for Anti Cascading Condition. |
| 3 | DC |  | 0 deg. | To be used as Section Tower. |
|  |  |  | 15-30 deg. | - Angle tower with tension insulator string. |
|  |  |  |  | - Also to be used for uplift forces resulting from an uplift span up to 200m under broken wire condition. |
|  |  |  |  | - Also to be used for anti-cascading condition. |
| 4 | DD |  | 30 - 60 deg. | - Angle tower with tension insulator string. |
|  |  |  |  | - Also to be used for uplift forces resulting from an uplift span up to 300m under broken wire condition. |
|  |  |  |  | Dead end with 0 deg to 15 deg deviation both on line side and sub-station side (slack span) |
|  |  |  | 0 deg. | - Complete Dead end |
|  |  |  |  | - For river crossing anchoring with longer wind span. |
| 5 |  | PDD (Monopole) | 30- 60 deg. | - Angle tower with tension insulator string. |
|  |  |  |  | - Also to be used for uplift forces resulting from an uplift span up to 100m under broken wire condition. |
|  |  |  | 0 deg. | - Complete Dead end |

Note:

1.	The above towers can also be used for longer span with smaller angle of 	deviations without infringement of ground clearance.

2.  	The above table provides indicative classification of Towers. Tower spotting data for various towers to be used in the transmission lines under the specific package shall be given to the contractor during execution stage.

  - Electrical Clearances

    - Ground Clearance

The minimum ground clearance from the bottom conductor shall not be less than 8840 mm for 400KV at the maximum sag conditions i.e. at max temperature as indicated in tower spotting data and still air.

a) 	An allowance of 150mm shall be provided to account for errors in stringing.

b) 	Conductor creep shall be compensated by over tensioning the conductor at a temperature as mentioned in section IV of this specification.

- Different Sections to Technical Specification

  - For the purpose of present scope of work, technical specification shall consist of following parts and they should be read in conjunction with each other: -

| Sl. No. | Section Number | Name of Section | Rev No. |
| --- | --- | --- | --- |
| 1 | Section-IA | Scope | Rev-9 (March’2024) |
| 2 | Section-IB | General Information | Rev-10 (Oct’2024) |
| 3 | Section-II | General Technical Conditions | Rev-2 (Feb’2022) |
| 4 | Section-III | Survey and Soil Investigation | Rev-5 (Dec’2023) |
| 5 | Section-IVA | Tower Design | Rev-6 (Dec’2023) |
| 6 | Section-IVB | Tower Testing | Rev-3 (Dec’2023) |
| 7 | Section-IVC | Fabrication, Erection and Stringing | Rev-7 (Dec’2023) |
| 8 | Section-IVD | Foundation (Contractor Design) | Rev-6 (Dec’2023) |
| 9 | Section-IV E | Foundation (Employer Design) | Rev-5 (Dec’2023) |
| 10 | Section-IV F | Monopole Structure, Foundation and Erection | Rev-2 (Mar’2023) |
| 11 | Section-V | Galvanised Steel Earthwire | Rev-1 (May’2024) |
| 12 | Section-VIA | Hardware Fittings and Accessories for Conductor & Earthwire | Rev-3 (Dec’2023) |
| 13 | Section-VIB | Clamp Fittings and Accessories for HTLS Conductor | Rev-2 (Jan’2022) |
| 14 | Section-VIIA | Conductor | Rev-3 (Dec’2023) |
| 15 | Section-VII B | HTLS Conductor | Rev-5 (Sept’2024) |
| 16 | Section-VIII | Composite Longrod Insulators | Rev-4 (Oct’2024) |
| 17 | Section-IX A | Pile foundation | Rev-6 (OCt’2024) |
| 18 | Section-IX B | Stone Column | Rev-0 (Dec’2023) |
| 18 | Section-X | OPGW | Revision (June’2024) |
| 20 | Section-XI | Drawings | Rev-1 (Aug’2023) |
| 21 | Section-XII | FAQ | Rev 0 (June’2021) |
| 22 | Section-XIII | Tower Schedule of Existing Line (only applicable for Re-conductoring packages) |  |

  - In case of any discrepancy between Section-IA (Scope) and Section-IB (General Information) and other technical specifications on scope of works, Section-IA (Scope) shall prevail over all other sections.

  - In case of any discrepancy between Section-IB (General Information) and individual sections for various equipment, requirement of individual equipment section shall prevail.

- Service Conditions:

Equipment/material to be supplied against this specification shall be suitable for satisfactory continuous operation under tropical conditions as specified below:

| Maximum ambient temperature (oC) | 50 |
| --- | --- |
| Minimum ambient temperature (oC) | 0 |
| Relative humidity (% range) | 10-100 |
| Wind zone (as per NBC) | 3 |
| Terrain Category | 2 |
| Maximum wind velocity (m/sec.) | 44 |
| Maximum altitude above mean sea level (Meters) | Below 1000m |
| Isokeraunic level (days/years) | 60 |

Moderately hot and humid tropical climate conducive to rust and fungus growth.

Annexure-A

PROFORMA OF UNDERTAKING BY THE PROPOSED AGENCY FOR PILE FOUNDATION

(On Non-Judicial Stamp Paper of appropriate value, wherever applicable)

To,

Power Grid Corporation of India Ltd.

B-9, Qutab Institutional Area

Katwaria Sarai

New Delhi - 110016

Dear Sir,

Whereas Power Grid Corporation of India Ltd., with its Registered Office at B-9, Qutab Institutional Area, Katwaria Sarai, New Delhi–110016 (hereinafter referred to be as the ‘’), having invited bids for ______________________  (Name of the package & Specification No.)_____________________________________, in response to which M/s._______________(Name of the Bidder), with its Registered office at _____________________________(Full Address _______________________________) are submitting the bid vide ref_________________ date___________________(hereinafter called the ‘Bid’).

We,__________________(Name of the Agency) with its Registered Office at___________________(Full Address____________________(hereinafter referred to as the ‘Agency’, which expression shall unless repugnant to the context and meaning therefore include its successor, administrator, executor and permitted assigns)do hereby undertake in the event of award of the Contract to execute the pile foundation  work covered under the scope of the Contract, fulfilling all the requirements and construction schedule agreed under the Contract.

Signed on this day of _________20__ at________________

(Signature)___________________

Authorised signatory on behalf of

M/s___________________

(Name)_________________

(Designation)__________________

Note: Separate undertaking to be provided in case of more than one agency proposed.

Annexure-B

PROFORMA OF UNDERTAKING BY THE PROPOSED AGENCY FOR STONE COLUMN

(On Non-Judicial Stamp Paper of appropriate value, wherever applicable)

To,

Power Grid Corporation of India Ltd.

B-9, Qutab Institutional Area

Katwaria Sarai

New Delhi - 110016

Dear Sir,

Whereas Power Grid Corporation of India Ltd., with its Registered Office at B-9, Qutab Institutional Area, Katwaria Sarai, New Delhi–110016 (hereinafter referred to be as the ‘’), having invited bids for ______________________  (Name of the package & Specification No.)_____________________________________, in response to which M/s._______________(Name of the Bidder), with its Registered office at _____________________________(Full Address _______________________________) are submitting the bid vide ref_________________ date___________________(hereinafter called the ‘Bid’).

We,__________________(Name of the Agency) with its Registered Office at___________________(Full Address____________________(hereinafter referred to as the ‘Agency’, which expression shall unless repugnant to the context and meaning therefore include its successor, administrator, executor and permitted assigns)do hereby undertake in the event of award of the Contract to execute the Stone column installation works covered under the scope of the Contract, fulfilling all the requirements and construction schedule agreed under the Contract.

Signed on this day of _________20__ at________________

(Signature)___________________

Authorised signatory on behalf of

M/s___________________

(Name)_________________

(Designation)__________________

Note: Separate undertaking to be provided in case of more than one agency proposed.