Technical Specification

SURVEY WORK-Route Alignment

TECHNICAL SPECIFICATIONS

SECTION- III

SURVEY WORK

1.0	General Information & Scope of Work

1.1	The technical specifications cover route alignment/preliminary survey/ walkover survey, optimization of route, for the transmission lines/ part of the transmission lines covered under this specification.

1.1.1	The scope of work inter-alia shall include the following: -

- Route preliminary/walkover Survey using Total Work stations, or alternatively using ALTM (Airborne Laser Terrain Modeling) techniques,

- Preparation of Survey reports including estimation of Bill of Quantities, identification and explanation of route constraints (like Forest, Animal/ Bird sanctuary, reserve coal belt areas, oil pipe line/ underground inflammable pipe lines etc.), infrastructure details available en-route etc.

1.2	The Provisional quantities for the scope of work are indicated in relevant Price Schedules of BPS. The final quantities for route alignment, (quantities in “kms” unit) shall be as approved by Site Engineer-in-charge and shall be along the approved route alignment. The route alignment, including tower spotting,  etc. shall be carried out by the Contractor as per the technical specifications stipulated herein. Contractor shall indemnify the Employer for any loss or damage to properties, trees etc. during the survey work.

1.3	The Contractor should note that Employer will not furnish topographical maps prepared by survey of India but will make available assistance that may be required in obtaining these by providing letters of recommendation to the  concerned.

| 1.4 | After carrying out the Route survey the contractor shall submit complete BOQ of |
| --- | --- |
|  | the transmission lines, Tower schedule, Survey report and other details |
|  | as per technical specification requirements to the Employer as per Format Annex-A |

- Route Alignment

2.1	The route Alignment shall be carried out by the contractor using Survey of India topographical maps.

2.2	Requirement of Transmission Line Routing

2.2.1.	The Re-alignment/ routing, if any required, of the transmission line shall be most economical from the point of view of construction and maintenance. The contractor shall identify & examine alternative route alignments and suggest to the Employer the optimal route alignment.

2.2.2.	Routing/ Re-routing of transmission line through protected/reserved forest area should be avoided. In case it is not possible to avoid the forests or areas having large trees completely, then keeping in view of the overall economy, the route should be aligned in such a way that involvement of forest area and cutting of trees is minimum.

2.2.3.	The route should have minimum crossings of Major river, Railway lines, National/ State highways, overhead EHV power line and communication lines. The number of angle points shall be kept to minimum The distance between the terminal points specified shall be kept shortest possible, consistent with the terrain that is encountered.

2.2.4.	Marshy and low-lying areas, river beds and earth slip zones shall be avoided to minimize risk to the foundations.

2.2.5.	It would be preferable to utilize level ground for the alignment.

| 2.2.6. | Crossing of power lines shall be minimum. Alignment of a transmission line with |  |
| --- | --- | --- |
|  | respect to existing line will be kept considering ROW and tower falling distance. |  |
| 2.2.7. | Crossing of communication line shall be minimized and it shall be preferably at |  |
|  | right angle. Proximity and parallelism with telecom lines shall be eliminated to |  |
|  | avoid danger of induction to them. |  |
| 2.2.8. | Areas subjected to flooding such as nalah shall be avoided. |  |
| 2.2.9. | Restricted areas such as civil and military airfield shall be avoided. Care shall also |  |
|  | be taken to avoid aircraft landing approaches. |  |
| 2.2.10. | All alignment should be easily accessible both in dry and rainy seasons to enable |  |
|  | maintenance throughout the year. |  |
| 2.2.11. | Certain areas such as quarry sites, tea, tobacco and saffron fields and rich |  |
|  | plantations, gardens & nurseries which will present the Employer problems in |  |
|  | acquisition of right of way and way leave clearance during construction and |  |
|  | maintenance should be avoided. |  |
| 2.2.12. | Angle points during survey should be selected such that shifting of the point within |  |
|  | 100 m radius is possible at the time of construction of the line. |  |
| 2.2.13. | The line routing should avoid large habitations, densely populated areas, Forest, |  |
|  | Animal/Bird sanctuary, reserve coal belt areas, oil pipe | line/underground |
|  | inflammable pipe lines etc. to the extent possible. |  |
| 2.2.14. | The areas requiring special foundations and those prone to flooding should be |  |
|  | avoided. |  |
| 2.3 | For examination of the alternatives & identification of the most appropriate route, |  |
|  | besides making use of information/ data/ details available/ extracted through |  |
|  | Survey of India Topographical maps, the contractor shall also carryout |  |
|  | reconnaissance/ preliminary survey as may be required for verification & |  |
|  | collection of additional information/ data/ details. |  |
| 2.4 | The contractor shall submit his preliminary observations & suggestions along with |  |
|  | various information/ data /details collected, topographical map data marked with |  |
|  | the alternative routes etc. The final evaluation of the alternative routes shall be |  |
|  | conducted by the contractor in consultation with Employer’s representatives and |  |
|  | optimal route alignment shall be proposed by the contractor. Site visit and |  |
|  | field verification shall be conducted by the contractor jointly with the |  |
|  | Employer’s representative for the proposed route alignment. |  |
| 2.5 | Final route alignment drawing with latest topographical and other details/ |  |
|  | features including all rivers, railway lines, canals, roads etc. up to 8 km on both |  |
|  | sides of selected route alignment shall be submitted by the contractor for |  |
|  | Employer’s approval along with report containing other information/details as |  |
|  | mentioned above. |  |
| 2.6 | Changes in the route alignment, if any, during detail survey, shall be incorporated |  |
|  | in the final route alignment drawings. |  |

3.0	Optimization of Tower Location/ Tower Spotting

3.1.1.	Optimization of tower locations (angle point) in the line route  general description of towers is for double circuit line is DA/DB1/DB2/DC1/DDC2/DD1/DD2 of this specification for information of the Bidders.

3.1.3.	Tower Spotting

While routing & spotting the towers, the following shall be borne in mind:

a)  Span

The number of consecutive spans between the section points shall not exceed 15 spans or 5 km in plain terrain and 10 spans or 3km in hilly terrain. A section point shall comprise of tension point with B/DB/QB type or C/DC/QC type or D/DD/QD type towers as applicable.

b)  Extension/Truncation

An individual span shall be as near to the normal design span as possible. In case an individual span becomes too short with normal supports on account of undulations in ground profile, one or both the supports of the span may be extended by inserting standard body/ leg extension. In case of locations where the ground clearance is available, truncated towers may be spotted. The provisions kept in the design of towers w.r.t. body/ leg extensions, truncations shall be intimated to the contractor by the Employer during execution stage.

c)  Loading

There shall not be any upward force on suspension towers under normal working conditions and the suspension towers shall support at least the minimum weight span as provided in the designs. In case uplift is unavoidable, it shall be examined if the same can be overcome by adding standard body extensions to the towers failing which tension towers designed for the purpose shall be deployed at such positions.

d)  Road Crossing

At all important road crossings, the tower shall be fitted with normal suspension and tension insulator strings depending on the type of tower, but the ground clearance at the roads under maximum temperature and in still air shall be such that even with conductor broken in adjacent span, ground clearance of the conductor from the road surfaces will not be less than specified minimum ground clearances. At all national highways, D/DD/QD type towers tension insulator strings shall be used and crossing span will not be more than 250 meters, unless higher span is permitted by national highways authority in case of highways having more lanes.

e)  Railway Crossings

All the railway crossings coming En-route the transmission line shall be identified by the Contractor. At the time of survey, the railway crossings shall be finalized based on the following and also confirming to the regulation laid down by the Railway Authorities.

- The crossings shall be supported on D/DD/QD type tower on either side.

- The crossing shall normally be at right angle to the railway track.

- The minimum horizontal distance measured at right angles from the center of nearest track to any part of a structure (all structures shall be rigid and well founded), carrying electrical conductors crossing a railway shall be equal to the height of the structure in meters above normal ground level plus 6 meters.

- No crossing shall be located over a booster transformer, traction switching station, traction sub-station, Overlap Section or a track cabin location in an electrified area. 0 % of the normal span for which the structure is designed whichever is less.

- Minimum ground clearance between crossing conductor under condition of maximum sag and railway line shall maximum of following:

  - Vertical Clearance for OHE (other than high rise OHE):

|  | Sl. | Transmission line | Minimum clearances from Rail Level |
| --- | --- | --- | --- |
|  | No. | Voltage level | New Power Line Crossing or Crossing |
|  |  |  | Planned for Alteration |
|  | 1 | Above 66 kV & up to 132 kV | 15.56 m |
|  | 2 | Above 132 kV & upto 220 kV | 16.46 m |
|  | 3 | Above 220 kV & upto 400 kV | 18.26 m |
|  | 4 | Above 400 kV & upto 500 kV | 19.16 m |
|  | 5 | Above 500 kV & upto 800 kV | 21.86 m |

- Vertical Clearance for high rise OHE:

| Sl. | Transmission line voltage | Minimum clearances from Rail Level |
| --- | --- | --- |
| No. | level | New Power Line Crossing or Crossing |
|  |  | Planned for Alteration |
| 1 | Above 66 kV & upto 132 kV | 17.56 m |
| 2 | Above 132 kV & upto 220 kV | 18.46 m |
| 3 | Above 220 kV & upto 400 kV | 20.26 m |
| 4 | Above 400 kV & upto 500 kV | 21.16 m |
| 5 | Above 500 kV & upto 800 kV | 23.86 m |

Note: Applicable only for electrification of routes where double stack container having maximum height of 6809mm is plying.

- Minimum Clearances between Highest Traction Conductor & Lowest Crossing Conductor

| 1 | Above 66 kV & upto 132 kV | 3.05 m |
| --- | --- | --- |
| 2 | Above 132 kV & upto 220 kV | 4.58 m |
| 3 | Above 220 kV & upto 400 kV | 5.49 m |
| 4 | Above 400 kV & upto 500 kV | 7.94 m |
| 5 | Above 500 kV & upto 800 kV | 7.94 m |

f)	River Crossings

In case of major river crossing, river crossing towers shall be of suspension type along with anchor towers of D/DD/QD type tower on either side of the main river crossing. Alternately on the basis of economics and / or site/ execution constraints crossing of rivers using normal extended angle towers (+18/+25/+30M Extensions) also shall be considered. For navigable rivers, clearance required by navigation authority shall be provided. For non-navigable river, clearance shall be reckoned with respect to highest flood level (HFL).

g)  Power line Crossings

Where the line is to cross over another line, towers with suitable extensions may be used, depending upon the merit of the prevailing site condition.

For power line crossing of 400 kV or above voltage level, large angle & dead-end towers (i.e. D/DD/QD) shall be used on either side of power line crossing (i.e. D/DD/QD- D/DD/QD arrangement).

For power line crossing of 132 kV and 220 kV voltage level, angle towers (B/C/D/DB/DC/DD/ QB/QC/QD) shall be used on either side of power line crossing depending upon the merit of the prevailing site condition and line deviation requirement.

For power line crossing of 66 kV and below voltage level, suspension/tension towers shall be provided on either side of power line crossing depending upon the merit of the prevailing site condition and line deviation requirement.

In case of crossing with B/C/DB/DC/QB/QC towers proper guying shall be provided to facilitate stringing of the power line crossing sections separately on obtaining line shutdowns.

Clearance between lines crossing each other shall be kept in accordance with the CEA (Measures Relating to Safety and Electric Supply) Regulations, 2010 as amended up-to-date. In order to reduce the height of the crossing towers, it may be advantageous to remove the ground-wire of the line to be crossed (if this is possible and permitted by the Employer of the line to be crossed).

Minimum clearance in meters between lines when crossing each other:

| Sl. | Nominal | 110- | 220 kV | 400 kV | 765 kV | 500 kV | 800 kV | 1200 kV |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| No. |  | 132 |  |  |  | HVDC | HVDC |  |
|  |  | kV |  |  |  |  |  |  |
| 1 | 110-132KV | 3.05 | 4.58 | 5.49 | 7.94 | 6.86 | 9.04 | 10.44 |
| 2 | 220KV | 4.58 | 4.58 | 5.49 | 7.94 | 6.86 | 9.04 | 10.44 |
| 3 | 400KV | 5.49 | 5.49 | 5.49 | 7.94 | 6.86 | 9.04 | 10.44 |
| 4 | 765KV | 7.94 | 7.94 | 7.94 | 7.94 | 7.94 | 9.04 | 10.44 |
| 5 | 500KV HVDC | 6.86 | 6.86 | 6.86 | 7.94 | 7.94 | 9.04 | 10.44 |
| 6 | 800KV HVDC | 9.04 | 9.04 | 9.04 | 9.04 | 9.04 | 9.04 | 10.44 |
| 7 | 1200 KV | 10.44 | 10.44 | 10.44 | 10.44 | 10.44 | 10.4 | 10.44 |
|  |  |  |  |  |  |  | 4 |  |

h)  Telecommunication Line Crossings

The angle of crossing shall be as near to 90 degree possible. However, deviation to the extent of 30 degree may be permitted under exceptionally difficult situations.

When the angle of crossing has to be below 60 degree, the matter will be referred to the authority in charge of the telecommunication System. On a request from the Contractor, the permission of the telecommunication authority may be obtained by the Employer.

Also, in the crossing telecommunication line between the wires.

span,	power	line	support	will	be	as	near	the

as  possible,  to  obtain increased  vertical  clearance

i)	Oil Pipe-Line Crossings

Wherever transmission line crosses an oil/gas pipeline, the angle of crossing shall be as near to 90 degree possible. Further, a minimum separation of 3m should be maintained between pipe line and transmission line footings & pipe/ counterpoise earthing.

j)	Details En-route

All topographical details, permanent features, such as trees, building etc. within following distance on either side of the alignment shall be on the profile plan: -

|  |  | 1 |  | 1200 kV Single Circuit |  |  | 44.5 m |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | 2 |  | 765 kV Double Circuit |  |  | 33.5 m |
|  |  | 3 |  | 765kV Single Circuit Delta |  |  | 32 m |
|  |  | 4 |  | 765kV Single Circuit |  |  | 42.5 m |
|  |  |  |  | Horizontal |  |  |  |
|  |  | 5 |  | +800 kV HVDC |  |  | 34.5 m |
|  |  | 6 |  | 400kV Single Circuit |  |  | 26.0 m |
|  |  | 7 |  | 400kV Double Circuit |  |  | 23.0 m |
|  |  | 8 |  | +500 kV HVDC |  |  | 26.0 m |
|  |  | 9 |  | 220 kV |  |  | 17.5 m |
|  |  | 10 |  | 132 kV |  |  | 13.5 |
| 3.1.4 | Clearance from Ground, Building, Trees etc. |  |  |  |  |  |  |

Clearance from ground, buildings, trees and telephone lines shall be provided in conformity with the CEA’s Regulations 2010 (Measures relating to Safety and Electric Supply).

3.1.5.	The Row for clearance from building, marking of trees any permanent structure is as below:

| 1 |  | 1200 kV Single Circuit |  | 44.5 m |
| --- | --- | --- | --- | --- |
| 2 |  | 765 kV Double Circuit |  | 33.5 m |
| 3 |  | 765kV Single Circuit Delta |  | 32 m |
| 4 |  | 765kV Single Circuit |  | 42.5 m |
|  |  | Horizontal |  |  |
| 5 |  | +800 kV HVDC |  | 34.5 m |
| 6 |  | 400kV Single Circuit |  | 26.0 m |
| 7 |  | 400kV Double Circuit |  | 23.0 m |
| 8 |  | +500 kV HVDC |  | 26.0 m |
| 9 |  | 220 kV |  | 17.5 m |
| 10 |  | 132 kV |  | 13.5 |

| 4.0 | Preliminary Schedule |  |
| --- | --- | --- |
|  | The report showing the locations of the towers together with preliminary |  |
|  | schedules of quantities indicating tower types, wind & weight spans, angle of |  |
|  | deviation, crossing & other details etc. shall be submitted by the contractor for |  |
|  | review & approval by Employer’s site-in-charge. |  |

4.1.1	The co-ordinates of all the tower locations shall also be recorded using GPS / DGPS of positional accuracy less than 3m for easy relocating. The position of all tower locations shall be marked in the final digitized route alignment drawing with relative distances from any permanent bench mark area.

4.1.2	The contractor shall also collect required data at each tower location in respect of soil strata, ground water level, history of water table in adjacent areas/surface water, distance from permanent bench mark (these details to be furnished in a tabulated form) and classify the suitable type of foundation at each tower location based on the data collected at each location.

5.0	Survey Methodology & Precision

5.1.1	 All elevations shall be referenced to benchmarks established by the survey of

India. Survey operations shall begin and end at benchmarks approved by the

Employer.

5.1.2	All-important objects and features along the transmission line centerline (railways, highways, roads, canals, rivers, transmission lines, distribution lines, telephone lines etc.) shall be surveyed and located with a positional accuracy of 1:2000 between points of known horizontal position.

6.0	Survey Report

6.1.1.	Complete BOQ of the transmission lines as per format enclosed with this technical specification at Annexure-A shall be furnished in the survey report.

6.1.2	Each angle point locations shall be shown with detailed sketches showing existing close by permanent land marks such as specific tree(s), cattle shed, homes, tube wells, temples, electric pole/ tower, telephone pole, canal, roads, railway lines etc. The relative distance of land marks from the angle points and their bearings shall be indicated in the sketch. These details shall be included in the survey report.

6.1.3	Information w.r.t infrastructure details available en-route, identification and explanation of route constraints, etc. shall also be furnished in the Survey report and shall inter-alia include the following:

6.1.4	Information regarding infrastructural facilities available along the final route alignment like access to roads, railway stations, construction material sources (like quarry points for stone, sand and availability of construction water), labor, existing transport facilities, fuel availability etc. shall be furnished in the survey report.

6.1.5	All observations which the Contractor thinks would be useful to the construction of the transmission lines mentioned under scope of work are to be reported.

6.1.6	Working months available during various seasons along the final route alignment, with period, time of sowing & harvesting of different type of crops and the importance attached to the crops particularly in the context of way leave problems and compensation payable shall be stated by the Contractor.

6.1.7	Some portions of the line may require clearance from various authorities. The Contractor shall indicate the portion of the line so affected, the nature of clearance required and the name of concerned organizations such as local bodies, municipalities, P&T (name of circle), Inland navigation, Irrigation Department, Electricity Boards and Zonal railways, Divisional Forest Authorities etc.

6.1.8	         A copies of survey reports shall be furnished by the contractor to the Employer.

……………………………………….End………………………………………………………………………………………………..