| Sl. No | Clause No | Existing clause | Amended as |
| --- | --- | --- | --- |
| 1 | S. No 3.1, Section-I, Invitation for Bids | Scope of Work a)……Both main and backup control centers shall work in active-active mode and in case of failure of main control center, backup shall come in role of main without any manual interruption (except commands & signals). e) …..The integration of new RTUs at the Control center end shall also be in the scope of the Contractor. Further, future bay integration shall not be treated as a new RTU integration during AMC period, and any bay extension during AMC shall be in the scope of the contractor without any commercial implication to the Owner. | Scope of Work Replace with - …..Both Main and Backup control centers shall work in active-active mode and in case of failure of Main control center, Backup shall come in role of Main without any manual interruption (except for taking over Control authority). - …..The integration of new RTUs at the Control center end shall also be in the scope of the Contractor. The scope of works under integration of RTU with control centre is inclusive of work of integration (including database and display) with DCPC/Terminal Server also, if any. Further, future bay integration at Control Center end shall not be treated as a new RTU integration during AMC period, and any bay extension at Control Center end during AMC shall be in the scope of the contractor without any commercial implication to the Owner. The future bay integration during AMC period at substation end shall be in the scope of contractor as mentioned in Bill of Quantity Appendix-G. |
| 2 | S. No 3.1, Section-I, Invitation for Bids | Scope of Work l) Development of complete Database displays and reports to display SCADA and RE related information with analysis and report generation facility. The text available in displays and reports shall have support of fonts for English and Hindi. Contractor shall develop and provide tools to convert CIM files for different versions based on customized CIM-profiles in the files used by vendors system. The displays shall comply with the Display Building guidelines as per Appendix-K, Part-B of Vol-II. | Scope of Work Replace with l) Development of complete Database displays and reports to display SCADA and RE related information with analysis and report generation facility. The text available in SCADA displays and reports shall have support of fonts for English and Hindi. Contractor shall develop and provide tools to convert CIM files for different versions based on customized CIM-profiles in the files used by vendors system. The displays shall comply with the Display Building guidelines IS 18058: 2023 and as per contract document. |
| 3 | S. No 3.1 , Section-I, Invitation for Bids | bb) During entire contract period (including extension of contract, if any), if OEM discontinues/declares end of support to any item supplied (Software/Hardware/Security Solution/OS) under the contract, causing security vulnerability, the contractor has to replace such hardware, software (or both, depending on software or hardware dependencies on each-other) without any additional cost to the Owner. Replacement shall be of either same or higher configuration. ii) C10 Capacity test of the Supplied Battery banks shall be done periodically (yearly), to determine whether the rating of battery is holding up using capacity test. If the battery capacity is less than 80% of its design value in any of the cases, the battery shall have to be replaced by contractor during entire period of contract (including extension of contract, if any) without any cost implications to owner. If number of cells replaced(cumulative) in battery bank exceeds more than 25% of total battery bank in any of the cases during entire period of contract, then contractor shall replace that entire battery bank without any additional cost to the Owner. Also, Refer Section 3 & Section 8, PART C of TS. jj) Necessary support for providing Security Logs from Firewalls & Other Cyber Security Devices to NCIIPC and integration of supplied SLDC cum REMC system cyber security systems with the future Security Operations Center (SOC) and Security Orchestration, Automation and Response (SOAR) systems to be procured by the Owner. | Replace with bb) During entire contract period, if OEM discontinues or declares end of support/end-of-life, whichever is later for any item supplied (Software/Hardware/Security Solution/OS) under the contract, the contractor has to replace such hardware, software (or both, depending on software or hardware dependencies on each-other) as per provisions mentioned under Clause 1.20, Section-1, Part-A of technical specifications along with other scope of works specified under the contract . The replacement due to EOL and EOS of Hardware/software shall be required if it has become either non-functional or the patches/updates have been discontinued from the OEM. ii) Capacity test @ C10 shall be done periodically (yearly), for assessment of health of the battery bank (UPS & DCPS wherever applicable) to determine charge holding capacity of battery bank. The conditions for batteries/battery bank replacement for one-year DLP and up to 6 years AMC period is as follows: - Irrespective of the design/expected life of the supplied battery banks, If the battery bank capacity is less than 80% of its design value at end cell voltage of 1.75V/cell in any of the cases, Replacement of faulty battery cells/battery banks shall be in the scope of the contractor, without any cost implication to the Owner. - If the number of cells replaced (cumulative) in the supplied battery bank exceeds more than 25% of total batteries, then contractor shall replace that entire battery bank without any additional cost implication to the Owner. Also, Refer Section 3 & Section 8 of PART C and Section 2 of PART D technical specification. jj) Necessary support for providing Logs from firewalls/other cyber security devices through SIEM to NCIIPC and for integration of entire SIEM logs with the future Security Operations Center (SOC) and Security Orchestration, Automation and Response (SOAR) systems to be procured by Owner(s). |
| 4 | S. No 3.1 , Section-I, Invitation for Bids | Inserted new clause | ll) Integration with Offline Applications (such as Scheduling, Outage, National Open Access Registry (NOAR), Metering data processing, REMC, Load forecast, IMD web, Day Ahed Market, Real Time Market, Enterprise Resource Planning (ERP), RLDC website, SLDC website etc.) with Main and Backup SLDC. The integration with these applications shall be as per the interface mentioned in the Technical Specification. mm) The SCADA/EMS system sizing shall be as per the appendix F. The Owner at its own discretion may allocate any unutilized quantum of analog points to status points and status points to analog points as per their requirement, within the overall limit of number of licensed points configured for the SLDC. Note :- The entire contract period includes the period from award to completion of AMC period (one year DLP and 6 year AMC). In bidding document, wherever “including extension of AMC period, if any”, is written, shall be read as “not applicable”. The extension referred here is after completion of AMC period. |
| 5 | GCC 42, Section-V: SCC, Vol.-I of the Bidding Documents | - | J. PRE DEFINED EVENTS 42. POWERGRID has a Policy on Assessment of performance of bidders before recommending a bidder for award of Contract. For this purpose, performance of a bidder based on events (pre-defined events) encountered during execution of contract(s) (Own as well as Consultancy) awarded by POWERGRID (including SPVs under TBCB) shall also be considered. In case of triggering of these events, the bids from such bidders shall be considered non-responsive/not eligible for a period of one year reckoned from the date of issuance of letter to such effect. As per this Policy, pre-defined events are as below: - Termination# of Contract due to Contractor’s default - Encashment of CPG due to non-performance - Repeated failure of major Equipment while in service - Substantial portion of works (more than 50% of the Contract*) is sub-contracted, under an existing Contract - More than 25% of the Contract price (awarded value), in aggregate, is paid to sub-contractors/suppliers as Direct payment, under an existing Contract, due to financial position of Contractor - Firm has been referred to NCLT under Insolvency & Bankruptcy Code (IRP has been appointed or Liquidation proceedings have been initiated under IBC) # Partial offloading under a Contract and/or Facilitation beyond 10% of the Contract Price shall also be treated as Termination. *For the purpose of working out 50% of the Contract, following shall be taken into account: - Scope of the contract which is permissible to be sub-contracted as per bidding documents, shall be excluded. - Scope of the Contract which primarily relates to the Qualification Requirement (QR) of the bidder. The Employer shall be the sole judge in this regard and the Employer’s interpretation on the aforesaid event(s) shall be final and binding. In accordance with above policy of POWERGRID, in case of triggering of any of the above events under this Contract, the bid of the Contractor in future tenders shall be dealt in line with the above policy or its subsequent amendments, if any. |