| S No | Clause | Provision of Bidding Documents | Bidder’s Query | POWERGRID's Reply |
| --- | --- | --- | --- | --- |
|  | Volume II Part-A, , Section-4, Clause no-4.2, Maintenance support | For all third-party equipment (Hardware & Software), Contractor shall have back to back support and warranty for all maintenance services & availability of Security Patches along with supply of spare with appropriate response time from OEM/OEM Authorized representatives and these Back-to-Back contracts will be shared with owner before start of defect liability period. | OEM Support life Cycle is 3 to 5 years. We maintain support from OEM partner. Kindly confirm. | Refer earlier issued Amendment – IV to technical specification. Bidder to comply technical specification. |
|  | Volume II Part-A, , Section-4, Clause no-4.2, Maintenance support | In case, any hardware / software / equipment / component items of the systems supplied under the contract shall reach its End-of-Life (EOL) or End-of-Support (EOS) whichever is earlier, and is causing security vulnerability, then the contractor shall replace such item with new Hardware or Software without any financial implication to owner. (g) OEM Back-to-back Support: | Life Cycle for the IT hardware and software if 3 to 5 years. In case of EOL/EOS OEM support is not available and any change are dependent on each other e.g. if we change the vision of third party software, it depends on the Operating system which is again dependent on hardware. | Refer earlier issued Amendment – IV to technical specification. Bidder to comply technical specification. |
|  | Volume II Part-A, , Section-4, Clause no-4.2, Maintenance support | The Owner at their own discretion may extend the duration of the maintenance period for up to 2 years based on the same rates, same terms, and conditions of the contract. For any addition (e.g., integration of new RTUs or new control center) during the maintenance period (as identified in the BoQ), the Contractor shall provide all the services at control center end without any additional cost during the entire period of contract including extension (if any) | Considering changing IT landscape we request remove extension of AMC from the scope. | Refer earlier issued Amendment – IV to technical specification. Bidders to comply Technical Specification |
|  | Volume II Part-A, , Section-4, Clause no-4.2, Maintenance support | J(iii)Contractor must submit proper cyber risk mitigation plan/risk offered by connecting the system to the internet (whenever required) along with necessary cyber security measures in place. The contractor is allowed then only when the plan is approved by the owner. | As per cyber security guidelines. All critical infra has to be Air Gap environments. Owner has to ensure the limited Internet connectivity vis their secured IT network. | Bidder to comply technical specification. |
|  | Volume II Part-A, , Section-4, Clause no-4.3, Preventive Maintenance Activity | (f) Addition and modification of database and displays, report generation, configuration and Database sizing activities including on-lining as detailed in the specification for all applications etc. and other day-to-day operational activities would primarily be the responsibility of Contractor | Please elaborate operational activity, our understanding is limited to maintenance only | Refer earlier issued Amendment – IV to technical specification. Bidders to comply Technical Specification |
|  | Volume II Part-A, , Section-4, Clause no-4.3, Preventive Maintenance Activity | (l) The contractor shall maintain a list of inventories of all hardware and software items being supplied along with software bill of material (SBoM). The inventory shall include version & firmware number for understanding of applicable vulnerabilities from publicly disclosed vulnerabilities databases and shall take required action. | Please include Inventory management tool in software BOM | Bidder to comply technical specification |
|  | Volume II Part-A, , Section-4, Clause no-4.3, Patch Management | The contractor shall upgrade the various applications delivered under the project through patch management and upgrade to make it compliant with IEC standards as envisaged under the specification during the entire contract period including extension of contract, if any. Updated patches shall be applied to the system within the timelines given below. Non-compliance will be considered under Severity-2. | Our understating from this para is for the patches only. Version change of the application change is not possible as it may depends on the OS version. | Refer earlier issued Amendment – IV to technical specification. Bidders to comply Technical Specification |
|  | Volume II Part-A, , Section-4, Clause no-4.3, Patch Management | Anti-virus , Firewall, HIPS ,HIDS & Network IPS signatures - Daily | It depends on the release of the patch from the OEM. Normally AV release the definition updates on daily basis but IDS/IPS etc. doesn't deliver the daily patches. | Bidder to comply technical specification. |
|  | Volume II Part-A, , Section-4, Table 4.5, Responsibility Matrix | 2.1 Report problem and assist with problem identification. 3.3 Restore or reinstall software from back-ups. 4.4 Restore operation of repaired/replaced equipment 5.0 HARDWARE SPARE PARTS 8.1 - 8.6 Patch/Signature/Update/firmware Updates etc. | 21. Problem reporting to be done by Owner. We have standard support for maintenance for S2, S3 and S4 and 24x7 for S1 issues. 3.3 We need assistance as it also depend on the Online system as well. 4.4 same as 3.3 5.0 Spares will be in Owners premises, so security has to be prime responsibility of the Owner and during replacement assistance is needed. 8.1 - 8.6 Owners assistance is required , as it requires downtime. | Bidder to comply technical specification. |
|  | Volume II Part-B, , Section-4, Clause no-4.2.2, Operating System | The operating system of all the equipment of SCADA/EMS & REMC system including network equipment shall be latest version released preferably up to six (06) months prior to FAT. | It depends on last release and tested with application software | Bidder to comply technical specification. |
|  | Volume II Part-B, , Section-4, Clause no- 4.2.2, Operating System | In case of end-of-life, obsolescence and end-of-support of the operating system, Anti-Virus or any other software delivered in the project, the contractor should provide latest version and license of operating system, Anti-Virus or any other software delivered in the project at its own cost. If changes of software and operating system require replacement of hardware, then, hardware shall also be replaced by the contractor without any cost implication to owner. Replacement shall be of either the same or higher configuration keeping required performance specified under the contract and from same OEMs. | IT hardware and software life cycle of 3 to 5 years. In case of EOS/EOL, we can maintain the delivered system. | Bidder to comply technical specification. |
|  | Volume II Part-B, , Section-4, Clause no- 4.3, Time and Calendar Feature | The internal clocks of all Servers and workstation consoles shall be automatically synchronized within the accuracy of +/-100 milliseconds of synchronized time on NTP or PTP protocol. | For local network NTP/SNTP protocol is used. PTP is required in where distance is very long e.g. in telecom network. We will use NTP/SNTP. | Bidders to comply Technical Specification |
|  | Volume II Part-B, , Section-4, Clause no- 4.6.10, Development System (DDS or PDS) as a test bench | This system shall also be used as a Test bench for Cyber security and shall accordingly be equipped with firewall, antivirus and enable mode wherein threat scenarios can be tested with configured security elements before implementing on the main/production system. | 1) Development System cannot be used for the testing of the Signatures/updates of the firewall. Firewall signature done not any testing. 2)It is not possible to simulate the Threat scenarios in the SCADA/REMC environment. Development system can be used only for the testing of signatures/definition/patch updates so as we can check any update is not impacting the running application/os. | Refer earlier issued Amendment No-IV to technical specification. Bidders to comply Technical Specification |
|  | Volume II Part-B, , Section-4, Clause no- 4.8.3, On-Line Monitoring Diagnostics | Designated backup server(s) and associated auxiliary memories shall be automatically tested for proper operation to ensure they are ready if needed for a failover contingency. Any failure to perform diagnostic functions correctly shall cause an alarm to be issued. | Online backup is automated process but restoration cannot be automated, it requires manual intervention with respective system in down condition e.g. if we have to restore the backup of IC2 in that case no other machine with the name of IC2 should be live. A new bare server will be placed in place of IC2 and then backup will be restored. Please elaborate , if there is any other understating. | Bidders to comply Technical Specification. |
|  | Volume II Part-B, , Section-5, Clause no- 5.2, Technical Requirements for Hardware | The Bidder shall ensure that the product/technologies/services quoted under this project are latest and it shall have more than 7 years of life initially (i.e.., “End of Support Life” for minimum 7 years, from date of the bid submission) which shall be extended during entire contract period (including extension of contract, if any) by extending the OEM warranty or replacing the product.). | We request to replace the clause with following clause: Contractor shall maintain Support from OEM/OEM stockiest/Partners/3rd parties for Maintenance period. Any upgrade or replacement shall not be in contractors scope. | Refer earlier issued Amendment – IV to technical specification. Bidders to comply Technical Specification. |
|  | Volume II Part-B, , Section-5, Clause no- 5.19, Provision of file transfer between OT and IT | Provision must be kept for secure file and data exchange between IT and OT system and between other OT systems. Keeping all security measures and guidelines, all necessary hardware & Software shall be provisioned by the contractor accordingly. | Please define the BOM. | Bidders to comply Technical Specification. |
|  | Volume II Part-B, Appendix-G, Table no. 1, BOQ for Ladakh SLDC cum REMC - Control Center | Identity Management Software and patch management software | Identity and patch management are the two different softwares. And to be deployed in different zones as per the cyber security requirements. | Refer earlier issued Amendment-IV to the technical specification. Bidders to comply Technical Specification |
|  | Volume II Part-B, Appendix-G, Table no. 1, BOQ for Ladakh SLDC cum REMC - Control Center | ----- | There is no line item for white listing tool | Refer Section –9, Clause 9.2.6 of technical specification. Bidders to comply Technical Specification |
|  | Volume II Part-B, Appendix-G, Table no. 1, BOQ for Ladakh SLDC cum REMC - Control Center | 13. Storage System | There is no line item for SAN Switches | Refer earlier issued Amendment – IV to technical specification. Bidders to comply Technical Specification |
|  | Volume II Part-B, Appendix-G, Table no. 1, BOQ for Ladakh SLDC cum REMC - Control Center | 16. Cyber Security Appliances | There is no line item for ATP (Sandboxing) | Refer earlier issued Amendment – IV to technical specification. Bidders to comply Technical Specification |
|  | Volume II ,Part- B, Section-2, Clause no.- 2.2, Power System Analysis | The principal PSA activities of Control Centre are summarized as follows: e. Listing all Circuit Breaker and Isolator which can be filtered voltage level/ station/area-wise in case the telemetered value is more than the threshold limit. On click, the user shall be able to navigate to corresponding single line diagram of sub-station containing the Circuit Breaker/Isolator. | Listing all Circuit Breaker and Isolator which can be filtered station/areawide Not Clear " in case the telemetered value is more than the threshold limit." | The threshold limit here refers to the limit of the difference between telemetered value and state estimated value. Bidders to comply Technical Specification. |
|  | Volume II ,Part- B, Section-2, Clause no. - 2.2.8.2, State Estimation Characteristics | f) …...................................... It shall be possible for the programmer to disable and enable the setting of the quality code in the real-time data base on a global basis.............................. | if quality code disables in real-time in SCADA then what quality code be considered in SE? | Bidders to comply Technical Specification. |
|  | Volume II ,Part- B, Section-2, Clause no.-2.2.9, Bus Load Forecast | * Change the filter parameters used by the smoothing process | What would be filter parameters in smoothing process? | This information shall be provided during detailed Engg. Bidders to comply Technical Specification. |
|  | Volume II ,Part- B, Section-2, Clause no.- 2.2.11.1, Contingency Cases: Following Features | d) In the event of generating unit outages or outages that cause a loss of load the change in generation/load shall be assigned to all remaining generating units/loads in proportion to its maximum capacity in the affected electrical island. | Understanding: Generation will be assigned to remaining unit but load cannot assign to other | Confirmed. For loss of Load, the generations shall be proportionately reduced as per the maximum capacity of generators in the affected island. Bidders to comply Technical Specification. |
|  | Volume II ,Part- B, Section-2, Clause no.- 2.2.12.3, OPF Output Data | An interchange summary shall be provided showing desired and calculated net interchange, Total losses, generation, load, tie-line flows, bus mismatch, maximum bus mismatch, and spinning reserve. | Understanding: Calculation of Spinning reserve is not a part of the network applications. It will be calculated under AGC functions. | Bidder can calculate the spinning reserve in any of the applications but the Interchange summary shall display the required data. Bidders to comply Technical Specification. |
|  | Volume II ,Part- B, Section-3, Clause no.- 3.8, Documentation | For this a web based “Document Management System” (DMS) software shall be supplied and installed at the owner’s facility by the contractor along with minimum 50 number of client access licenses. DMS shall have multiuser capability with user role and privileged management. DMS shall have complete capability of tracking the documents version, ownership and editing. This DMS shall be used as central document repository for the entire lifecycle of the Project for easy managing and referencing of the project documentation. | We understand that the DMS should be implemented first at Owner's premises after awarding of the contract as Documentation and Design is the first part of a Project. Please elaborate. | The document management system can be implemented in the beginning or after delivery of the system. Bidder to comply technical specification |
|  | Volume II ,Part- B, Section-3, Clause no.- 3.8, Documentation |  | Is the document approval through DMS is in time bound manner? E.g.: The submission by Contractor and responses from Employer are bound to be with in some time apart from Appendix E Row Number 3 , pdf page number 143. Please elaborate | Bidder to comply technical specification. |
|  | Volume II ,Part- B, Section-1, Clause no.- 1.16, Main and Backup Control Center Operational Philosophy | In case user required to sync data between main and backup control center historian for a selected period, it shall be possible. | Please explain with a situation where this functionality will be required for better understanding of the requirement. | Bidder to comply technical specification. |
|  | Volume II, Part- B, Section-1, Clause no.- 1.1.1.8, CFE Requirement | CFE server should be able to operate in listening mode (able to receive signal without request). | Please elaborate the exact Requirement | Refer earlier issued Amendment-IV to the technical specification. Bidders to comply Technical Specification |
|  | Volume II ,Part- B, Section-1, Clause no.- 4.4.2, Network Services |  | What's is (h) LAN Global Naming Facilities? Please clarify. | It refer to assigning naming facility to devices over LAN in the control center. Bidders to comply Technical Specification |
|  | Volume II ,Part- B, Section-1, Clause no.- 8.3.3, Web Applications & Web Historian | There shall be no limitation on Sized to support 500 concurrent external clients/users for providing access to real-time and Historical data. There shall be no limitation on number of users. - This statement is contradictory. The licenses will be calculated according to the number of users. We understand that web user count shall be considered as 500. | Please clarify if the understanding is correct or not. | Bidders to comply Technical Specification |
|  | Volume II ,Part- B, Section-1, Clause no.- 9.2.9, Database Development System (DDS) as a test bench for Cyber Security Requirement | Database Development System (DDS) as a test bench for Cyber Security Requirement | How this test bench can be used for cyber security requirement. How the threat scenarios can be created to test? | Bidders to comply Technical Specification |