| Sl. No | Clause No | Existing clause | Amended clause |
| --- | --- | --- | --- |
|  | Vol-II Part- A, | CONTENTS Part-A APPENDIX K METEROLOGICAL DATA | CONTENTS Replace with Part-A APPENDIX K METEROLOGICAL DATA APPENDIX L Type Test Validity |
|  | Vol. II Part-A, Section – 1, Clause no. –1.11 | Overview of the Proposed Systems ……..If there is any conflicting requirement, the applicable requirement shall be decided by the employer and that shall be binding on the Supplier….. | Overview of the Proposed Systems Replace with ………If there is any conflict in requirements specified in different sections of technical specification, the applicable requirement shall be decided by the employer and that shall be binding on the contractor….. |
|  | Vol. II Part-A, Section – 1, Clause no. – 1.12 | Scope of Work a)……Both main and backup control centers shall work in active-active mode and in case of failure of main control center, backup shall come in role of main without any manual interruption (except commands & signals). e) …..The integration of new RTUs at the Control center end shall also be in the scope of the Contractor. Further, future bay integration shall not be treated as a new RTU integration during AMC period, and any bay extension during AMC shall be in the scope of the contractor without any commercial implication to the Owner. | Scope of Work Replace with - …..Both Main and Backup control centers shall work in active-active mode and in case of failure of Main control center, Backup shall come in role of Main without any manual interruption (except for taking over Control authority). - …..The integration of new RTUs at the Control center end shall also be in the scope of the Contractor. The scope of works under integration of RTU with control centre is inclusive of work of integration (including database and display) with DCPC/Terminal Server also, if any. Further, future bay integration at Control Center end shall not be treated as a new RTU integration during AMC period, and any bay extension at Control Center end during AMC shall be in the scope of the contractor without any commercial implication to the Owner. The future bay integration during AMC period at substation end shall be in the scope of contractor as mentioned in Bill of Quantity Appendix-G. |
|  | Vol. II, Part-A, Section-1, Clause- 1.12, Scope of Work | Scope of Work I) Development of complete Database displays and reports to display SCADA and RE related information with analysis and report generation facility. The text available in displays and reports shall have support of fonts for English and Hindi. Contractor shall develop and provide tools to convert CIM files for different versions based on customized CIM-profiles in the files used by vendors system. The displays shall comply with the Display Building guidelines as per Appendix-K, Part-B of Vol-II. | Scope of Work Replace with - Development of complete Database displays and reports to display SCADA and RE related information with analysis and report generation facility. The text available in SCADA displays and reports shall have support of fonts for English and Hindi. Contractor shall develop and provide tools to convert CIM files for different versions based on customized CIM-profiles in the files used by vendors system. The displays shall comply with the Display Building guidelines IS 18058: 2023 and as per contract document. |
|  | Vol. II, Part-A, Section-1, Clause- 1.12, Scope of Work | bb) During entire contract period (including extension of contract, if any), if OEM discontinues/declares end of support to any item supplied (Software/Hardware/Security Solution/OS) under the contract, causing security vulnerability, the contractor has to replace such hardware, software (or both, depending on software or hardware dependencies on each-other) without any additional cost to the Owner. Replacement shall be of either same or higher configuration. ii) C10 Capacity test of the Supplied Battery banks shall be done periodically (yearly), to determine whether the rating of battery is holding up using capacity test. If the battery capacity is less than 80% of its design value in any of the cases, the battery shall have to be replaced by contractor during entire period of contract (including extension of contract, if any) without any cost implications to owner. If number of cells replaced(cumulative) in battery bank exceeds more than 25% of total battery bank in any of the cases during entire period of contract, then contractor shall replace that entire battery bank without any additional cost to the Owner. Also, Refer Section 3 & Section 8, PART C of TS. jj) Necessary support for providing Security Logs from Firewalls & Other Cyber Security Devices to NCIIPC and integration of supplied SLDC cum REMC system cyber security systems with the future Security Operations Center (SOC) and Security Orchestration, Automation and Response (SOAR) systems to be procured by the Owner. | Replace with bb) During entire contract period, if OEM discontinues or declares end of support/end-of-life, whichever is later for any item supplied (Software/Hardware/Security Solution/OS) under the contract, the contractor has to replace such hardware, software (or both, depending on software or hardware dependencies on each-other) as per provisions mentioned under Clause 1.20, Section-1, Part-A of technical specifications along with other scope of works specified under the contract . The replacement due to EOL and EOS of Hardware/software shall be required if it has become either non-functional or the patches/updates have been discontinued from the OEM. ii) Capacity test @ C10 shall be done periodically (yearly), for assessment of health of the battery bank (UPS & DCPS wherever applicable) to determine charge holding capacity of battery bank. The conditions for batteries/battery bank replacement for one-year DLP and up to 6 years AMC period is as follows: - Irrespective of the design/expected life of the supplied battery banks, If the battery bank capacity is less than 80% of its design value at end cell voltage of 1.75V/cell in any of the cases, Replacement of faulty battery cells/battery banks shall be in the scope of the contractor, without any cost implication to the Owner. - If the number of cells replaced (cumulative) in the supplied battery bank exceeds more than 25% of total batteries, then contractor shall replace that entire battery bank without any additional cost implication to the Owner. Also, Refer Section 3 & Section 8 of PART C and Section 2 of PART D technical specification. jj) Necessary support for providing Logs from firewalls/other cyber security devices through SIEM to NCIIPC and for integration of entire SIEM logs with the future Security Operations Center (SOC) and Security Orchestration, Automation and Response (SOAR) systems to be procured by Owner(s). |
|  | Vol. II, Part-A, Section-1, Clause- 1.12, Scope of Work | Inserted new clause | mm) The SCADA/EMS system sizing shall be as per the appendix F. The Owner at its own discretion may allocate any unutilized quantum of analog points to status points and status points to analog points as per their requirement, within the overall limit of number of licensed points configured for the SLDC. |
|  | Vol. II, Part-A, Section-1, Clause- 1.12, Scope of Work | Note: The contract period includes the period from award to completion of AMC period, including extension of AMC period, if any. | Note:- The entire contract period includes the period from award to completion of AMC period (one year DLP and 6 year AMC). In technical specification, wherever “including extension of AMC period , if any”, is written, shall be read as “not applicable”. The extension referred here is after completion of AMC period |
|  | Vol. II, Part-A, Section-1, Clause- 1.13 | General Requirements …..The supplied system (hardware & software) shall comply with cyber security standard relevant clause of the Central Electricity Authority (Technical Standards for Communication System in Power System Operations) Regulations, 2020, Indian or International Security Standards e.g., IT and IT related elements against ISO/IEC 15408 standards, for Information Security Management System against ISO 27000 series Standards, IEC 62443 for OT Network Security, IEC 62351. The procurement & bid proposal shall be compliant with these standards. The contractor shall ensure compliance with all the statutory guidelines issued during the entire period of the contract by all the regulatory bodies. Before supplying, the contractor shall certify the items for relevant cyber security standards…. | General Requirements Replace with ….The supplied system (hardware & software) shall comply with cyber security standard relevant clause of the Central Electricity Authority (Technical Standards for Communication System in Power System Operations) Regulations, 2020, Indian or International Security Standards e.g., IT and IT related elements against ISO/IEC 15408 standards, for Information Security Management System against ISO 27000 series Standards, IEC 62443 (IEC 62443-3-3 and IEC 62443-4-1) for OT Network Security, IEC 62351. The procurement & bid proposal shall be compliant with these standards. The contractor shall ensure compliance with all the statutory guidelines issued during the entire period of the contract by all the regulatory bodies as per the provisions mentioned under Clause 1.20, Section 1, PART A of technical specifications along-with other scope of works specified under the contract. Before supplying, the contractor shall certify the items for relevant cyber security standards…. |
|  | Vol. II, Part-A, Section-1, Clause- 1.13 | General Requirements …..The contractor must ensure during the entire contract period, if any supplied item (software and hardware including third party solutions, services) under the contract is discontinued, ends support, is end-of-life, for all such items the contractor must replace and provide the software, hardware, solution, service as per scope of technical specification without any additional cost to Employer/Owner…… | General Requirements Replace with ….The contractor has to ensure maintenance and services of entire system supplied under the contract during the entire period of contract as per provisions mentioned under Clause 1.20, Section 1, PART A of technical specifications along-with other scope of works specified under the contract. …. |
|  | Vol. II, Part-A, Section-1, Clause- 1.14.2, Contractor’s Responsibilities and Obligations | p) Contractor shall provide end to end web-based data exchange solution between SLDC, Forecast Service Providers, Weather service provider or any other required place including internet services from two different service providers to ensure smooth and reliable functioning of all tools (SCADA, forecasting and scheduling tool etc.). The cost towards the same including internet services shall be under the scope of the Contractor. | Replace with p) Contractor shall provide end to end web-based data exchange solution between SLDC, Forecast Service Providers, Weather service provider. The contractor has to provide internet services during FAT at his own cost. Internet services at site for the same shall be provided by the Owner. |
|  | Vol. II, Part-A, Section-1, Clause- 1.14.2 | Contractor’s Responsibilities and Obligations z) Provide Type Test report to the Employer/Owner and if required, conduct type test. The contractor shall submit type test reports for all the equipment as per specification for review & approval by the Employer within 30 days of the Contract Award. The type test reports submitted shall be of the tests conducted within last five (5) years prior to the date of NOA. In case the test reports are older than five (5) years ago on the date of NOA or the type test reports do not meet the specification requirement, the contractor shall carry out the type testing at no additional cost to the Employer/Owner. mm) All provisions and orders of GOI, DPIIT, MoP, DoT, Meity etc. or any other Nodal Ministry have to be mandatorily complied by the contractor with subsequent amendments in the entire period of contract (including extension of contract, if any)… | Contractor’s Responsibilities and Obligations Replace with z) Provide Type Test report to the Employer/Owner and if required, conduct type test. The requirement of type test is mentioned at Part-A, Section-3, Clause no. – 3.7.8 and refer Appendix L in Annexure A mm) All provisions and orders of DPIIT, MoP, DoT, Meity or any other Nodal Ministry have to be mandatorily complied by the contractor with subsequent amendments during entire contract period as per the provisions mentioned under Clause 1.20, Section 1, PART A of technical specifications along-with other scope of works specified under the contract... New Clause Added nn) The contractor shall provide Email Interface and SMS Interface application and shall be responsible for integrating with the SMS and EMAIL services provided by the Owner. |
|  | Vol. II, Part-A, Section-1, Clause- 1.14.4 | Owner’s Responsibilities and Obligations | Owner’s Responsibilities and Obligations Inserted p) Providing internet connectivity of required bandwidth at SLDC cum REMC Control Center (Both Main and Backup CC) and public IP for remote diagnostic before commencement of SAT. q) SMS Service shall be provided by the owner preferably from govt. agencies such as NIC etc. r) Adequate Storage Space at site for supply items including spare parts. s) Proper environmental conditions for equipment’s supplied under this project at site for their smooth functioning. |
|  | Vol. II, Part-A, Section-1, Clause- 1.16 | Main and Backup Control Center Operational Philosophy …The takeover of Main Control Center functions by Backup Control Center shall not require manual intervention and the same shall be configurable…. | Main and Backup Control Center Operational Philosophy Replace with …The takeover of Main Control Center functions by Backup Control Center shall not require manual intervention except for taking over Control authority |
|  | Vol. II, Part-A, Section-1, Clause- 1.17, General Technical Requirements | b. Commercial Off-The-Shelf (COTS) product The contractor shall offer Commercial Off-The-Shelf (COTS) as mentioned in BOQ. The COTs product means a product which is independently commercially available in the market. The contractor shall provide at least three references in Govt/Public Listed companies where the product has been supplied as an independent product and the solution shall be in successful operation for at least one year as on the date of NOA. | b. Commercial Off-The-Shelf (COTS) product The contractor shall offer Commercial Off-The-Shelf (COTS) as mentioned in BOQ. The COTs product means a product which is independently commercially available in the market. The contractor shall provide at least three references in Govt/Public Listed companies where the product has been supplied as an independent product and the solution shall be in successful operation for at least one year as on the date of NOA. However, in case of historian which are categorized as Commercial Off-The-Shelf (COTS) products in the technical specifications and Bill of Quantities (BoQ), the contractor can supply their own product subject to submission of at least three references in Govt/Public Listed companies and solution shall be in successful operation for at least one year as on the date of NOA. |
|  | Vol. II, Part-A, Section-1, Clause- 1.17, General Technical Requirements | d. Energy Accounting & Billing Software The contractor shall offer proposed Energy Accounting & Billing software (EABS) from OEMs who have supplied and implemented one project/system with similar type of software for Energy Scheduling or Energy Accounting or Billing Software, designed in line with SAMAST guideline for any RLDC/SLDC. The EABS shall be in operation for at least one year as on the date of NOA. | Replace with d. Energy Accounting & Billing Software The contractor shall offer proposed Energy Accounting & Billing software (EABS) from OEMs who have supplied and which is implemented in one project/system with similar type of software for Energy Scheduling or Energy Accounting or Billing Software, designed in line with SAMAST guideline for any RLDC/SLDC as on date of NOA. |
|  | Vol. II Part-A, Section – 1, Clause no. – 1.19 | Applicable Standards ……….. All latest guidelines issued by regulatory authorities such as MoP CEA, NCIIPC, MEITY etc. shall be complied by the bidders for the offered products (hardware and software) under the project. These should be established and tested product (hardware and software) considering criticality of the system. In this regard, bidder has to comply with order issued by MoP No. 25-11/6/2018-PG dated 2.7.2020 (with all amendments) and CEA Cyber Security in Power System Guidelines, 2021 (with all amendments) throughout the period of contract……… | Applicable Standards Replace with ……….. All latest guidelines issued by regulatory authorities such as MoP, CEA, NCIIPC, MEITY etc. shall be complied by the contractor for the offered products (hardware and software) under the project. These should be established and tested product (hardware and software) considering criticality of the system. In this regard, contractor has to comply with order issued by MoP No. 25-11/6/2018-PG dated 2.7.2020 (with all amendments) and CEA Cyber Security in Power System Guidelines, 2021 (with all amendments) throughout the period of contract as per the provisions mentioned under Clause 1.20, Section 1, PART A of technical specifications along-with other scope of works specified under the contract….. |
|  | Vol. II Part-A, Section-1, Clause No.-1.20 | New Clause added Maintenance and Support Services Scope | New Clause added Maintenance and Support Services Scope Inserted Maintenance and Support Services Scope Clause attached at Annexure-A. |
|  | Vol. II Part-A, Section – 3, Clause no. – 3.7.8 | Type Testing ….. - The Contractor shall submit, within 30 days of the Contract Award, copies of test reports and certificates for all the Type Tests that are specified in the specifications and that have previously been performed. The type test reports submitted shall be of the tests conducted within the last five (5) years prior to the date of NOA. In case the test reports are older than five (5) years ago on the date of NOA or the type test reports are not meeting the specification requirement, the contractor shall carry out the type testing at no additional cost to the Employer/Owner…… | Type Testing ….. Replace with - The Contractor shall submit, within 30 days of Contract Award, copies of test reports and certificates for all of the Type Tests that are specified in the specifications and that have previously been performed. The type test reports submitted shall be of the tests conducted within the duration specified in the Table no. 1 of Part-A, Appendix-L (attached at Annexure-A) prior to the date of NOA. In case the test reports are older than specified duration on the date of NOA or the type test reports are not meeting the specification requirement, the contractor shall carry out the type testing at no additional cost to the Employer/owner….. |
|  | Vol. II Part-A, Section – 4, Clause no. – 4.2, Maintenance support | Maintenance support The Owner at their own discretion may extend the duration of maintenance period for up to 2 years based on the same rates, same terms and conditions of the contract. | Maintenance support Para Deleted |
|  | Vol. II Part-A, Section – 4, Clause no. – 4.2, Maintenance support | Table 4.1 Maintenance support and Availability requirements All systems & subsystem such as SCADA, EMS, REMC Applications, Energy Accounting & Billing Application, ICCP, Web System, Historian, NMS, VPS, Cyber security system etc. supplied in this project | Table 4.1 Maintenance support and Availability requirements Replace with All systems & subsystem such as SCADA, EMS, REMC Applications, Energy Accounting & Billing Application, ICCP, Web System, Historian, NMS, VPS, Video Conferencing System, Cyber security system etc. supplied in this project |
|  | Vol. II Part-A, Section – 4, Clause no. – 4.2, Maintenance support | Maintenance support ....For any addition (e.g. integration of new RTUs or new control center) during maintenance period (as identified in the BoQ), the contractor shall provide all the services at control center end without any additional cost during entire period of the contract including extension (if any)……. | Maintenance support Replace with ….For any addition (e.g. integration of new RTUs or integration of new control center) during maintenance period as per BoQ |
|  | Vol. II Part-A, Section – 4, Clause no. – 4.2, Maintenance support | Maintenance support For all third-party equipment (Hardware & Software), Contractor shall have back to back support and warranty for all maintenance services & availability of Security Patches along with supply of spare with appropriate response time from OEM/OEM Authorized representatives and these Back-to-Back contracts will be shared with owner before start of defect liability period. The contractor shall be responsible for coordination with the OEM on all matters related to that equipment & software. In case, any hardware / software / equipment / component items of the systems supplied under the contract shall reach its End-of-Life (EOL) or End-of-Support (EOS) whichever is earlier, and is causing security vulnerability, then the contractor shall replace such item with new Hardware or Software without any financial implication to owner. The Contractor shall be responsible for meeting the overall response times and availability requirements specified in the Specification. The contractor shall also be responsible for hardware & software replacement and upgradation without any additional cost to the Owner in case OEM declares end of life, end of support and obsolescence for the product. | Maintenance support Replace with …..For all third-party equipment (Hardware & Software), Contractor shall have back to back support and warranty for all maintenance services & availability of Security Patches along with supply of spare with appropriate response time from OEM/OEM Authorized representatives and these Back-to-Back contracts will be shared with owner before start of defect liability period. Scope of contractor shall be as per the provisions mentioned under Clause 1.20, Section 1, PART A of technical specifications along-with other scope of works specified under the contract. |
|  | Vol. II Part-A, Section – 4, Clause no. – 4.2, Maintenance support | g) OEM Back-to-back Support: i. All the supplied system shall be under OEM (Hardware and Software) warranty & support till the completion of the entire contract period (including extension of contract, if any). | f. OEM back-to back support Replace with i. All the supplied system shall be under OEM (Hardware and Software) warranty & support as per the provisions mentioned under Clause 1.20, Section 1, PART A of technical specifications along-with other scope of works specified under the contract. |
|  | Vol. II Part-A, Section – 4, Clause no. – 4.2, Maintenance support | g) OEM back-to back support ii. During entire contract period (including extension of contract, if any), if OEM discontinues, declared ends support to any item supplied (software, hardware, security solution, OS) under the contract, contractor must replace such hardware, software (or both, depending on software or hardware dependencies on each-other) without any additional cost to Owner. Replacement shall be of either the same or higher configuration keeping required performance specified under the contract. | g. OEM back-to back support Replace with ii. During entire contract period, If OEM discontinues / declared end of support/end-of-life, whichever is later for to any item supplied (software/hardware/security solution/OS) under the contract, contractor has to replace such hardware, software (or both, depending on software or hardware dependencies on each-other) without any additional cost to Owner as per the provisions mentioned under Clause 1.20, Section 1, PART A of technical specifications along-with other scope of works specified under the contract. Replacement shall be of either the same or higher configuration keeping required performance specified under the contract. |
|  | Vol. II Part-A, Section – 4, Clause no. – 4.2, Maintenance support | g) OEM back-to back support iv. C10 Capacity test shall be done periodically (yearly), to determine whether the rating of battery is holding up using capacity test. If the battery capacity is less than 80% of its design value in any of the cases, the battery shall have to be replaced by contractor during entire period of contract (including extension of contract, if any) without any cost implications to owner. If number of cells replaced(cumulative) in battery bank exceeds more than 25% of total battery bank in any of the cases during entire period of contract (including extension of contract, if any), then contractor shall replace that entire battery bank without any additional cost to the Owner. Also, Refer Section 3 & Section 8 PART C of TS. | g) OEM back-to back support Replace with iv. Capacity test @ C10 shall be done periodically (yearly), for assessment of health of the battery bank to determine charge holding capacity of battery bank. The conditions for batteries/battery bank replacement shall be as per the provisions mentioned under Clause 1.12, Section 1, PART A of technical specifications along-with other scope of works specified under the contract. |
|  | Vol. II, Part-A, Section-4, Clause- 4.3, Preventive Maintenance Activity | f) Addition and modification of database and displays, report generation, configuration and Database sizing activities including on-lining as detailed in the specification for all applications etc. and other day-to-day operational activities would primarily be the responsibility of Contractor. | Replace with f) Addition and modification of database and displays, report generation, configuration and Database sizing activities including on-lining as detailed in the specification for all applications etc. would primarily be the responsibility of Contractor. |
|  | Vol. II, Part-A, Section-4, Clause- 4.3, Preventive Maintenance Activity | n) Routine works like database building, addition of analog and status points, report generation etc. and other such day-to-day operational activity would primarily be the responsibility of Contractor and the same shall be completed in close coordination with Owner. | Replace with n) Routine works like database building, addition of analog and status points, report generation etc. would primarily be the responsibility of Contractor and the same shall be completed in close coordination with Owner. |
|  | Vol. II Part-A, Section – 4, Clause no. –4.3.3.3 | Cyber security System monitoring and Monitoring and compliance manager for Critical Infrastructure Protection …… All advisories given by CERT-In / CERT-GO/NCIIPC /CEA/ Meity etc. shall be complied with in the timely manner during entire contract period including extension of contract, if any….. | Replace with Cyber security System monitoring and compliance manager for Critical Infrastructure Protection …. All advisories given by CERT-In / CERT-GO/NCIIPC /CEA/ Meity etc. shall be complied with in the timely manner during entire contract period as per the provisions mentioned under Clause 1.20, Section 1, PART A of technical specifications along-with other scope of works specified under the contract. ….. |
|  | Vol. II Part-A, Section – 4, Clause no. –4.3.5, Patch Management | The contractor shall upgrade the various applications delivered under the project through patch management and upgrade to make it compliant with IEC standards as envisaged under the specification during entire contract period including extension of contract, if any. Updated patches shall be applied in the system within the timelines given below. Non-compliance will be considered under Severity-2. | Replace with The contractor shall update patches including security patches in the various applications/solutions delivered under the project through patch management solution and update to make it compliant with IEC 62443 during entire contract period, if any. Updated patches shall be applied in the system within the timelines given below. Non-compliance will be considered under Severity-2. However, if patch update support to any supplied solution gets discontinued by the OEM, the upgradation/replacement of the same shall be done by the contractor without any additional cost to owner. |
|  | Vol-II Part- A, Section-4, Para 1 of Clause- 4.3.9 | Preventive and Break down maintenance of the supplied DCPS & Battery System 19. C-3 discharge test on batteries once a year during 3rd quarterly visit. | Preventive and Break down maintenance of the supplied DCPS & Battery System Replace with 19. Yearly C-10 discharge test on batteries |
|  | Vol-II Part- A, Section-4, Para 1 of Clause- 4.3.10 | Furniture The Furniture and fixtures supplied with the system shall have comprehensive maintenance contract with OEM. Any spares…....……. | Furniture Replace with The Motorized Furniture and fixtures supplied under this contract shall have comprehensive maintenance contract with OEM and for non-motorized furniture supplied under this contract, contractor shall ensure maintenance by themselves or through back-to-back OEM/3rd party support. Any spares….... |
|  | Vol-II Part- A, Section 4, Clause 4.4 | Spare Inventory ……. In case mandatory spares (Table 4.2) have been used in the system, the replenishment of such spare shall be done within 45 calendar days (for UPS Spares it shall be 15 calendar days), otherwise it will be considered as non-availability as per Severity-2. ….. | Spare Inventory …… In case mandatory spares (as specified in Part-B, Appendix-G, Bill of Quantity) have been used in the system, the replenishment of such spare shall be done within 45 calendar days otherwise it will be considered as non-availability as per Severity-2. |
|  | Vol-II Part- A, Section 4, Clause 4.5 | Integration of new equipment and or control center The numbers specified in BOQ are indicative only. The actual number of RTUs and CCs integration during AMC period may vary. Payment to the contractor shall be based on the unit rate and actual number of RTUs or CCs integrated. | Integration of new equipment and or control center Replace with The numbers specified in BOQ for Services (Integration and supply) and Annual Maintenance Contract including DLP period are tentative only. Actual numbers of services may vary during Services (Integration and supply) and AMC (including DLP) period. Payment to the contractor shall be released based on the unit rate and actual number of services availed. |
|  | Vol. II Part-A, Section – 4, Clause no. – 4.6.1.2, Severity-2 | c) Failure of any redundant system component affecting the critical redundancy like loss of any one Application Processor, Router and CFE would also be included in this category. | Replace with c) Failure of any redundant system component affecting the critical redundancy like loss of any one Application Processor, Firewall, Router, Switch and CFE would also be included in this category. |
|  | Vol. II Part-A, Section – 4, Clause no. – 4.6.1.2, Severity-2 |  | Inserted t) Failure of complete DCPS or its battery bank shall be considered under severity level 2. In case of failure of DCPS or its battery bank, a maximum time of 48 hrs for arrangement of manpower/spares and travelling shall be provided in the worst case. The failure of redundant rectifier modules or battery cells of DCPS, not impacting the functioning, shall be treated under severity-3. |
|  | Vol. II Part-A, Section – 4, Clause no. – 4.6.1.3, Severity-3 | Also, Non-functioning of video conferencing system shall be considered under severity level 3. | Replace with The non-functioning of Video Conferencing System shall be treated under severity-3. In case of failure of Video Conferencing System, a maximum time of 48 hrs for arrangement of manpower/spares and travelling shall be provided in the worst case. Failure to replace weak battery cells identified in C-10 capacity test for UPS and DCPS batteries, within a week time, not impacting the functioning of entire UPS system, shall be also treated under Severity-3. |
|  | Vol. II Part-A, Section – 4, Clause no. –4.11 | Detailed Scope of work during the entire Contract Period viii. A Technical upgrade of the installation to the new version (wherever applicable), as and when required, shall be done by the Contractor. Any version upgrade (in version) of the software , tool, appliance by Contractor to be done after taking prior approval of Owner and after submitting impact assessment of such upgrade at no additional cost to Owner. | Detailed Scope of work during the entire Contract Period Replace with viii. A Technical upgrade of the installation (wherever applicable), as and when required, shall be done by the Contractor. If patch update support to any solution gets discontinued by the OEM, then upgrade (in version)/replacement of the software, tool, appliance by Contractor to be done after taking prior approval of Owner and after submitting impact assessment of such upgrade at no additional cost to Owner. Software embedded with the SCADA/EMS Application software shall not be treated as 3rd party software for this version upgrade requirement subject to security vulnerabilities. |
|  | Vol. II Part-A, Section-4, Clause No.- 4.11 | Detailed Scope of work during Warranty and AMC Period xi) Provide a single-point-of-contact for the resolution of Hardware related problems or to request an equipment upgrade or consultation. If the Hardware supplied by the Contractor is to be replaced permanently, then the Contractor shall replace the equipment of same Make, Model, configuration or of higher configuration. | Detailed Scope of work during Warranty and AMC Period Replace with xi) Provide a single-point-of-contact for the resolution of Hardware related problems or to request an equipment upgrade or consultation. If the Hardware supplied by the Contractor is to be replaced permanently, then the Contractor shall replace the equipment of same configuration or of higher configuration as per the provisions mentioned under Clause 1.20, Section 1, PART A of technical specifications along-with other scope of works specified under the contract. |
|  | Vol. II Part-A, Section-4, Clause-4.12.1 | Introduction …..If any special testing equipment/s is/are required for testing and repair of the system, same shall be arranged by the contractor. | Introduction Replace with …..If any special testing equipment/s is/are required for testing and repair of the system, same shall be arranged by the contractor with no additional cost to owner. |
|  | Vol. II Part-A, Section – 4, Clause no. – 4.12.4, (c) | C. Integration of new bays & reconfiguration The scope of work under Integration of new bays & reconfiguration work includes- …… Further, integration of new Bays shall not be treated as new RTU integration during AMC period, and any such bay extension during AMC shall be in the scope of the contractor without any commercial implication to the Owner. | C. Integration of new bays & reconfiguration Replace with A separate line item has been provisioned in Price Schedule & Appendix G for new bay integration at Substation end during AMC period for the scope described below: - The scope of work under Integration of new bays & reconfiguration work includes- ….Further, integration of new Bays at Control Centre end shall not be treated as new RTU integration during AMC period, and any such bay extension during AMC shall be in the scope of the contractor without any commercial implication to the Owner. The future bay integration during AMC period at substation end shall be in the scope of contractor as mentioned in Bill of Quantity Appendix-G. |
|  | Vol. II Part-A, Section – 4, Clause no. – 4.15 | Table 4.5 Responsibility Matrix | Responsibility Matrix Replace with The revised table 4.5 Responsibility Matrix is attached at Annexure-A. |
|  | Vol. II Part-A, Appendix-B | Interoperability Profile Testing specifications with IEC 60870 5-104 IEC defines IEC 60870-5-601/604 document with the basis test procedures to validate controlling and controlled station that use the standards IEC 60870-5-101/104. The test cases to be executed depend on the device capabilities defined in their interoperability document. | Interoperability Profile Replace with Testing specifications with IEC 60870 5-104 IEC defines IEC 60870-5-601/604 document with the basis test procedures to validate controlling and controlled station that use the standards IEC 60870-5-101/104. The test cases to be executed depend on the device capabilities defined in their interoperability document and shall be used for the conformance testing of the protocol supplied for control center end and RTU supplied under this project. This requirement is not for the routine, field testing and integration at site. …… |
|  | Vol. II Part-A, Appendix-D, NETWORK ARCHITECTURE of SLDC cum REMC | Typical Network Architecture for Ladakh SLDC cum REMC | Replace with Revised Typical Network Architecture for Ladakh SLDC cum REMC is attached at Annexure-A. |
|  | Vol. II, Part-A, Appendix-L | Inserted New Appendix | Appendix-L, Type Test Validity is attached at Annexure-A. |
|  | Vol. II Part-B, Introduction | Inserted New Part-B Introduction | Part-B Introduction section is attached at Annexure-A. |
|  | Vol. II Part-B, Section-1, Clause 1.1.1 | Data Acquisition ….All the functions for RTU data acquisition as described in the sub-sections below shall be implemented for existing RTUs (if applicable). Feature shall be available in SCADA System to accumulate data for a user defined time period (i.e.,15-minutes,1- day,1-week,1-month) and it shall be automatically reset the same after user defined time…. | Data Acquisition Replace with …All the functions for RTU data acquisition as described in the sub-sections below shall be implemented for RTUs.Feature shall be available in SCADA System to accumulate data for a user defined time period (i.e.,15-minutes, 30-minutes etc. shall be automatically reset the same after user defined time. Further, for accumulation period of 1-day,1-week,1-month, it can be provided either in SCADA or in historian.… |
|  | Vol-II Part- B, Section-1, Para 1 of Clause 1.1.1.3 | Backup Communication Channel Processing …. If valid data cannot be acquired from one of the RTUs, the Control Centre System shall automatically failover to the backup Communication channel. ....... | Backup Communication Channel Processing Replace with …. If valid data cannot be acquired from one of the channels of RTUs, the Control Centre System shall automatically failover to the backup Communication channel.......... |
|  | Vol. II, Part-B, Section-1, Clause-1.1.1.8, CFE requirement | CFE requirement CFE server should be able to operate in listening mode (able to receive signal without request). | Replace with CFE requirement The CFE Server, when operating in Listen mode, shall be able to read the power system data from RTU and process this data and forward it to SCADA servers. CFE server may not send the data poll request or establish communication with the RTU. |
|  | Vol. II Part-B, Section-1, Clause 1.2.1 | Data Exchange with Control Centres c)Block 4 (information messages) | Data Exchange with Control Centres c)deleted |
|  | Vol. II Part-B, Section-1, Clause- 1.2.3 | Data Exchange with Other Systems & Third-party applications …. The SCADA system shall provide web services that allow multiple applications to exchange any real time data points & vice-versa including alarms and events in secure manner ensuring latest cyber security guideline from statutory authority…. | Data Exchange with Other Systems & Third-party applications Replace with …. The SCADA system shall provide web services either on SOAP or on REST API that allow multiple applications to exchange (bi-directional) any data points (real time, future values (like various forecasts/schedules) including alarms and events in secure manner ensuring cyber security measures and guidelines specified in this specification. Data transfer from SCADA/EMS to IT/Any Other network should be made through secure services such as API calls. As per the requirement of the User, the Contractor shall incorporate new APIs in the SCADA System during AMC period also. If required, the APIs should be modified in such a way that, the corresponding data can only be accessed using API Keys. Standard API to fetch the data from SCADA/EMS system for example SCADA/EMS server and Data Historian server to provide the data to other owner applications. It should at least include the following. - Data values with quality code identified by point id/tag - Multiple values (at least 1000 samples every 10 sec) of same point id/tag with quality code - Range of values of consecutive point id/tag upto 100 nos. - State estimator values, Area Control Errors ……. |
|  | Vol. II Part-B, Section-1, Clause 1.2.3 | Data Exchange with Other Systems & Third-party applications ….SCADA System shall have inbuilt OPC-UA Server and client functionality. ….. | Data Exchange with Other Systems & Third-party applications Replace with ….SCADA System shall have OPC-UA Server and client functionality. ….. |
|  | Vol-II Part- B, Section -1, Clause- 1.2.4 | Data Exchange with Market Applications and Open Access …… All data mentioned in the above bulleted points would be available in one or more of the following formats shall be finalized during detail engineering– Dedicated API, SOAP/REST, OPC etc…. | Data Exchange with Market Applications and Open Access …… All data mentioned in the above bulleted points would be available in one or more of the following formats shall be finalized during detail engineering– • Dedicated API • Either SOAP or REST • OPC …. |
|  | Vol. II Part-B, Section-1, Clause 1.3.1 | c) Limit Monitoring ….. The override value shall be recognized, and any display, report, or log containing the value of the overridden limit shall include it as such. An override value shall be used instead of the permanent value until the user removes the override condition, selects an alternative limit set, or the system is re-initialized…… | c) Limit Monitoring Replace with ….. The override value shall be recognized, and any display, report, or log containing the value of the overridden limit shall include it as such. An override value shall be used instead of the permanent value until the user removes the override condition, selects an alternative limit set…… |
|  | Vol-II Part- B, Section- 1, Clause 1.3.3 | Calculated Data Processing SCADA/EMS system shall be capable of performing the following calculations at the indicated rates and storing the result in the database as calculated data corresponding to same SCADA field/point and shall be available for display. This calculation output shall not be considered as additional SCADA field/point for system sizing….. | Calculated Data Processing Replace with SCADA/EMS system shall be capable of performing the following calculations at the indicated rates and storing the result in the database as calculated data corresponding to same SCADA field/point and shall be available for display. The inherent Calculations associated with the field point (i.e., MVA, ROC, Min. Max. Avg etc.) shall not be considered as additional SCADA field/point for system sizing…… |
|  | Vol-II Part- B, Section- 1, Clause 1.3.3 | Calculated Data Processing ……The user interface and suitable API shall be provided to real time Calculations for SCADA Data as well as estimated Data. There shall be no limitation on number of calculations and arguments involved in each calculation, which shall be defined in the real-time calculations.…. | Calculated Data Processing Replace with …. Suitable application/GUI/display shall also be provided to define calculations. There shall be no limitation on number of calculations and there shall be capability to create calculations with a number of arguments involved in each calculation as per limit specified in Part-B, Appendix-C….. |
|  | Vol. II Part-B, Section-1, Clause 1.3.3.3 | # Rate of Change The rate of change of variables shall be automatically calculated for each analog data using the following formula that filters the rate of change via exponential smoothing: NewRate = A * OldRate + (1 - A) (NewValue - OldValue)/Time Interval ……… | # Rate of Change Replace with The rate of change of variables shall be automatically calculated for each analog data using the following formula that filters the rate of change: NewRate = (NewValue - OldValue)/TimeInterval ……… |
|  | Vol. II Part-B, Section-1, Clause 1.3.3.4 | Average Value Calculations For calculation of the average value of an analog points (all lines, loads, generators and transformers), the sampling frequencies of the point shall be same as scan rate and the time periods duration of interest shall be defined by the user. # Average of value over duration of interest = Sum of values of samples/No. of samples……….. | Average Value Calculations Replace with For calculation of the average value of an analog points (all lines, loads, generators and transformers), the sampling frequencies of the point shall be same as scan rate and the time periods duration of interest shall be defined by the user. The average shall be calculated as time weighted average. # Deleted the formula………. |
|  | Vol. II Part-B, Section-1, Clause 1.3.3.5 | Max. and Min. Value Calculations …These calculations shall use the real- time clock and initially shall be performed for 15-minute intervals and it should be available to operators for last 24 hours……… | # Max. and Min. Value Calculations Replace with # ………These calculations shall use the real- time clock and initially shall be performed for 15-minute intervals and it shall be available to operators for last 24 hours either in SCADA or in Historian ………. |
|  | Vol. II Part-B, Section-1, Clause 1.3.5 | Real-time Data Storage and Playback Para-2 ….. It shall also be possible to set a different sampling rate for playback than the sampling rate for data storage. It shall be possible to have tabular and graphical trends from the stored data. The trending of graphs from the displays of the playback shall also represent historical data with corresponding time-stamp. Para-3 The user shall be able to view the stored data on SCADA/EMS system displays such as on Single Line diagram, Network Diagram & Trend display by placing a workstation console monitor in a history mode for a specified time and date. Any system displays subsequently called up on that monitor shall display the data that existed at the specified time and date, or the closest previous time available…. Para-5 The users shall be able to select the time window of interest to save part of above playback data in a separate file (file name of the playback data file could be user editable for describing incident/disturbance data contained in the file) for archival of above important data in the Historian system for future retrieval and playback in SCADA system. This archived data shall be transferable in database of Historian system for generation of reports. The snapshot of archived data shall be used by EMS applications in study mode. Para-6 Trending of any Analog Data should be possible during playback period. Playback can be done in same display no changes shall be required for HDR, only selection required input shall be required. | Real-time Data Storage and Playback Replace with Para-2 …It shall also be possible to set a different sampling rate for playback than the sampling rate for data storage. # Para-3 # The user shall be able to view the stored data on SCADA/EMS system displays such as on Single Line diagram, Network Diagram & Trend display by placing a display window in a history mode/playback mode for a specified time and date. Any system displays subsequently called up on that display window shall show the data that existed at the specified time and date, or the closest previous time available….. # Para-5 Deleted # Para-6 …….Playback can be done in same display no changes shall be required for historical data playback, only selection of required input (time duration, playback rate ) shall be required. |
|  | Vol. II Part-B, Section-1, Clause 1.4 | Network Status Processor …..Network Status Processor shall be able to compute availability of elements in real-time and given duration of interest based on historical data of output of NTP. | Network Status Processor ….Deleted this para |
|  | Vol-II Part- B, Section 1: SCADA System Functions. Para 2 of Clause 1.8 | Historian ……Functionalities mentioned under this section (including visualization) shall be meet by the Historian itself and from SCADA wherever specifically mentioned… | Historian Replace with ….. Functionalities mentioned under this section (including visualization) shall be met by the Historian and from SCADA wherever specifically mentioned… |
|  | Vol. II Part-B, Section-1, Clause 1.8.3 | e. Graphical user interface i. The UI should have interface with MS tool and XML. | e. Graphical user interface i. Deleted |
|  | Vol-II Part- B, Section 1, Clause 1.8.3, Point (b) | b)Organization of data and configuration The asset or power system topology model hierarchical structure shall be stored in Historian System with versioning/archiving capability, and with roll-ups to aggregate data on real-time basis. The Historian System must be able to link data points held within the Historian to the process model defined in SCADA System. | b)Organization of data and configuration Replace with The structure of Historian shall be as per power system hierarchical structure with versioning/archiving capability. The Historian System must be able to automatically populate the data points in the Historian once defined/modelled in SCADA System. |
|  | Vol. II Part-B, Section – 1, Clause no. –1.8.3 , Point (c) | c) Real-time data interfaces …The Historian System shall provide real-time, fault-tolerant, high-speed links from any industrial automated real-time data sources through an industry standard interfaces such as multiple OPC industry standards, OPC DA, OPC UA and OPC HDA, connector. Also, it shall have interfaces compatible with DAS (1.0a and 2.0) compliant servers, SOAP, REST, SQL, ODBC, OLEDB, Modbus, ASCII, and text…. | c) Real-time data interfaces Replace with …The Historian System shall have real-time, fault-tolerant, high-speed links for data exchange (import & export) from/to any industrial automated real-time and archived data sources through industry standard interfaces such as multiple OPC industry standards, OPC DA, OPC UA and OPC HDA, connector. Also, it shall have interfaces compatible with either SOAP or REST, SQL, ODBC, OLEDB, Modbus, ASCII, and text (csv/excel formats)….. |
|  | Vol. II Part-B, Section – 1, Clause no. –1.8.3 , Point (d) | d)Calculated values …The calculation engine shall be able to define calculation functions as aggregations; based on equipment type, system voltage, station-wise, region-wise, area-wise, asset type, totalizers (accumulators), and performance equations formulas and shall support periodic or time-based or event-based triggers… | d)Calculated values Replace with ..The calculation engine shall be able to define calculation functions as per user requirements and shall support periodic or time-based or event-based triggers… |
|  | Vol. II Part-B, Section – 1, Clause no. –1.8.3, Point (e) | e) Graphical user interface j)… End-users tool to build, modify and manage displays SLD (Single-Line-Diagrams) and multiple build-in analytics from amongst graphs, bar-charts (horizontal or vertical), XY plots (can be rotated in any direction), pie-charts, scatter plot, box-plot (refer to Appendix-B), heat map, GG Plots, Correlation Matrix , violin plot, Density Plot, candlestick chart, histograms, 3-D plots, multi-state symbols, layers, etc. | e) Graphical user interface Replace with j)… End-users tool to build, modify and manage displays SLD (Single-Line-Diagrams) and multiple build-in analytics from amongst graphs, bar-charts (horizontal or vertical), XY plots (can be rotated in any direction), pie-charts, scatter plot, box-plot (refer to Appendix-B), heat map, GG Plots, Correlation Matrix , violin plot, Density Plot, candlestick chart, histograms, 3-D plots etc.… |
|  | Vol. II Part-B, Section – 1, Clause no. –1.8.3 , Point (g) | g)Manual Data Entry …. An API tool to be provided for bulk insertion of manual data on schedule basis/or on demand. | g) Manual Data Entry Replace with... ….An API tool to be provided for bulk insertion of data on schedule basis/or on demand. |
|  | Vol. II Part-B, Section – 1, Clause no. –1.8.3, point (h) | h)Interface with Business Applications …. The Historian System must offer connectivity to third party systems using multiple protocols (at least two) e.g; OPC/ ODBC/ OLEDB/ JDBC and web services….. | h)Interface with Business Applications Replace with …. The Historian System must offer connectivity to third party systems using multiple protocols e.g., OPC, ODBC,OLEDB, JDBC and web services….. |
|  | Vol-II Part- B, Section 1, Clause no. - 1.8.3, point (j) | j)Interface with External System …The Historian system shall provide web services on SOAP and REST to publish data into the database through multiple applications… | j)Interface with External System Replace with …The Historian system shall provide web services on either SOAP or REST to publish data into the database through multiple applications… |
|  | Vol-II Part- B, Section 1, Clause no. - 1.8.4 | Reports A Business Tool shall be provided with user friendly configurable with drag and drop query builder, report builder and trend builder facility….. | Reports Replace with A Report Development & Generation Software shall be provided with user friendly configurable with drag and drop query builder, report builder and trend builder facility. |
|  | Vol. II Part-B, Section – 1, Clause no. –1.8.5, Historical Trending | Historical Trending r) Shall be able to put two cursor points on the trend, with a feature to calculate the value difference between the cursor points. | Historical Trending Deleted |
|  | Vol. II Part-B, Section-2, Clause No.-2.2 | Power System Analysis c) Import and export a detailed CIM (latest Version) based model of the power system under its area of jurisdiction as well as Power System of boundary-regions (Nearby systems), consisting all the Network elements at 33 kV and above. The supplied system should support IEC 61970-452 (i.e., Equipment Profile), and IEC 61970-456 (i.e., Analog Measurements Profile, Discrete Measurements Profile, State Variable Profile and Topology Profile) standards. | Replaced with Power System Analysis c) Import and export a detailed CIM (latest Version) based model of the power system under its area of jurisdiction as well as Power System of boundary-regions (Nearby systems), consisting of all the Network elements at 33 kV and above. The supplied system shall have feature to convert the older versions of CIM compliant data to latest CIM version and import the same in the EMS system, any tools for such conversion shall also be under the scope of the Contractor. The supplied system should support IEC 61970-452 (i.e., Equipment Profile), and IEC 61970-456 (i.e., Analog Measurements Profile, Discrete Measurements Profile, State Variable Profile and Topology Profile) standards. |
|  | Vol. II Part-B, Section-2, Clause No.-2.2 | Power System Analysis d)…EMS application should have compatibility for exchange of synchro phasor measurements directly from the available PDC of the control center through IEC 104 protocol. | Power System Analysis Replace with d)… SCADA/EMS system shall have compatibility to exchange PMU data from other systems through their respective SCADA system. |
|  | Vol. II Part-B, Section – 2, Clause no. – 2.2.2 Modelling | - HVDC Links - Two-terminal and multi-terminal HVDC systems with LCC and VSC shall be represented in application with comprehensive converter models and flexible DC network configurations. | Replace with - HVDC Links - Two-terminal HVDC systems and multi-terminal (may be modelled with combination of two-terminal) HVDC systems with LCC and VSC shall be represented in application with comprehensive converter models and flexible DC network configurations. |
|  | Vol. II Part-B, Section-2, Clause No. 2.2.5.3 | Alternating Current Model The EMS-CIM should be able to do conversion of third-party network model formats to CIM compliant model and vice versa. | Replaced with Alternating Current Model The EMS-CIM should be able to do conversion of CIM compliant third-party network model formats to another version of CIM compliant model and vice versa. |
|  | Vol. II Part-B, Section-2, Clause No.- 2.2.5.3 Alternating Current Model | r) It shall model Flexible A.C. Transmission Systems (FACTS) devices such as Thyristor Controlled Series Compensator (TCSC), STATCOM, Thyristor Controlled Phase Angle Regulator (TCPAR), etc. s) It shall model Renewable energy sources such as Wind generator, Solar generation and Battery Energy Storage System (BESS) including electrolyser model as per IEEE standard, WECC generic models & user defined model. Model type with attributes will be decided during the finalization of the engineering document. | Replace with r) It shall model Flexible A.C. Transmission Systems (FACTS) devices such as Thyristor Controlled Series Compensator (TCSC), STATCOM etc. s) It shall model Renewable energy sources such as Wind generator, Solar generation and Battery Energy Storage System (BESS) including electrolyser model with attributes will be decided during the finalization of the engineering document. |
|  | Vol. II Part-B, Section-2, Clause No.- 2.2.5.4 | High Voltage Direct Current Model • Multi-terminal HVDC | Heading replace with HVDC Model Application Replace with • Multi-terminal HVDC (may be modelled with combination of two-terminal) |
|  | Vol. II Part-B, Section-2, Clause No.- 2.2.5.5 | Inserted new clause | Inserted High Voltage Direct Current Model New clause of High Voltage Direct Current Model is attached at Annexure-A. |
|  | Vol. II Part-B, Section – 2, Clause no. – 2.2.8, State Estimation | State Estimation shall provide a complete and reliable power system model solution containing information for use by other PSA functions and for display…… | State Estimation shall provide a complete and reliable power system model solution (using weighted least square algorithm or better) containing information for use by other PSA functions and for display…… |
|  | Vol. II Part-B, Section – 2, Clause no. – 2.2.8, State Estimation | User shall be able to select algorithm for State Estimation (SE) out of orthogonal and Weight Least Square Algorithm. | Replace with The state estimation (SE) shall be developed with Weighted Least Square Algorithm or better. |
|  | Vol. II Part-B, Section-2, Clause 2.3 | Dispatcher Training Simulator c) It shall model Renewable energy sources such as Wind generator and Solar model. The generator models of type 1, 2, 3, 4 and 5 must also be provided. Wind model detail is given in Appendix L (2). | Dispatcher Training Simulator Replace with c) It shall model Renewable energy sources such as Wind generator and Solar model. The generator models of type 1, 2, 3 and 4 must also be provided. Wind model detail is given in Appendix L (2). |
|  | Vol. II Part-B, Section-2, Clause 2.3.1 | b) Energy Source and Frequency Models ……The Instructor shall be able to enable/disable (block) governor action on an individual unit basis. The ability to include the steady state effects of automatic voltage regulators (AVRs) and power system stabilizers (PSS) shall be provided…… | b) Energy Source and Frequency Models Replace with …….The Instructor shall be able to enable/disable (block) governor action on an individual unit basis. The ability to include the steady state effects of automatic voltage regulators (AVRs) shall be provided….. |
|  | Vol. II Part-B, Section-2, Clause 2.3.1 | j) User Defined models that can be built from smaller logical blocks (such as low pass filter, high pass filter, differentiator block, integrator block, band pass, band reject filters etd) to simulate the performance of power electronic devices or other non-standard models of equipment such as AVR/PSS etc. | Replace with j) User Defined models that can be built from smaller logical blocks (such as low pass filter, high pass filter, differentiator block, integrator block, band pass, band reject filters etc.) to simulate the performance of power electronic devices or other non-standard models of equipment such as AVR. |
|  | Vol. II Part-B, Section-2, Clause 2.3.2 | Hydro System Model ….. HSM shall include a representation of mechanisms that allow personnel other than the Control Centre computer system user to affect the hydro system plus a simulation of the hydro equipment the Control Centre computer system monitors and controls. HSM shall include the ability to compute …..: | Hydro System Model Replace with ….. HSM shall include a representation of mechanisms that allow personnel other than the Control Centre computer system user to affect the hydro system plus a simulation of the hydro equipment the Control Centre computer system monitors and controls. Since Inflow forecasting is not required in real-time applications, Contractor may develop a simple simulation for reservoir fill level, one inflow value and one spillway outflow value and by defining a relationship between these parameters. HSM shall include the ability to compute …..: |
|  | Vol. II Part-B, Section-2, Clause 2.3.4 | Instructor control c) Probabilistic Events: The instructor shall be able to define an event within a given time interval with a pre-defined probability. Such as there is a 25 percent chance that a load point will increase by 100 MW during the specified time window. | Instructor control Deleted |
|  | Vol-II Part- B, Section -2, Clause- 2.3.4(2) b) & Point f) Instructor Control | Point (b) Slow Forward (Power System Model only): Allows the Instructor to move a training scenario forward at an Instructor-specified speed slower than real-time. Point (f) Periodic Snapshot: Allows the Instructor to create a historical file that is periodically updated with session data necessary to resume simulation as it occurs during the simulation. The DTS shall not pause while the snapshots are being collected and saved. The snapshot save area shall be circular in nature where the oldest snapshot will be overwritten each time a new snapshot is saved when the save area is full. | Replace with Point (b) Simulation Speed change (slow/fast) (Power System Model only): Allows the Instructor to move a training scenario forward at an Instructor-specified speed other than real-time simulation. Point (f) Periodic Snapshot: Allows the Instructor to create a historical file that is periodically updated with session data necessary to resume simulation as it occurs during the simulation. The snapshot save area shall be circular in nature where the oldest snapshot will be overwritten each time a new snapshot is saved when the save area is full. |
|  | Vol-II Part- B, Section 3: Clause - 3.4 | User Interface Environment ……. Geo-spatial display shall be updated on monthly or on-demand basis. Getting dynamic map tiles through map server shall be the owner’s responsibility but its corresponding integration and deployment in displays shall be the responsibility of contractor. | User Interface Environment Replace with …... Geo-spatial display shall be updated on monthly or on-demand basis. Providing map server, getting dynamic map tiles through map server and its subscription shall be the owner’s responsibility but its integration and deployment in displays shall be the responsibility of contractor. However, if on-line map tiles are not available, the geo-spatial displays shall be provided with downloaded offline map tiles. |
|  | Vol-II Part- B, Section 3: Clause - 3.6 | Display recording and playback A licensed application in the main User Interface itself shall be delivered to capture any display screen continuously. The recording should enable playback in standard format such as mp4. The video-file shall get played in any standard video-player software. Video recording shall also be possible in historical reconstruction over a display. | Display recording and playback Replace with A licensed application (DISPLAY SCREEN RECORDING SOFTWARE as specified in BoQ) in the main User Interface itself shall be delivered to capture any display screen continuously. The recording should enable playback in standard format such as mp4. The video-file shall get played in any standard video-player software. Video recording shall also be possible in historical reconstruction over a display. |
|  | Vol-II Part- B, Section 3: Clause - 3.7.2 | Display Note Pad/Memo …….A link to navigate the corresponding SLD shall be available in the same summary display Provision for “Group based Note-Pad/Memos” and “Global Note-Pad/Memos” shall be provided with following visibility requirements:- • Global Note-Pad/Memos: shall be visible to all categories of users. • Group Based Note-Pad/Memos: shall be visible only to specific user-group type (e.g. Dispatcher, Programmer, etc.). | Display Note Pad/Memo Replace with …….A link to navigate the corresponding SLD shall be available in the same summary display Provision for “Global Note-Pad/Memos” shall be provided with following visibility requirements:- • Global Note-Pad/Memos: shall be visible to all categories of users. |
|  | Vol. II Part-B, Section-3, Clause 3.9 | Trending (SCADA Application) Trending is a display of series of values of parameters on a time axis. Graphical trends shall be supported by the system for both real-time SCADA data and Historical data separately as per user selectable source for trending. The minimum features to be provided as part of Trending are listed below -…… Bullet No. 6 - Trending of at least 10 parameters on the same display shall be supported (with no limitation on nos. of such trend displays). - …. Bullet No. 10 - Major and minor interval of x & y axis should be user configurable for any data or time. There shall not be any limitation of trends associated with a single display. - … Bullet No. 18 - Trending application shall have standard regression functionalities like linear, polynomial and exponential etc. .…… | Replace with Trending Trending is a display of series of values of parameters on a time axis. Features specified herein under shall be supported by the supplied systems. The minimum features to be provided as part of Trending are listed below – …… Bullet No. 6 - Trending of at least 10 parameters on the same display shall be supported and with minimum 100 nos. of such trend displays. - …. Bullet No. 10 - Major and minor interval of x & y axis should be user configurable for any data or time. - …. Bullet No. 18 - Deleted - …… |
|  | Vol-II Part- B, Section 3: Clause - 3.9.1 | Graphical Trending m) Trend point marker functionality to compare the data for different periods. | Graphical Trending Replace with m) Trend point marker functionality to compare the data for different periods on a single trend window. |
|  | Vol-II Part- B, Section 3: Clause - 3.10 | Alarms ….. The minimum features required in alarm messages system are listed below- …… Bullet No. 8 - Minimum 1,00,000 (One Lakhs) alarm messages shall be available in real-time. | Alarms ….. The minimum features required in alarm messages system are listed below- …… Replace with Bullet No. 8 Minimum 20,000 on alarm messages shall be available in real-time. The system shall support upto 1,00,000 alarm to be displayed (auto refresh) either through SCADA or SCADA-Historian on demand by the operator. |
|  | Vol. II Part-B, Section-3, Clause 3.10.1 | Alarm Categories …..A means shall be provided for changing operating shifts without reassignment of alarm categories at a console. Console failure shall result in automatic reassignment of alarms to other consoles in a pre-defined manner and shall generate an alarm. ….. | Alarm Categories: Replace with ….. A means shall be provided for changing operating shifts without reassignment of alarm categories at a console. Console failure shall generate an alarm and the user shall be able to reassign the alarms of failed console to other consoles in a pre-defined manner. …… |
|  | Vol. II Part-B, Section-3, Clause 3.10.2 | Alarm Priority levels Each alarm shall be assigned to an alarm priority level. A Minimum 16 alarm priority levels shall be supported.…… i) Every Alarm shall be accompanied by an Audible tone (different audio tones for different types of Alarms configurable by the user) which shall be user configurable also in real time for some particular events also. | Alarm Priority levels Replace with Each alarm shall be assigned to an alarm priority level. Priority levels mentioned in Part-B, Appendix-C shall be supported……… i) Every Alarm shall be accompanied by an Audible tone. The different audio tones for different types of Alarms shall be configurable by the programmer/engineer for some particular events also. |
|  | Vol. II Part-B, Section-3, Clause 3.11 | Events ……Event messages shall be displayed on an events summary. Event messages shall be archived in chronological order. Minimum 100000 (One Lakhs) event messages shall be available in real-time. It shall be possible to sort, display, filter and print event messages from any console.……. | Events Replace with ……Event messages shall be displayed on an events summary. Event messages shall be archived in chronological order. Minimum 20000 event messages shall be available in real-time. The system shall support upto 1,00,000 events to be displayed (auto refresh) either through SCADA or SCADA-Historian on demand by the operator. It shall be possible to sort, display, filter and print event messages from any console. |
|  | Vol. II Part-B, Section-3, Clause 3.15.17 | ### Contour & Heat Map Displays ….Geo-spatial display with contour map of Data within geographical boundary of India shall be provided in which Zoom-in, Zoom-out, Panning option shall be available in the map. Display Builder shall be capable of importing point and placing a predefined picture/symbol as per the Latitude and Longitude specified by the user. ### The“ Playback” option shall be made available in the map so that the continuous pattern over the period of time shall be visualized. The pattern shall be exported in a video format so as to use it in offline mode………. | ### Contour & Heat Map Displays Replace with ……….Geo-spatial display with contour map of Data within geographical boundary of region/state shall be provided in which Zoom-in, Zoom-out, Panning option shall be available in the map. Display Builder shall be capable of importing point and placing a predefined picture/symbol as per the Latitude and Longitude specified by the user. ### The “Playback” option feature shall also be made available in the Geo-spatial display pattern over the period of time shall be visualized. The pattern shall be exported in a video format so as to use it in offline mode. |
|  | Vol-II Part- B, Section 3, Clause: 3.15.18 | ### Voltage Profile Display Voltage profile displays shall be provided to present different voltage levels on a geographical display in form of contours & heat map. Further, the areas with various voltage levels shall be shown with different colours.. | ### Voltage Profile Display Replace with ### Voltage profile displays shall be provided to present different voltage levels on a geographical display in form of contours & heat map either based on the per unit values or based on the actual value. Further, the areas with various voltage levels shall be shown with different colours…… |
|  | Vol. II Part-B, Section-3, Clause 3.15.25 | Weather data on Geographical map display The display shall show the weather data superimposed on a geographical display with background such as “Google Maps/Bhuwan Maps/etc.” A sample illustration is included in Appendix –B. | ### Weather data on Geographical map display Replace with The display shall show the weather data superimposed on a geographical display with background such as “Google Maps/Bhuwan Maps/etc.” A sample illustration is included in Appendix–B. Weather data shall be provided by owners. However, the contractor shall display map superimposing weather data. |
|  | Vol. II Part-B, Section-4, Clause- 4.1 | General Requirements …..Also, the contractor must provide the latest version of all third party application software supplied under the project before the start of Factory Acceptance Test (FAT) without any cost implication. The contractor shall provide details of all the API’s including its source code supplied/used under the contract to the owner without any additional cost. | General Requirements Replace with ….Also, The Contractor shall provide the latest version of all third party application software supplied under the project before the start of Factory Acceptance Test (FAT) without any cost implication. The 3rd party software embedded with the SCADA/EMS Application software shall not be treated as 3rd party software for this version upgrade requirement subject to security vulnerabilities. The contractor shall provide details of all the API’s (used in the project) including its source code supplied/used under the contract to the owner without any additional cost. |
|  | Vol. II Part-B, Section – 4, Clause no. – 4.2.1 | Design and Coding Standards for SCADA/EMS applications ….. h) Antivirus Software - All computers and firewalls shall be provided with the latest antivirus software as on date of supply. The antivirus software shall have the capability of having its virus definitions updated from time to time. The Contractor shall be responsible for the maintenance & update of the antivirus software. | Design and Coding Standards for SCADA/EMS applications …… Replace with h) Application Logging - The SCADA/EMS system applications shall have logging that contains information regarding events occurred within the software application. These events logged out by the application shall be written and stored in a file. The feature to export the logs in text format for any of the SCADA/EMS application shall be provided. The event logs include errors and warnings as well as informational events. The types of information and format of messages found in an application log file shall generally include - - Context information: Background information that provides insight into the state of the application at the time of the message. - Timestamps: A specific piece of contextual information for tracking and correlating issues. - Log levels: Labels that help calculate the level of importance for the entries in log file. Levels such as include INFO, DEBUG, WARN, and ERROR. The logs shall be in sufficient details to support the following - - Troubleshooting: Logs shall help identify the root cause of errors or unexpected behaviour by providing context and clues for efficient issue resolution. - Monitoring: Logs shall help in real-time monitoring of performance and health is enabled, allowing detection of anomalies and ensuring optimal application operation. - Auditing and Compliance: Logs shall help meet regulatory requirements by recording events and user actions for security and compliance purposes. - Performance Optimization: Logs shall help identify performance bottlenecks and areas for improvement, leading to better resource allocation. - Security Analysis: Logs shall assist in detecting security breaches and unauthorized access, enhancing application security. |
|  | Vol. II Part-B, Section – 4, Clause no. – 4.2.2 | Operating System ………..The system security shall also be maintained in line with cyber security guidelines/recommendations issued by various statutory authorities like CEA, CERT-In, NCIIPC etc. from time-to-time throughout the life cycle of the project……. | Operating System Replace with ………. The system security shall also be maintained in line with cyber security recommendations/guidelines issued by various statutory agencies like CERT-In, NCIIPC, CEA, Meity etc. from time-to-time during entire contract period as per the provisions mentioned under Clause 1.20, Section 1, PART A of technical specifications along-with other scope of works specified under the contract. |
|  | Vol. II, Part-B, Section-4, Clause-4.4, Network Software | The network software for the SCADA/EMS & REMC system shall include software for network communication and network services. Network software shall include the user node software that provides the connection of that node to the network. The network node software shall be provided for each type of network node connection supplied with the initial system and shall be licensed for the quantities and types of nodes defined for the SCADA/EMS & REMC System configuration. It should be able to generate reports for a defined period regarding availability of communication links. In case any communication link is DOWN/OUT/Failure, then a pop-up should come up for it along with the SMS and e-mail facility shall be implemented for the same. | Replace with The network software for the SCADA/EMS & REMC system shall include software for network communication and network services. Network software shall include the user node software that provides the connection of that node to the network. The network node software shall be provided for each type of network node connection supplied with the initial system and shall be licensed for the quantities and types of nodes defined for the SCADA/EMS & REMC System configuration. |
|  | Vol-II Part- B, Section 4, Clause: 4.5 | Network Management System (NMS) All Active devices such as Servers, Workstations, Storage Devices (SAN, NAS, HDD,SDD etc.) | Network Management System (NMS) Replace with All Active devices such as Servers, Workstations, Storage Devices (SAN, NAS etc.) |
|  | Vol. II, Part-B, Section-4, Clause-4.5, Network Management System (NMS) | Inserted new para | Inserted j) It should be able to generate reports for a defined period regarding availability of communication links. In case any communication link is DOWN/OUT/Failure, then a pop-up should come up for it along with the SMS and e-mail facility shall be implemented for the same. |
|  | Vol. II Part-B, Section-4, Clause 4.6 | Database Development Tools The background color of database tool shall be user configurable. | Database Development Tools Deleted |
|  | Vol-II Part- B, Section 4: Clause 4.6.5 | Database Integration (on-lining) … The database changes made in the Main Control Center shall be reflected immediately in Backup Control Center with minimal user intervention and without requiring any downtime. At regular intervals (Daily/ at pre-configured time intervals) the database of Main and Backup Control Centers be checked for any differences in entries, linkages, calculations, and database elements and necessary updation shall be done for the same. | Database Integration (on-lining) Replace with The database changes made in Main Control Center shall be reflected immediately in Backup Control Center with minimal user intervention. The database of Main and Backup Control Centers shall be checked for differences in entries, linkages, calculations and database elements as and when required by owner with minimal user intervention and necessary updation shall be done for the same. |
|  | Vol-II Part- B, Section 4: Clause 4.6.10 | Development System (DDS or PDS) as a test bench | Replace with Complete clause of Development System (PDS) as a test bench replace which is attached as Annexure-A to this amendment. |
|  | Vol-II Part- B, Section 4: Clause 4.6.11 | CIM (Common Information Model- 61970) compliant Data Modelling Import & Export Tool ……Owner is in process to establish centralized database system which will be CIM complaint. User will have access to this database and shall model required component in this centralized database. Subsequently related database shall be extracted and imported in this proposed system. Contractor shall be responsible to develop CIM tool which shall be able to exchange the files from this database in CIM format….. | CIM (Common Information Model- 61970) compliant Data Modelling Import & Export Tool This para deleted. |
|  | Vol. II Part-B, Section-4, Clause 4.7 | Display Generation and Management …. Utility to import & export displays through DXF or DWG or XML format (latest version with backward compatibility) from other control centers shall be provided | Display Generation and Management Replace with .…Utility to import & export displays through any of the formats DXF, DWG, XML formats from other control centers shall be provided. For DXF, DWG and XML format (for any of the format), it should support latest version with backward compatibility. |
|  | Vol. II Part-B, Section-4, Clause 4.7.3 | The display generator shall also have facility to export the SCADA/EMS displays in XML or DXF or DWG format (latest version with backward compatibility) to be used in AUTOCAD. For DXF, DWG, XML, AUTOCAD it should support latest version with backward compatibility. | Replace with The display generator shall also have facility to export the SCADA/EMS displays in any of the formats such as XML or DXF or DWG (latest version with backward compatibility) to be used in AUTOCAD. |
|  | Vol-II Part- B, Section- 4, Clause-4.8.5 | Data Exchange Utilities • Through SOAP and REST: The SCADA system shall provide web services on SOAP and REST that allow multiple applications to exchange any data points including alarms and events. | Data Exchange Utilities Replace with • Through either SOAP or REST: The SCADA system shall provide web services on either SOAP or REST, that allow multiple applications to exchange any data points including alarms and events. |
|  | Vol. II Part-B, Section-5, Clause No.-5.2 | Technical Requirements for Hardware d) The Bidder shall ensure that product/technologies/services quoted under this project are latest and it shall have more than 7 years of life initially (i.e.., “End of Support Life” for minimum 7 years, from date of bid submission) which shall be extended during entire contract period (including extension of contract, if any) by extending the OEM warranty or replacing the product.). g) All the supplied system shall be under OEM (Hardware and Software) warranty & support till the completion of entire AMC period (including extension of contract, if any). h) During entire contract period (including extension of contract, if any), if OEM discontinues/ ends support to any item supplied (software/hardware/security solution) under the contract, bidder has to replace such hardware, software (or both, depending on software or hardware dependency) without any additional cost to Owner. Replacement shall be of either same or higher configuration. | Technical Requirements for Hardware Replace with d) The Bidder shall ensure that product/technologies/services quoted under this project are latest and it shall have more than 7 years of life initially (i.e.., “End of Support Life” for minimum 7 years, from date of bid submission) as per the provisions mentioned under Clause 1.20, Section 1, PART A of technical specifications along-with other scope of works specified under the contract. g ) The supplied system shall be under OEM (Hardware and Software) warranty & support till the completion of entire AMC period as per the provisions mentioned under Clause 1.20, Section 1, PART A of technical specifications along-with other scope of works specified under the contract. h) Refer Clause 1.20, Section 1, PART A of technical specifications along-with other scope of works specified under the contract. |
|  | Vol. II Part-B, Section-5, Clause 5.5 | CFE (Communication Front-End) Server …….However, all the data from field to CFE shall be routed through internal Firewall. | CFE (Communication Front-End) Server Replace with …….However, all the data from field to CFE shall be routed through external Firewall. |
|  | Vol. II Part-B, Section-5, Clause No.-5.7.3 | WAN Routers cum Firewall …. There shall be 50% spare ports. Routers shall have the built-in firewall/security features as required.….. | WAN Routers cum Firewall Replace with …. Routers shall have the built-in firewall/security features as required. All routers shall have spare ports as per Appendix H. |
|  | Vol. II, Part-B, Section-5, Clause-5.8.1, | Storage Area Network (SAN) based storage Inserted new line | Storage Area Network (SAN) based storage Inserted new line SAN shall operate in active-active mode. |
|  | Vol. II Part-B, Section-5, Clause No.-5.19 | Provision of file transfer between OT and IT Provision must be kept to for secure file and data exchange between IT and OT system and between other OT systems. Keeping all security measures and guideline. All necessary hardware & Software shall be provisioned by the contractor accordingly. File exchange shall be as per the owner convenience periodicity. | Replace with Provision of file transfer between OT and IT Provision shall be provided for secure file and data exchange between IT and OT system and between other OT systems keeping all security measures and guidelines specified in the technical specification. The periodicity of File exchange shall be as per the owner requirements. The secure file and data exchange between IT and OT system shall be as per functionalities specified in different section of this specification. |
|  | Vol. II Part-B, Section-6, Clause 6.6.1 | Server Failover ….The on-line functions of the failed Server, having execution periodicity less than or equal to 30 seconds, shall be assigned to its backup Server within 30 seconds of the failure except for Historian Server…. | Server Failover Replace with ….The on-line functions of the failed Server, having execution periodicity less than or equal to 30 seconds, shall be assigned to its backup Server within 30 seconds of the failure. The failover time for historian server shall be within 60 seconds….. |
|  | Vol. II Part-B, Section-6, Clause 6.6.2 | 6.6.2 Restart Restart involves the ability of any server to self-detect its non-recoverable errors and to attempt to restart the SCADA/EMS & REMC system functions. The restart logic shall determine the desired state of the failed Server and the online function(s) to be initiated in this Server. The restart logic shall also preclude conflicts among Servers, such as assigning too few or too many Servers to the primary state and the erroneous duplication of functions in multiple Servers. All maintenance functions executing in the restarting Server shall be suspended to expedite the restart process. Restart shall include initialization of the SCADA/EMS & REMC function(s) and internal parameters, updating of databases, establishing access to peripheral devices, and execution of the function(s). Databases may be updated from backup databases or from static initialization database copies stored on auxiliary memory depending on the nature of the restart. The use of the static initialization databases shall be restricted to user-invoked restarts. If insufficient peripheral devices are available to perform the on-line function(s), the restart logic shall generate an alarm requesting user intervention. Restart as described above shall be completed within 30 seconds except for EMS server which can be 120 seconds. Also, the cold restart of the devices (Firewall, Router, Switch etc.) shall be completed within 5 minutes. | Replace with 6.6.2 Application Restart Application Restart involves the ability of any server to self-detect its non-recoverable errors and to attempt to restart the SCADA/EMS & REMC system functions. The restart logic shall determine the desired state of the failed Server and the online function(s) to be initiated in the respective Application. The restart logic shall also preclude conflicts among Servers, such as assigning too few or too many Servers to the primary state and the erroneous duplication of functions in multiple Servers. Application restart on command by user shall also be treated similarly. All maintenance functions executing in the restarting server shall be suspended to expedite the restart process. Restart shall include initialization of the SCADA/EMS & REMC function(s) and internal parameters, updating of databases, establishing access to peripheral devices, and execution of the function(s). Databases may be updated from backup databases or from static initialization database copies stored on auxiliary memory depending on the nature of the restart. The use of the static initialization databases shall be restricted to user-invoked restarts. If insufficient peripheral devices are available to perform the on-line function(s), the restart logic shall generate an alarm requesting user intervention. Application Restart as described above shall be completed within 2 minutes for all application(except EMS applications), 3 minutes for EMS applications and 5 minutes for Historian application. Application restart shall not include user interface(s) response time which shall be as per performance requirement. |
|  | Vol. II Part-B, Section-6, Clause 6.6.3 | 6.6.3 Server Start-Up A Server start-up shall be performed when commanded by a user and when Server input power is interrupted and restored such that the operating environment of the Server is established prior to restarting the on-line functions. Establishment of the operating environment may include execution of self-diagnostics, reloading the operating system and system services, and connection to and verification of communications with all nodes on the control center computer system LAN. The server start up shall be completed within 5 minutes with all functions scheduled for execution. | Replace with 6.6.3 Server Restart A Server restart shall be performed when commanded by a user (soft reboot) and/or when Server input power is interrupted (hard reboot) and restored such that the operating environment of the Server is established. The server shall automatically restart itself when input power is interrupted and restored. Establishment of the operating environment may include execution of self-diagnostics, reloading the operating system and system services, initialization of all interfaces, initialization of peripheral devices such as storage, printer etc. , connection to the databases, connection to and verification of communications with all nodes on the control center computer system LAN, resumption of all SCADA/EMS & REMC functions, initialization of all communications with data sources and other control centers and notifications to the users that restart has been completed. Server restart shall be completed within 10 (ten) minutes or earlier. Device Restart The restart of the devices (Firewall, Router, Switch etc.) shall be completed within 5 minutes. |
|  | Vol. II Part-B, Section-6, Clause 6.6.4 | System Power-On-Start-Up The SCADA/EMS & REMC system shall automatically restart itself when input power is interrupted and restored. System start-up shall include Server start up, initialization of all network devices, initialization of peripheral devices, initialization of all communications with data sources and other control centers, resumption of all SCADA/EMS & REMC functions and notifications to the users that startup has been completed. System power-on startup shall be completed within 5 (five) minutes or earlier. | This Para Deleted |
|  | Vol. II, Part-B, Section-6, Clause-6.9, | Database and Display ..It shall be possible to synchronize databases used for development, display building and source code on daily basis automatically and manually both… | Database and Display Replace with ..It shall be possible to synchronize databases used for development, display building and source code of Project specific API/scripts/configurations etc. on daily basis automatically and manually both… |
|  | Vol. II Part-B, Section – 7, Clause no. –7.11 | Criteria for Successful Operation The system shall be designed to meet the total system availability of 99.95%. That is, the ratio of total operational time minus downtime to total operational time shall be equal to or greater than 99.95%. Total operational time shall not include the hold time. | Criteria for Successful Operation Replace with The system shall be designed to meet the total system availability of 99.95%. That is, the ratio of total operational time minus downtime to total operational time shall be equal to or greater than 99.95%. Also, the resource utilization (RAM, CPU) of the servers, workstations etc. shall not exceed the maximum utilization as specified in Part-B, appendix-D. Total operational time shall not include the hold time. …….. |
|  | Vol. II Part-B, Section-8, Clause No.-8.3.4 | A. SMS Interface …Contractor shall take services of SMS service provider and integrate the SMS interface with SMS service provider services to achieve SMS delivering functionality. Contractor shall take the services of SMS service provider for entire contract period (including extension of contract, if any). The contractor shall also provide services of SMS service provider for testing purposes during FAT, SAT etc. at its own cost. The interface application shall be preferably hosted in web system to securely connect with SMS service provider services through use of encrypted APIs. However, the provided solution shall meet the cyber security related guidelines/policy envisaged in the technical specification. Keeping cyber security aspects in design, SMS services from govt. agencies such as NIC etc. shall be preferred. As a minimum, following functionality shall be provided by contractor in the SMS interface at RLDC and SLDCs: …………. | A. SMS Interface Replace with …Contractor shall integrate the SMS interface with SMS services provided by the owner to achieve SMS delivering functionality. The owner shall provide SMS services before the site installation. However, the contractor shall provision SMS services during FAT at its own cost. The interface application shall be preferably hosted in web system to securely connect with SMS service provider services through use of encrypted APIs. However, the provided solution shall meet the cyber security related guidelines/policy envisaged in the technical specification. As a minimum, following functionality shall be provided by contractor in the SMS interface at RLDC and SLDCs: …………. |
|  | Vol. II Part-B, Section-8, Clause No.-8.3.4 | A. SMS Interface m) SMS Interface application shall be configured as redundant in Main Control Centre and Backup Control Centre utilizing the same SMS service provider as envisaged in BoQ. n) Any unused quota of yearly SMS service provider (as envisaged in BoQ) shall be carry forward to subsequent years for utilization. | A. SMS Interface Replace with m) SMS Interface application shall be configured as redundant in Main Control Centre and Backup Control Centre n) Deleted |
|  | Vol-II Part- B, Section 9, Clause 9.2.2 | Remote Diagnostic The contractor shall indicate number of public IPs and bandwidth requirement to be required for remote diagnostics. | Remote Diagnostic Replace with .…Public IP shall be provided by the owner. Inserted new para The new para is attached at Annexure-A. |
|  | Volume II Part-B, Section-9, 9.2.5 Cyber Security Requirements | 9.2.5 Security Information and Event management (SIEM) - Create custom remediation packages to address recurring configuration issues, remove unauthorized files and applications, and patch software. | 9.2.5 Security Information and Event management (SIEM) This Bullet DELETED |
|  | Vol. II Part-B, Section-9, Clause No.- 9.2.9 | Database Development System (DDS)/Program Development System (PDS) as a test bench for Cyber Security Requirement A Test bench PDS i.e. (as specified in section 4.3.6) PDS shall be delivered by the Contractor. Along with functions defined in that section, this will be used for following purposes also- a) This system shall also be used as a Test bench for Cyber security and shall accordingly be equipped with firewall, antivirus and enable mode wherein threat scenarios can be tested with configured security elements before implementing on the main/production system. b) This Test bench for Cyber security shall also be used for VAPT (Vulnerability Assessment & Penetration Tests) e.g., OS fingerprinting, Port scanning, etc. | Replace with Test Bench for Cyber Security The revised para is attached at Annexure-A. |
|  | Vol. II, Part-B, Section-12, Clause-12.1.1, Profile of Ladakh | The UT of Ladakh is in the process of establishing the EABA as per the SAMAST guidelines. At present, the EABA is being managed by the JKPTCL and it is being manually done. However, the EABA mechanism shall gradually be independently managed by Ladakh. The details of various entities existing and future i.e. DISCOM, IPPs, State generators, Open access Customers, Renewable energy Generators shall be shared during detail engineering. | Replace with The UT of Ladakh is in the process of establishing the EABA in this project. At present, it is being manually done. The details of various entities existing and future i.e. DISCOM, IPPs, State generators, Open access Customers, Renewable energy Generators shall be shared during detail engineering. |
|  | Vol. II, Part-B, Section-12, Clause-12.2, System Design Outline | d. The web-based GUI shall be sized to support 100 concurrent clients/users for providing access to application/module. There shall be no limitation on the number of named users. Each user shall be assigned to a user type. | d. The web-based GUI shall be sized to support 100 users with 20 concurrent clients/users for providing access to application/module. There shall be no limitation on the number of named users. Each user shall be assigned to a user type. |
|  | Vol. II Part-B, Appendix-B SAMPLE REPORTS & DISPLAY FORMATS | B6. Sample Trend Displays B27: Text Transfer in ICCP: | Replace with B6. Sample Trend Displays attached at Annexure A B27: Text Transfer in ICCP: Deleted. |
|  | Vol. II Part-B, Appendix-C | Table 5 - DESIGN PARAMETERS FOR USER INTERFACE Name; Design Capacity; Execution Rate. TREND (Online) in SCADA. c) Samples per trend variable; 10,000. | Table 5 - DESIGN PARAMETERS FOR USER INTERFACE Name; Design Capacity; Execution Rate. TREND (Online). c) Samples per trend variable; - Minimum 1500 in real time - 10,000 in SCADA-Historian (auto refresh). |
|  | Vol. II Part-B, Appendix-C | Table 5 - DESIGN PARAMETERS FOR USER INTERFACE Name; Design Capacity; Execution Rate. ALARMS. Alarm priority levels; 10. Alarm Message Recording on auxiliary memory; 1,00,000. EVENTS. Event Message Recording on Auxiliary memory; 1,00,000. | Table 5 - DESIGN PARAMETERS FOR USER INTERFACE Replace with Name; Design Capacity; Execution Rate. ALARMS. Alarm priority levels; 8. Alarm Message; Minimum 20,000 Alarms on auxiliary memory 1,00,000 alarm to be displayed (auto refresh) either through SCADA or SCADA-Historian; Real time On-demand. EVENTS. Event Message; Minimum 20,000 Events on auxiliary memory 1,00,000 event to be displayed (auto refresh) either through SCADA or SCADA-Historian; Real time On-demand. |
|  | Vol. II Part-B, Appendix-C | TABLE 6 - Design Parameters for Configuration Characteristics (Specification Reference -Section 4 & 6) Server failover Function Period < 30 secs 60 sec Function Period > 30 secs 120 sec Server Start-Up Hot Start 2 minutes Warm Start 3 minutes Cold Start 5 minutes Device failover 30 sec | TABLE 6 - Design Parameters for Configuration Characteristics (Specification Reference -Section 4 & 6) Replace with Server failover 30/120 sec for Server (Refer Section 6.6.1) and 60 sec for Historian Application restart - 2 minute for all applications (except EMS application) - 3 minutes for EMS application - 5 min for Historian application Server Restart (hard/soft reboot) 10 minutes Device Restart 5 minutes Device failover 30 sec |
|  | Vol. II Part-B, Appendix-D | Table 1- PERFORMANCE REQUIREMENTS (iv) ¦ Display (including Trends) update rate ¦ Every 2 sec for 4 displays together to be completed in 0.5 secs. Added new point(xviii) | Table 1- PERFORMANCE REQUIREMENTS Replace with (iv) ¦ Display (including Trends) update rate ¦ Displays shall be updated every 2 sec (periodicity of update) and Callup of 4 displays together shall be completed in 0.5 secs. (execution time) xviii) ¦ Callup and Display of data in historian dashboard ¦ within 30 secs |
|  | Vol. II Part-B, Appendix-D | Table 1- PERFORMANCE REQUIREMENTS (x) ¦ Video projection system display update rate (Shall be performed during SAT) ¦ Every 2 sec for 4 displays together to be completed in 0.5 secs. | Table 1- PERFORMANCE REQUIREMENTS Replace with (x) ¦ Video projection system display update rate (Shall be performed during SAT) ¦ Displays shall be updated every 2 sec (periodicity of update) and Callup of 4 displays together to be completed in 0.5 secs. (execution time) |
|  | Vol. II, Part- B, Appendix - E: | Appendix - E: Questionnaire Question Nos: 18(d), 24, 27, 156, 159, 165 | Appendix - E: Questionnaire Q 18(d) Appendix C to be referred as Appendix F. Q 24. Appendix C to be referred as Appendix F. Q 27 Max display 25 to be referred as Max display 20 Q 156 Appendix B (B27) to be referred as Appendix B(B19). Q 158 Appendix B (B34-C) to be referred as Appendix M. Q 165 A sample display is attached in Appendix B to be considered as deleted. |
|  | Vol. II Part-B, Appendix-E, Q.129 | Appendix - E: Questionnaire Q.129 Provide an availability analysis for the proposed configurations to meet an availability goal of 99.9%. The analysis shall include the mean time between failures (MTBF) and mean time to repair (MTTR) of all components, and the historical, statistical basis for the analysis. Specific assumptions on availability of spare parts, maintenance responsibility etc. not in line with proposed contract shall be listed. The analysis shall also present the availability for individual devices. | Appendix - E: Questionnaire Replace with Q.129 Provide an availability analysis for the proposed configurations to meet an availability goal of 99.95%. The analysis shall include the mean time between failures (MTBF) and mean time to repair (MTTR) of all components, and the historical, statistical basis for the analysis. Specific assumptions on availability of spare parts, maintenance responsibility etc. not in line with proposed contract shall be listed. The analysis shall also present the availability for individual devices. |
|  | Vol. II, Part- B, Appendix - G - Bill of Quantity & Price Schedule | Appendix - G: Bill of Quantity | Appendix - G: Bill of Quantity Replace with Revised, Vol. II, Part- B, Appendix - G - Bill of Quantity for SCADA/EMS & REMC System are attached as Annexure-G1. |
|  | Vol. II, Part-B, Appendix-H, Hardware DRS, Table no. -2 | Servers: 2.1 SCADA/EMS 2.2. Program Development (PDS/DTS) Server & Test Bench 2.3. Historian Server along-with GUI, Report Generation Application 2.4. Repository Server | Replace with Servers: 2.1 SCADA/EMS Server 2.2. Program Development (PDS) Server 2.3 Test Bench PDS 2.4. Historian Server along-with GUI, Report Generation Application 2.5. Repository Server 2.6. DTS Server |
|  | Vol. II, Part-B, Appendix-H, Hardware DRS, Table no. -3 | Servers: 3.1.Data Replica Server 3.2.ICCP Application 3.3.CFE Application 3.4. Identity & Patch Management 3.5. Server Management Console 3.6. NMS | Replace with Servers: 3.1. Data Replica Server 3.2. ICCP Application 3.3.CFE Application 3.4. Identity Management Server 3.5. Server Management Console 3.6. NMS 3.7 Patch Management Server 3.8 DRS DMZ Servers |
|  | Vol-II Part- B, Appendix-H: Hardware Specifications, Table no. -4.1 | 4.1 FC Switch for SAN Storage Point no. 4: Interface ports ** 16Gbps FC ports | 4.1 FC Switch for SAN Storage Replace with Point no. 4: Interface ports 24 **nos (16 Gbps FC ports |
|  | Vol-II Part- B, Appendix-H: Hardware Specifications, Table no. -5 | Inserted new Note after Table-5 | Inserted ** NOTE: Storage capacity of SAN and NAS doesn’t include the SIEM logs storage capacity (as per TS requirement). Log storage capacity of SIEM varies from OEM to OEM as per compression ratio, hence, storage space for SIEM log shall be considered additionally over and above the specified SAN storage capacity for the control centre without any additional cost to Owner. |
|  | Vol. II, Part-B, Appendix-H, Hardware DRS, Table no. -8 | LAN Switches: a. 24 Port L3- LAN switch for SCADA/EMS LAN b. 24 Port L3- LAN switch for Historian LAN c. 24 Port L3- LAN switch for External DMZ LAN d. 24 Port L3- LAN Switch for ICCP/RTU LAN e. 24 Port L3- LAN Switch for Server Management LAN f. 24 Port L3- LAN Switch for Data LAN | Replace with LAN Switches: a. 24 Port L3- LAN switch for SCADA/EMS LAN b. 24 Port L3- LAN switch for Historian LAN c. 24 Port L3- LAN switch for External DMZ LAN d. 24 Port L3- LAN Switch for ICCP/RTU LAN e. 24 Port L3- LAN Switch for Server Management LAN f. 24 Port L3- LAN Switch for Data LAN g. 24 Port L3- LAN Switch for firewall and routers h. 24 Port L3- LAN Switch for SMC (Server Management Console) LAN Point no. 4: General (new point s.no. f. added) f. Switch shall be non-blocking and shall have wire-speed. |
|  | Vol. II Part-B, Appendix-H Hardware DRS | Table no.-7 7. Router cum Firewall for ICCP & RTU Communication, Remote Console and for External World Connectivity: Point No. 4(b): The Router should have minimum 2 GB of on-board/inbuilt DRAM/RAM for data plane + control plane processes and 4 GB Flash. Point No. 4(e): Router should be IPv6/USGv6 Certified/IPv6 logo ready Point No. 8 Routing Protocol: Static Routes, OSPFv2, OSPFv3, BGP4, MP-BGP, BFD, IPCP, IP forwarding, Policy based routing, VLAN & MPLS etc. Point No. 14: The Router shall have capability to add on demand IPSec VPN tunnels dynamically established hub -to-spoke IPSEC tunnels Note: However, the no of ports in a router shall be as per the network architecture & requirement at site and shall have 50% spare ports. | Table no.-7 7. Router cum Firewall for ICCP & RTU Communication, PDS, Remote Console and for External World Connectivity Replace with Point No. 4(b): The Router should have minimum 2 GB of on-board/inbuilt DRAM/RAM for data plane + control plane processes and min 1 GB Flash Point No. 3(e): Router should be IPv6 ready from day one. Point No. 8 Routing Protocol: Static Routes, OSPFv2, OSPFv3, BGP4, MP-BGP, BFD, IP forwarding, Policy based routing, VLAN & MPLS etc. Point No. 14: The Router shall have capability to add on demand IPSec VPN tunnels established hub -to-spoke IPSEC tunnels Note: However, the no of ports in a router shall be as per the network architecture & requirement at site. |
|  | Vol-II Part- B, Appendix-H-1: Software Specifications | 3. SIEM Sl no. 12 Logs must be retained for at least three years (3 months online and remaining offline/ compressed) on centralized storage (SAN/NAS). All logs must get auto archived on centralized storage directly from Log management layer and archived logs must be readable from archival/ central storage directly. | 3. SIEM Replace with Sl no. 12 Logs must be retained for at least one year (3 months online and remaining offline/ compressed) on centralized storage (SAN/NAS/Server). All logs must get auto archived on centralized storage directly from Log management layer and archived logs must be readable from archival/ central storage directly. Storage capacity of SAN and NAS doesn’t include the SIEM logs storage capacity (as per TS requirement). Log storage capacity of SIEM varies from OEM to OEM as per compression ratio, hence, storage space for SIEM log shall be considered additionally over and above the specified SAN storage capacity for the control centre without any additional cost to Owner. |
|  | Vol-II Part- B, Appendix-H-1: Software Specifications | 4. Identity Management System Point no. 11. The solution should support risk-based policies be created in the solution to support notification/ alerting when user risk profiles change. Point no.13. The solution should detect and alert on role violations before assigning roles to users. Point no.16. The solution should provide out-of-the-box connectors for automatically pushing changes to enterprise IT systems. | 4. Identity Management System Replace with Point no. 11. The solution should support risk-based policies be created in the solution to support notification/ alerting when user risk profiles change (location of log in, type of browser, type of LAN, time). Point no.13. The solution should detect and alert on role violations before assigning roles to users such as role violations alert in case of assignment of network admin role and database admin role to a user. Point no. 16. The solution should provide out-of-the-box connectors for automatically pushing changes to IT systems (such as NMS, NAC etc. supplied in this project) |
|  | Vol. II Part-B, Appendix-I | A.2 Minimum Information to be associated with an analog for Time block (for each 15 min) • Reactive Energy as per SEM philosophy | A.2 Minimum Information to be associated with an analog for Time block (for each 15 min) Replace with • Reactive Energy as per Owner provided SEM (Special Energy Meter) philosophy: |
|  | Vol. II Part-B, Appendix-O, List of RE Pooling Station | List of RE Pooling Station | Replaced with Revised List of RE Pooling Station attached at Annexure-A. |
|  | Vol. II Part-C, Section-2, Clause 2.5.2 | Display …Front Panel 7” or more Graphical Display: The UPS control panel shall provide a touch color graphic display for indication of UPS status, metering, battery status, alarm/event log, and advanced operational features….. | Display Replace with …The UPS control panel shall have front facia display for indication of UPS status, metering, battery status, alarm/event log, and advanced operational features…. |
|  | Vol-II Part- C, Section 2, Clause: 2.9 | Enclosures/Earthing ............ Modules and subassemblies shall be easily replaceable and maintainable with front access only. .......... | Enclosures/Earthing Replace with .......... Modules and subassemblies shall be easily replaceable and maintainable. ........... |
|  | Vol-II Part- C, Section 3, Clause: 3.0 | Introduction … The supplier, supplying the cells/batteries as per this document shall be responsible to replace/repair free of charge, the battery/cell becoming faulty, owing to defective workmanship or material. Contractor shall be responsible for the replacement of faulty battery cells during entire period of contract (including extension of contract, if any). Irrespective of the design/expected life of the supplied batteries, Replacement of faulty batteries and or entire battery bank up to the completion of one year DLP and 6 years AMC period including extension of contract, if any, shall be in the scope of the contractor, without any cost implication to the Owner. Batteries shall be tested and maintained as per the code mentioned in Indian Standard IS: 14782:2000. As per this standard, the Contractor shall periodically (quarterly) determine whether the rating of battery is holding up using capacity tests. Also, C10 Capacity test shall be done periodically (yearly), to determine whether the rating of battery is holding up using capacity test. If the battery capacity is less than 80% of its design value in any of the cases, the battery shall have to be replaced by contractor during entire period of contract (including extension of contract, if any) without any cost implications to owner. If number of cells replaced(cumulative) in battery bank exceeds more than 25% of total battery bank then contractor shall replace that entire battery bank without any additional cost to the Owner during entire period of contract (including extension of contract, if any). | Introduction Replace with ….The supplier, supplying the cells/batteries as per this document shall be responsible to replace/repair free of charge, the battery/cell becoming faulty, owing to defective workmanship or material during entire period of contract without any cost implication to the Owner. Batteries shall be tested and maintained as per the code mentioned in Indian Standard IS: 14782:2000. Capacity test @ C10 shall be done periodically (yearly), for assessment of health of the battery bank to determine charge holding capacity of battery bank. The conditions for batteries/battery bank replacement shall be as per the provisions mentioned under Clause 1.12, Section 1, PART A of technical specifications along-with other scope of works specified under the contract. |
|  | Vol- II, Part-C, Section 5, Clause-5.1 | Power Cables All external power cables i.e., LT Panel to Input ACDB/UPS shall be stranded Aluminum conductor, armoured XLPE/PVC insulated and sheathed, 1100V grade as per IS 1554 Part-I. The conductor for the Neutral connection from UPS to Output ACDB shall be sized 1.8 times the size of the Phase conductors to take care of the non-linear loads. However, all other cables i.e., between UPS and Battery bank / UPS, ACDB to Distribution Box, Load /all inter-panel cabelling etc. shall be of copper conductor (Armoured/ flexible type, which will be decided by Employer/owner, wherever applicable). | Power Cables All external power cables i.e., LT Panel to Input ACDB/UPS shall be stranded Copper conductor, armoured XLPE/PVC insulated and sheathed, 1100V grade as per IS 1554 Part-I. The conductor for the Neutral connection from UPS to Output ACDB shall be sized 1.8 times the size of the Phase conductors to take care of the non-linear loads. All cables such as between UPS and Battery bank / UPS, ACDB to Distribution Box, Load /all inter-panel cabelling etc. shall be of copper conductor (Armoured/ flexible type, which will be decided by Employer/owner, wherever applicable). |
|  | Vol-II PART-C Section 7, Clause 7.2 | Scope of Work a) …….. . if not replenished/replaced immediately, shall be replenished /replaced within 15 Days at site. c) Monthly and quarterly report of routine and breakdown maintenance will be forwarded to Owner coordinator for review & comments. The report should be submitted so as to reach Owner office by 7th day of every month. d) Contractor shall repair/replace faulty cards/modules or equipment identified during the maintenance within fifteen (15) days. | Scope of Work Replace with a) ……. if not replenished/replaced immediately, shall be replenished /replaced within 45 Days at site. c) Monthly/Quarterly reports (as applicable) for Routine and Breakdown Maintenance will be forwarded to Owner coordinator for review & comments. The report should be submitted so as to reach Owner office within 7th day of each due month. d) Contractor shall repair/replace faulty cards/modules or equipment identified during entire contract period. |
|  | Vol. II Part-C, Section-7, Clause-7.4.1 | 7.4.1 Scope of Maintenance of Batteries & UPS Batteries shall be tested and maintained as per the code mentioned in Indian Standard IS: 14782:2000. As per this standard, the Contractor shall periodically (quarterly) determine whether the rating of battery is holding up using capacity tests. Contractor shall be responsible for the replacement of faulty battery cells during entire period of contract (including extension of contract, if any). Irrespective of the design/expected life of the supplied batteries, Replacement of faulty batteries and or entire battery bank up to the completion of one year DLP and 6 years AMC period including extension of contract, if any, shall be in the scope of the contractor, without any cost implication to the Owner. Also, C10 Capacity test shall be done periodically (yearly), to determine whether the rating of battery is holding up using above test. If the battery capacity is less than 80% of its design value in any of the cases, the battery shall have to be replaced by contractor during entire period of contract (including extension of contract, if any) without any cost implications to owner. If number of cells replaced(cumulative) in battery bank exceeds more than 25% of total battery bank then contractor shall replace that entire battery bank without any additional cost to the Owner during entire period of contract (including extension of contract, if any). | 7.4.1 Scope of Maintenance of Batteries & UPS Replaced with ….. Batteries shall be tested and maintained as per the code mentioned in Indian Standard IS: 14782:2000. Capacity test @ C10 shall be done periodically (yearly), for assessment of health of the battery bank to determine charge holding capacity of battery bank. The supplier, supplying the cells/batteries as per this document shall be responsible to replace/repair free of charge, the battery/cell becoming faulty, owing to defective workmanship or material during entire period of contract without any cost implication to the Owner. The conditions for batteries/battery bank replacement shall be as per the provisions mentioned under Clause 1.12, Section 1, PART A of technical specifications along-with other scope of works specified under the contract. |
|  | Vol. II Part-D, Section-2, Clause-2.6 | Expected Battery Life ……However, irrespective of the design/expected life of the supplied batteries, Replacement of faulty batteries and or entire battery bank up to the completion of one-year DLP and 6 years AMC period, shall be in the scope of the contractor, without any cost implication to the Owner. | Replace with Expected Battery Life for DCPS ……Batteries shall be tested and maintained as per the code mentioned in Indian Standard IS: 14782:2000. Capacity test @ C10 shall be done periodically (yearly), for assessment of health of the battery bank to determine charge holding capacity of battery bank. The conditions for batteries/battery bank replacement shall be as per the provisions mentioned under Clause 1.12, Section 1, PART A of technical specifications along-with other scope of works specified under the contract. |
|  | Vol-II PART-E, Section-1 | Video Conferencing Equipment | Video Conferencing Equipment Replace with Revised TS is attached at Annexure-A. |