Annexure-A to Amendment of technical specification (Volume-II)

- Part-A, Section -1, Clause:1.20

1.20 Maintenance and Support Services Scope

The Contractor shall be responsible for the maintenance and support services of entire systems (Hardware and Software) supplied under the project during entire period of the Maintenance contract of the maintenance contract.

Maintenance and support services shall include various scopes specified under various sections of technical specifications which inter-alia includes following without any additional cost to owner:

1. OEM Back-to-back Support during one-year DLP and 6-year AMC:

- The Contractor shall have OEM back-to-back support from OEMs for all the supplied system items (Hardware and Software) under the project till completion of AMC period.

- OEM back-to-back support shall mean, OEM back-to-back warranty and support from OEMs for all the supplied system items (Hardware and Software) under the project. OEM back-to-back shall also include all patch supports (including security patches), replacement of hardware/software from OEM in case of, if OEM discontinues or declared end of support/end-of-life, whichever is later for any item supplied items (software/hardware) under the contract.

- During the period of one year DLP and 6 year AMC, if OEM discontinues or declares end of support/end-of-life, whichever is later, for any item supplied (Hardware/Software) under the contract, the contractor has to replace such hardware, software or both, depending on software or hardware dependencies on each-other, without any additional cost to the Owner, with appropriate response time from OEMs. The items, Security Solutions/Operating System/Databases, are also considered Hardware/Software items. The replacement due to EOL and EOS of Hardware/software shall be required if it has become either non-functional or the patches/updates have been discontinued from the OEM.

- OEM back-to-back warranty shall be provided for a period of seven years from the completion of operational acceptance, for all the supplied items (Hardware/Software).

- SCADA/EMS and REMC applications shall be under OEM warranty & support during the period of one-year DLP and 6 years AMC.

- In case of item(s) (Hardware and Software), supplied under the contract, becomes non-functional/degraded in performance during the contract period, the same shall be replaced by the Contractor/respective OEM without any additional cost to the Owner. Replacement shall be of either same or higher configuration considering required performance specified under the contract and either from the same OEMs or from approved OEMs under the contract.

- In case of requirement(s) of any new hardware/software solution which is not envisaged/supplied under this contract, need to be deployed to meet the compliance requirements of various advisories issued by Government bodies time-to-time during the contract period of one-year DLP and 6-year AMC, the same shall be provided/procured by the Owner. However, integration of such additional hardware/software (procured by owner) in the SCADA/EMS and REMC system, for complying statutory guidelines, shall be under the Contractor’s scope without any additional cost to the Owner/Employer.

- If any inter-dependency in replacement of either hardware or software, necessary suitable solution shall be provided by the contractor without any additional cost to Owner as per above provisions.

- Part-A, Appendix-L, Type Test Validity

Table 1 – keeping req Validity of Equipment

| S.No. | Name of Equipment | Validity of Type Test (in Years) |
| --- | --- | --- |
| 1. | Battery | 7 |
| 2. | Battery Charger (DCPS) | 7 |
| 3. | UPS | 5 |
| 4. | RTU | 7 |
| 5. | Transducer | 10 |
| 6. | Cable (Power, Control) | 10 |
| 7. | Cable (FO) | 5 |
| 8. | Auxiliary Relays | 7 |

- Part-A, Section-4, Maintenance & Support Services

Table 4.5 Responsibility Matrix

| Item | Task | Owner | Contractor |
| --- | --- | --- | --- |
| 1.0 | PROBLEM IDENTIFICATION |  |  |
| 1.1 | Root cause analysis to determine whether the fault is attributable to Hardware or Software. | ---- |  |
| 1.2 | Resolution of problems involving third party maintainer where there is uncertainty whether the root cause is hardware or software. | ---- |  |
| 2.0 | SOFTWARE PROBLEM RESOLUTION |  |  |
| 2.1 | Report problem |  | A |
| 2.2 | Problem identification | ------ |  |
| 2.3 | Provide or recommend corrections, temporary patches, workarounds or other fixes to system problems. | ---- |  |
| 2.4 | Install and test corrections, temporary patches, workarounds or other fixes to system problems. | ---- |  |
| 3.0 | ROUTINE SOFTWARE SUPPORT |  |  |
| 3.1 | Build and maintain database, displays and reports. | ---- |  |
| 3.2 | Perform system back-ups. | ---- |  |
| 3.3 | Restore or reinstall software from back-ups. | ---- |  |
| 3.4 | Monitor system logs (part of remote monitoring service) | A |  |
| 3.5 | Maintain system (Hardware, Software, Network etc.) logs | ---- |  |
| 3.6 | Maintain user accounts |  | A |
| 4.0 | HARDWARE PROBLEM RESOLUTION |  |  |
| 4.1 | Report problem |  | A |
| 4.2 | Defining problem | ------ |  |
| 4.3 | Troubleshoot problem to diagnose if it is software- related or hardware-related | ---- |  |
| 4.4 | Identify failed component, replace failed components in the system using parts from spares inventory | ---- |  |
| 4.5 | Restore operation of repaired/replaced equipment | ---- |  |
| 5.0 | HARDWARE SPARE PARTS |  |  |
| 5.1 | Manage local spares inventory | ---- |  |
| 5.2 | Replenish local spares inventory | ---- |  |
| 6.0 | INTEGRATION AND DATABASE WORK AT CONTROL CENTRE END |  |  |
| 6.1 | RTU/DCPC/TERMINAL SERVER Integration | ---- |  |
| 6.2 | ICCP Integration | ---- |  |
| 6.3 | WAMS/REMC/Other application integration | ---- |  |
| 6.4 | Database and Display | A |  |
| 7.0 | AUXILIARY POWER SUPPLY SYSTEM |  |  |
| 7.1 | Troubleshoot problem to diagnose | ---- |  |
| 7.2 | Replenish local spares inventory | ---- |  |
| 8.0 | CYBER SECURITY MONITORING |  |  |
| 8.1 | Patch/Signature/Update/firmware Updates | A |  |
| 8.2 | Cyber Security Monitoring | A |  |
| 8.3 | Six monthly Cyber Security Audits | A |  |
| 8.4 | Implementation of Recommendations during Audit | ---- |  |
| 8.5 | Implementation of Monitoring and compliance for Critical Infrastructure Protection |  |  |
| 8.6 | Maintenance of Spares | ---- |  |
| 9.0 | RTU & DCPS MAINTENANCE | ---- |  |
| 10.0 | VPS & VC MAINTENANCE | ---- |  |

- Vol-II, Part-B, Introduction

#### PART B

INTRODUCTION

PART B: INTRODUCTION

Introduction

Part B of Volume-II describes the technical specifications for SCADA/EMS & REMC System, to be procured as a part of this Project. The description includes requirements in respect of   Control Center computer hardware and software, SCADA/EMS & REMC functions, user interface, testing, maintenance etc. The supplier of the system shall ensure that support services for maintenance are also available even after the maintenance period.

Proposed System

The SCADA/EMS & REMC system shall establish a modern computer and control system at the Main & Backup Control Centre. The technical requirements for various functions of the SCADA/EMS & REMC system are described in subsequent sections.

The Bidders are encouraged to offer their standard products that meet or exceed the specification requirements. However, the proposal will be judged by its conformance to the Specification. These products may be provided from their in-house baseline offerings, the computer manufacturer and established third-party software suppliers.

The System Design Parameters and Performance requirements for SCADA/EMS & REMC system are specified in Part B Appendices C & D.

All the variable parameters of SCADA/EMS & REMC System, which require adjustment from time- to-time, shall be defined in the database and shall be adjustable by system users through graphic user interface displays. All periodicities and time intervals contained in the Specification that define these parameters shall be considered as initial values to be used for performance purposes. The adjustments made to parameters by the dispatcher, or the programmer shall become effective without having to reassemble or recompile programs.

The specific requirements for output results are described along with the other requirements of each function. However, all results shall be stored in a form accessible for display and printing, whether explicitly specified in the relevant subsection. The application result storage details shall be submitted during detail design stage. The system shall be designed such that failure of a single server or single peripheral device shall not render the system unavailable.

Critical & Non-Critical functions

SCADA/EMS & REMC System functions are classified as Critical or Non-critical functions. At control centre every critical function must be supported by sufficient hardware and software redundancy to ensure that no single hardware failure will interrupt the availability of the functions for a period exceeding the failover time defined in the specification.

Non-critical functions may not be supported by hardware redundancy and can be suspended in case of non-availability of corresponding hardware.

- The following functions are classified as Critical functions:

  - SCADA System Functions

  - EMS functions

  - REMC Forecasting & Scheduling Application

  - FEP and ICCP System

  - Historian system

  - User Interface Requirements

  - Network Management system

  - Web Applications

  - Cyber Security System (Firewalls, Routers, Switches etc.)

  - Dispatcher Training simulation (DTS)

- The following functions are classified as non-Critical functions:

  - Database modification and generation.

  - Display modification and generation.

  - Report modification and creation.

  - Software configuration and system generation.

  - Document Management System

  - Centralized Management System

  - Antivirus and Patch Management

  - SIEM

  - Anti APT Server

Organization of PART-B of the specification

Sections-1 through 11 and Appendices provide the requirements for SCADA/EMS system to be procured for this project as follows:

SECTIONS

SECTION 1: SCADA SYSTEM FUNCTIONS

SECTION 2: EMS FUNCTIONS

SECTION 3: USER INTERFACE REQUIREMENTS

SECTION 4: SYSTEM SOFTWARE REQUIREMENTS

SECTION 5: HARDWARE REQUIREMENTS

SECTION 6: CONFIGURATION CHARACTERISTICS

SECTION 7: INSPECTION &TESTING

SECTION 8: WEB AND SCHEDULING APPLICATIONS

SECTION 9: CYBER SECURITY REQUIREMENTS

SECTION 10 FORECASTING APPLICATION REQUIREMENTS

SECTION 11 RE SCHEDULING APPLICATION REQUIREMENTS

SECTION 12 ENERGY ACCOUNTING & BILLING APPLICATION

APPENDICES

APPENDIX A	GLOSSARY

APPENDIX B	SAMPLE REPORTS & DISPLAY FORMATS

APPENDIX C	SYSTEM DESIGN PARAMETERS

APPENDIX D	PERFORMANCE REQUIREMENT

APPENDIX E	QUESTIONNAIRE

APPENDIX F	SYSTEM SIZING

APPENDIX G	BILL OF QUANTITY FOR SLDC CUM REMC

APPENDIX H	HARDWARE AND SOFTWARE DATA REQUIREMENT SHEET

APPENDIX I	TENTATIVE DATA STRUCTURE FOR HISTORIAN SYSTEM

APPENDIX J	EXTRACTS OF IEC 62351-5 CLAUSE 11

APPENDIX K	PHILOSOPHY FOR DEVELOPMENT OF SCADA SYSTEM DISPLAYS

APPENDIX L	NETWORK TRUNCATION, EXTERNAL EQUIVALENCE AND RE MODELLING

APPENDIX M	HISTORIAN DASHBOARD

APPENDIX N	GUIDELINES ON NAMING CONVENTION IN SCADA DATABASE AT LOAD DESPATCH CENTRES

APPENDIX O	LIST OF RE POOLING STATION

------------------------------------------End of the Section---------------------------------

- Part-B, Section-2, Clause – 2.2.5.5

2.2.5.5 High Voltage Direct Current Model

The High Voltage Direct Current (HVDC) model shall represent the both, the DC transmission system and Back to Back station under Power System Model. The HVDC transmission system consists of DC transmission lines and associated converter stations and back-to-back stations without any DC Transmission line.

Each converter is an operating unit consisting of an AC switch, a converter transformer with OLTC, the DC valve, and a by-pass switch. AC harmonic filters and capacitor banks are connected to the bus on the AC side of the converter, which provide reactive requirements of converter. In addition, the converter is connected to the DC line through reactors and DC filters to limit fault currents and to smooth high frequency components of the DC current.

Reactive Power Controller (RPC) is provided in the DC transmission. The purpose of RPC is as follows:

a) Prevent over voltages

b) Keep AC voltage within limits

c) Control the reactive exchange with the AC system

d) Ensure that the maximum connectable shunts are not exceeded.

e) Ensure that the minimum number of AC filters are connected.

Typically, RPC has two operating modes:

I. Automatic: Filter/shunt capacitor switching is performed by RPC, without user action. II. Manual: Filter/shunt capacitor switching is performed by user action.

Transfer of control between Automatic and Manual modes is a user action and needs to be configured in a similar manner. The RPC also has the following two control modes in Automatic mode:

a) Reactive Control: RPC regulates the reactive power exchange with the AC network within a user-adjustable band of a reference value set by the user. Control is subject to constraints imposed by AC voltage limits or maximum connectable shunts.

b) Voltage Control: RPC orders appropriate filter switching whenever the AC bus voltage is outside limits set by the user.

The control modes are user-selectable and can be changed according to the needs of the AC system. The HVDC model should have the ability to include Multi-terminal HVDC (may be modelled with combination of two-terminal) and VSC (Voltage Source Converter) along with conventional models of HVDC also.

- Part-B, Section – 4

### 4.6.10 Development System

Two system has been envisaged one as a main development system and other as a Test PDS as per functionalities described herein under:

### 4.6.10.1 Development PDS System

The Development PDS system shall be considered as main development system which shall be used to keep full databases of all the SCADA/EMS System applications i.e. SCADA, EMS, PSA (Power System Application Database), ICCP, Data historian etc. This system shall meet all the requirements of database modeling, display building, reports building tool. It shall be the source for all online database of the SCADA/EMS system .

### 4.6.10.2 Test PDS System

The Test PDS system has been envisaged for integration and testing activities so that the Database and Display Development for the online system is not impacted.

The Test PDS system shall have all the SCADA/EMS applications (SCADA/EMS/ICCP/CFE)  running on a sample database/model.

The test PDS system shall have testing facility for integration of new RTU and new Control centres over the specified protocols before its integration with Real-time system as specified below:

- Integration of New RTU: The Test PDS system shall have the same functions of CFE.  It shall be used to test the integration of new RTU on all RTU protocols as envisaged in the specification. It will facilitate in validating all the functionalities of the CFE & SCADA such as data acquisition, supervisory control, communication monitoring, alarming as specified for SCADA application in earlier sections.

The test PDS system shall also have a ‘listen’ mode wherein the data exchanged between the online system and field RTUs is simultaneously monitored and updated in the database of the test PDS system. This is to facilitate testing of pending database changes on the Test PDS system without interfering with the existing communications on the online system.

- Testing of Integration of new control Centre: Test PDS System shall have the functions to test the integration of new Control Centre on ICCP with other Control Center. It shall model the new ICCP connections for both Main and Backup Control Centres, interfaces with the SCADA system (in Test PDS).

- SCADA/EMS Test bench : The Test PDS shall be setup to resemble the SCADA/EMS functionality including the interfaces between the RTU, CFE, ICCP, SCADA and EMS applications for testing and development. The application patches, Operating system patches, signature updates, security policy configuration, shall be tested on the test bench to analyse the impact of these modification on the functionalities of SCADA/EMS applications. It shall also be used for cyber security testing as described in Section 9.

The Test PDS System shall be able to connect to a new RTU and/or new Control Centre association as per architecture Appendix-D, Part-A. It shall test the communication, step-by-step as well as in continuous run mode for up to 24 hours, to observe the data acquisition/exchange process. During the continuous run mode, the data collected shall be stored in a temporary files /tables for review to assess effectiveness and stability of integration.

The Test PDS shall be able to continuously run for 24 hours the SCADA/EMS applications including the interface between the RTU, CFE, ICCP, SCADA and EMS on a sample database/model to assess the impact of a modification on normal functioning.

All relevant logs, for monitoring the communication with RTU and/or Control Centre under test and among the various functions  as defined for realtime SCADA/EMS system, shall be stored and presented/reported on similar displays.

The Hardware required for necessary connectivity including the interfaces with communication links shall be included as part of test bench PDS Hardware.

- Part-B, Section-9, Cyber Security Requirements

9.1.9 Test Bench for Cyber Security

The Test PDS system as mentioned in Clause 4.6.6.2, Section 4, Part B, shall be used for cyber security related testing of SCADA/EMS system as described below:

- Testing of patches for Operating System

- Testing of End Point, HIPS, antivirus signature updates, etc

- Testing of hardening/whitelisting policy

The Test PDS system shall have similar environment as production servers and accordingly be equipped with host firewall, antivirus/HIPS wherein threat        scenarios can be tested with configured security elements before implementing on the main/production system.

- Part- B, Section 9: Cyber Security Requirements

Clause 9.2.2 Remote Diagnostic

Remote diagnostic facility (either software or hardware or combination of both) shall be used for remote access to the systems/devices provided for SCADA/EMS and REMC support and shall be provided by contractor: The following minimum features are required but the contractor shall include any additional feature/function required to support the systems/devices supplied in this project.

- Remote Access Protocol Support:  It shall support various remote access protocols such as Remote Desktop Protocol (RDP), Virtual Network Computing (VNC), and SSH.

- Operating System Compatibility: It shall have compatibility with a wide range of operating systems, including Windows,  Linux  and the other Operating Systems of all supplied systems.

- Network Connectivity: This tool shall work over various network types, including LAN, WAN, VPN, and the Internet.

- Session and Screen Recording and Logging: This tool shall have the capability to record screen and remote sessions for auditing and troubleshooting purposes. Detailed logs of all activities on per user basis, shall be recorded for tracking changes and identifying issues.

- Authentication Features: The remote logins shall be on secured network (such as SSL over VPN etc.). The login shall be protected by a username & password entry. Two factor Authentication (OTP Based) shall be done by using perimeter firewall.

- Cross-Platform Compatibility: The ability to diagnose and manage various device types, including servers, workstations, laptops etc.

- Reporting and Analysis: This tool shall provide reporting capabilities (PDF, HTML etc.) to track each maintenance tasks.

- Remote Control and View: The ability to provide required access i.e. full control of a remote system or view-only access for observing and assisting users.

- Selected System: It shall be possible to assign selected systems (servers, workstations etc) on user basis. User shall not able to access system other than the assigned to the user.

- Part-B, Appendix-B, Sample Report and Display Format

B6.  Sample Trend Displays

  - Frequency Chart with Past Day

B. Trend of Frequency of two regions

C. Trend of Frequency of two regions

- Vol-II, Part-E, Video Conferencing Equipment TS

Volume-II

Part-E

VIDEO CONFERENCING EQUIPMENT

Table of Contents

1.1	Introduction	17

1.2	LCD Video Wall (LVW)	17

1.3	Controller Features	19

1.4	Multipoint Control Unit (MCU)	20

1.5	Video Endpoints	22

1.6	Camera	24

1.7	Wireless Microphone System	24

1.8	Accessories	24

1.9	FAT methodology for VC equipment	25

1.10	Technical Specifications for Wall Mount Speakers	25

1.11	Technical Specifications for Amplifier	25

VIDEO CONFERENCING EQUIPMENT

# Introduction

This section describes the functional and technical requirements of Video Conferencing Systems being supplied. The minimum hardware & software requirements are specified here, the Contractor shall assess the adequacy of the same & if any additional hardware, software & interfaces are required to meet all the functional requirements of the technical specifications, the same shall be included in the offer. The BOQ of the equipment’s to be supplied is indicated at Appendix-G, Part-B.

The Contractor shall supply the required furniture and panel with the system. Supplied Video Conferencing (VC) System consists of LCD Video Wall System, Multipoint Control Unit (MCU), Video End Point along with omnidirectional microphones, Camera, Wireless Microphone, and any accessory as per the BOQ.

There shall be a provision to conduct video conferencing between the Main Control Center and Backup Control Center without MCU and if any additional hardware/software is required to meet this functionality, Contractor shall supply the same to provide this feature.MCU will be required only when more than two control centers are involved in VC.

Wall mountable type LCD Video Wall System (LVWS) consists of LCD Video Walls (LVW) and associated Controller/ drivers shall be supplied by the Contractor. The Contractor shall supply LVWS with all necessary hardware, software, and interfaces, including LCD modules, supporting/mounting/fitting arrangement including cabling etc. to make the entire system operational.

# LCD Video Wall (LVW)

- The LVW shall be able to take Video signals (from CCTV/Dish TV/DVD Player & video conferencing unit) and Laptop Feeds. The LVWS shall enable users to display inputs from multiple sources/applications simultaneously in freely resizable and repositionable windows on entire display area to enable effective collaboration.

- LCD Video wall (LVW) shall be wall-mounted type.

- Other technical specifications required of LVW are given below: -

LCD video wall

| S.No. | Description of the Parameters |  |  |
| --- | --- | --- | --- |
|  | LCD wall features | Parameters | Offered by contractor |
|  | Display Type | LCD screen |  |
|  | Backlit | White LED, Full array |  |
|  | LED Lifetime | Minimum 50000 Hours |  |
|  | Module/Cube size | 55” diagonal |  |
|  | Video screen configuration (No. of modules) | As per BoQ |  |
|  | Display Colours | 16.7 million |  |
|  | Horizontal & Vertical viewing angle | > +1600 (approx.) |  |
|  | Minimum Resolution of each module | 1920x1080 (Full HD) |  |
|  | Driver/Operating System | OS: Preinstalled OEM Licensed Microsoft Windows Pro 64-bit or equivalent in Primary SSD hard-drive |  |
|  | Interface ports | 2*DP-in, 2*HDMI, 1*DP-out |  |
|  | Speaker Output | yes |  |
|  | Aspect ratio of each Module/Cube | 16:9 |  |
|  | Minimum Brightness | 170 candelas/sq.m |  |
|  | Brightness & Colour adjustable Manually | Yes |  |
|  | Contrast ratio (minimum) | 1500:1 |  |
|  | Operating temperature range | 160C to 300 C |  |
|  | Operating Relative Humidity | 20-80% non-condensing |  |
|  | Power supply (nominal) | AC 230V±5%, 50±5%, Hz |  |

# Controller Features

- The Controller of LVWS supplied with each set of Video walls shall have the following features as a minimum.

- Support 64 Bit latest Windows Operating System

- Quad Core or higher

- Minimum 16 GB expandable to 32 GB

- DVD-ROM, Keyboard & mouse with 2-buttom + wheel/button

- Internal Auxiliary Memory 480GB SSD minimum

- Common Monitor, Keyboard & Mouse (dual band wireless) for all controllers

- Redundant AC power supply

- Dual Gigabit Ethernet port

- Interface for CCTV

- Type of Vídeo Signals Supported-

- RGB Analog up to 1920x1200 (up to 165 MHz pixel clock)

- DVI up to 1920x1200 (Up to 165 MHz pixel clock)

- Interface for Video conferencing Equipment

- Interface for Laptop

- Controllers should be capable of mirror images through dual LAN.

- Four videos and three universal input ports.

- A Laptop with the installation kit for Video Conferencing system shall be provided to operate/control all Video Walls. The DRS for the Laptop shall be the same as

mentioned at Appendix-H (Hardware DRS), of Part-B Vol. II.

- VC equipment shall have only one interface point to connect controller. For further connection to remaining controllers, supplier shall include additional switch/distributer etc. as required to display VC output on all LVWs.

- Supplier shall offer OEM application software (with licenses) for wall setup source switching and other controls required for optimization of the display system. The software should be able to configure different layouts. The software shall be able to pre-configure various display layouts (arrangement of different windows) and access them at any time with a simple mouse click. The window can	be of different size and could contain display from different applications/sources. The software shall be able to push the screen content of a Laptop/Windows PC to be shown on the Display wall in scalable and moveable windows in real time environment. The Laptop/Windows PC shall be connected to the Controller. Necessary hardware required to run the application software shall be in the scope of vendor.

# Multipoint Control Unit (MCU)

Under this project, one number of MCU shall be supplied and installed at SLDCs. Technical Specifications of above is given below:

- CAPACITY

- MCU should be a Hardware/appliance solution of either 1U or 2U with all the accessories rack mount into 19-inch rack.

- Should have the ability to connect at least 12 video sites over SIP and H.323 protocols without cascading and MCU license shall be perpetual (no subscription based). At any point of time at least 12 Full HD total participants shall be able to join a meeting on MCU in any combination via VC end point, WebRTc, Application, software-based desktop, Mobile, Laptop/desktop etc.

- Up to 12 sites in continuous presence with auto layout and shall support voice switching.

- All video ports must support 30 fps of 1080p or better resolution.

- Shall support 2 Mbps or more bandwidth per port without any loss of ports at higher bandwidth.

- Minimum 8 layouts which can be accessed during a conference.

- Shall support Far end camera control.

- Should support combination of Full HD, HD & SD in the same conference.

- Shall support connections with remote users over the Internet. MCU shall support software-based desktop and webRTc to join from internet.

- It should support an external appliance-based recording & streaming solution of at least 500GB of video streams from each location and collectively in one grid and shall support 3 concurrent meetings at 1080p from day one.

- Shall support Active Speaker selection using voice switching and shall support automatic face detection and framing to create an optimized view of that single participant or group.

- Dedicated console port (serial/RJ45) or Web based management options for configuration/administration from network or a remote location.

- MCU shall support management tool for monitoring & managing ongoing meetings, creating meeting and directory.

- The MCU solution should support presentation sharing on H.239 or  BFCP through the video endpoint.

- Shall support user end and managed mute control.

- Dial-in and dial out facility in a conference without disturbing ongoing conference on SIP and H.323

- Shall support external recording and video-on-demand solutions.

- The solution must support to display participants in one monitor and presentation on the second monitor

- VIDEO STANDARDS

- Shall support H.261, H.263, H.263+ & H.264 video algorithms.

- Shall support H.239 or BFCP {Presenter and Presentation mode)

- AUDIO STANDARDS

- Shall support audio standards like: G.711, G.722, G.7Z2.1, G729A & AAC-LD/LC.

- Shall support individual site audio mute.

- ITU STANDARDS

- H.224/H.281 far end camera control

- NETWORK FEATURES

- 10/100/1000 NIC (RJ 45 connector) or better

- IPv4 & IPv6 support

- Diffserv or QoS support

- IP address conflict warning

- H.323 and SIP at 6 Mbps or more.

- USER INTERFACE & SECURITY

- Direct control from remote sites

- Web-based control

- Support for SNMP

- Support to operate in integration with existing industry standard MCUs and Video recorders.

- This MCU shall support 128 bit and 256-bit AES encryption on H.323 & SIP using H.235 for every participant without affecting any other feature, functionality, or port count. There should be no port loss when AES encryption is turned on.

- The complete MCU solution (MCU, Software and associated hardware) & Endpoints should be supplied from the same OEM.

# Video Endpoints

Video endpoints shall be installed at various control centres as listed in the BoQ. The technical specifications are as described below:

- CAPACITY

- End point must support 30 fps of 1080p or better resolution.

- Shall support 6 Mbps or more bandwidth.

- Minimum 5 pre-sets which can be accessed during a conference using remote.

- Shall support combination of HD & SD in the same conference.

- Shall support IP & SIP.

- VIDEO RESOLUTION

- Input for PC: 4K@15fps and 1080p

- Output for PC: 4K@15fps and 1080p

- VIDEO STANDARDS

- Shall support H.264AVC and H.265 or better video algorithms.

- Shall support H.239 & BFCP {Presenter and Presentation mode)

- Picture in picture facility.

- AUDIO STANDARDS

- Shall support audio standards like: G.711, G.722, G.772.1 or better.

- Shall support Automatic Gain control, Noise block & Instant Adaptation Echo cancellation.

- ITU STANDARDS

- H.224/H.281 far end camera control

- NETWORK FEATURES

- 10/100/100a NIC (RJ 45 connector) or better

- IPv4 & IPv6 support

- Diff serve or QoS support.

- H.323 and SIP at 6 Mbps or more.

- USER INTERFACE & SECURITY

- Direct control from remote sites

- Web-based control

- Support for SNMP

- Support to operate in integration with existing industry standard MCUs and Video recorders.

- This endpoint shall support 128 bit and 256-bit AES encryption on IP & SIP using H.235 for every participant without affecting any other feature, functionality or port count. There should be no port loss when AES encryption is turned on.

- VIDEO INPUT

- Shall have minimum one Full HD input from the camera.

- Shall have 1x HDMI/DVI/USB/HDCI for an external camera source.

- Shall have a minimum of one HDMI input for PC connectivity.

- VIDEO OUTPUT

- Shall	have minimum two HDMI Output integrating with TV/ Plasma/Projector/Video Walls

- Shall be capable of displaying main video on one Full HD Screen and presentation/dual video on another screen.

- AUDIO INPUTS

- Codec must support 3 microphone ports and bidder shall supply minimum 2 omni directional mics.

- Codec should support third party certified DSP via USB to connect 8 microphones.

- Should have minimum one PC audio in 3.5 mm jack.

- AUDIO OUTPUTS

- Should have Minimum 2 Audio Outputs; 3.5mm jack and HDMI.

- USB PASSTHROUGH

- Codec should have USB C Port to use VC system as an external camera and microphones when connected to a Laptop/PC over a single USB cable without using any external hardware, software components or converter to connect to any Cloud Based VC platform like Cisco Webex, Zoom, BlueJeans, Microsoft Teams, Google Meet, etc.

- Should support minimum 1080p60fps video transmission in USB Pass-thru mode.

- Other requirements of endpoint

- USB cable to be supplied.

- Endpoint should support a minimum 8"inch touch controller from the same OEM.

# Camera

- Camera shall be installed – to be supplied along with end point from the same OEM. The technical specification of the same is defined below:

- Shall support 1080p 60fps or better resolution.

- Shall have both auto or manual options in setting Focus and Brightness.

- Shall support 12 x or above optical zoom, minimum +/- 80-degree pan & +/- 10-degree tilt capability to operate in normal room illumination conditions.

- Shall support far end camera Control.

# Wireless Microphone System

The specification of the Microphone System is detailed below-

The number of microphones in each Control Centre shall be as per BoQ. Microphones should be immune to GSM noise caused by mobile phones. Microphones should have a wide band frequency response. Microphones should have buttons for muting and pairing and indications for the same. Shall be equipped power charger with base station for holding and charging microphones. Microphones shall be capable of providing a minimum of 6 hours of talk time on battery on full charge. The base station shall support interface with HD Video Conferencing System compatible to connect at least 8 microphones. The supplied microphones should have at least 02 lapel microphones. The system should support 220V AC, 50Hz input Power.

# Accessories

All necessary cable/accessories must be supplied along with for the interconnectivity with the Video Wall/Laptop to make videos conferencing fully functional. All power cord shall be with Indian Power Connectors. All other accessories must be supplied to ensure proper compatibility, connectivity, and functionality of the supplied video conferencing system.

# FAT methodology for VC equipment

Total BoQ quantity of the VC equipment supplied by the Contractor shall be tested under Factory acceptance testing (FAT) for acceptance. All required FAT tests as per approved FAT procedures, shall be performed. The physical verification and Power ON tests shall also be carried out as per the approved FAT procedure. The above requirement is tentative, the exact methodology for FAT shall be finalized during Detail Engineering stage.

# Technical Specifications for Wall Mount Speakers – 2 pairs

- Passive Two-way wall mount speakers with minimum 6.5-inch woofer and 1 inch tweeter.

- Frequency Range: 65 Hz to 19 kHz, 60 W rms continuous pink noise, 120 W RMS continuous program. 87 dB Spl.

- Coverage Angle: Horizontal: 115°, Vertical: 55° or better.

- Tapping: 32, 16 watt selectable @70/100 volt. Provided with 360-degree mounting accessories.

# Technical Specifications for Amplifier

- Dual Channel Class D amplifier with 100 watt per channel.

- Input: 2x balanced/unbalanced,

- Output: 2 channels @ 70/100V.

- THD+Noise: 0.1%,

- Signal to Noise ratio: 100 dB or better.

- Shall have protection from Clip limiting, thermal, short circuit.

- Shall meet Regulatory compliance: CE, ENERGY STAR, FCC RoHS, UL.

---------------------------------------------- End of Section --------------------------------------------

- Part-A, Appendix-D, NETWORK ARCHITECTURE

Network Architecture for CONTROL CENTRE

- Vol-II, Part-B, Appendix- O

List of RE Pooling Station

| List of Existing & Under construction RE Pooling Station (STU) or Point of Common Coupling (PCC) details |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| S.No. | Name of RE Project | Type | Location | Capacity (GW) | Remarks |
| 1 | Phyang RE Project | Solar | Taru (Leh) | 0.05 |  |
| 2 | Phey RE Project | Solar | Phey (Leh) | 0.01 |  |
| 3 | Pang RE Project | Solar/Wind (Hybrid) With Battery Storage | Pang (Leh) | 13 |  |
| 4 | Pashkum RE Project | Solar | Pashkum (Kargil) | 0.05 |  |
| 5 | Khangral RE Project | Solar | Khangral ( Kargil) | 0.005 |  |
| 6 | Zanskar RE Project | Solar | Zanskar (Kargil) | 0.005 |  |
| 7 | Shashithang RE Project | Wind/Solar (Hybrid) | Shasithang (Kargil) | 0.03 |  |
| Total |  |  |  | 13.15 |  |
| Note- The above list is tentative, the final list shall be shared at the time of detail engineering |  |  |  |  |  |