| S No | Clause | Provision of Bidding Documents | Bidder’s Query | POWERGRID's Reply |
| --- | --- | --- | --- | --- |
|  | Volume II Part-A, Page no-12, Clause no-1.8, (SLDC cum REMC system architecture | Figure 1.2 SLDC cum RLDC System Architecture | Current System architecture of SLDC CUM REMC only depicts the system architecture will be limited to REMC and not covers the building blocks of SAMAST and EABP applications. Hence required to kindly amend the architecture considering all the scope of applications & software as mentioned in the RFP | Refer Section –12 of technical specification. Bidders to comply Technical Specification. |
|  | Volume II Part-A, Section-1, General Information of the Project, 1.12, Scope of Work | b) Supply of REMC Forecasting and Scheduling applications and their integration with the SCADA/EMS applications and Historian system. | Please confirm if there is already an existing SCADA/EMS system. If yes, kindly provide the details. | There is no existing SCADA/EMS system in Ladakh. |
|  | Volume II Part-A, Section-1 General Information of the Project, 1.12, Scope of Work | e) The integration of new RTUs at the Control center end shall also be in the scope of the Contractor. Further, future bay integration shall not be treated as a new RTU integration during the AMC period, and any bay extension during AMC shall be in the scope of the contractor without any commercial implication to the Owner. | Request POWERGRID to remove this clause or please ensure to make integration of new bay/RTU as billable price schedule line item. It will be very difficult for vendors to do the same without any charges. | Refer Amendment-IV to the technical specification |
|  | Volume II Part-A, Section-1, General Information of the Project. 1.12, Scope of Work | Further, future bay integration shall not be treated as a new RTU integration during the AMC period, and any bay extension during AMC shall be in the scope of the contractor without any commercial implication to the Owner. | PGCIL to specify the no. of bays extension to be considered per year for future provisions. | Refer Amendment-IV to the technical specification. |
|  | Volume II Part-A, Section-1, General Information of the Project, 1.12, Scope of Work | l) Development of complete Database displays and reports to display SCADA and RE related information with analysis and report generation facility. The text available in displays and reports shall have support of fonts for English and Hindi. Contractor shall develop and provide tools to convert CIM files for different versions based on customized CIM-profiles in the files used by vendors system. The displays shall comply with the Display Building guidelines as per Appendix-K, Part-B of Vol-II | A per our understanding SCADA system should display text and reports in English and Hindi format and it is not required for RE F&S Tool and SAMAST/EABA module. Please confirm. | Refer Amendment-IV to the technical specification. |
|  | Volume II Part-A, Section-1, General Information of the Project, 1.12, Scope of Work | All IT products procured & supplied shall have a valid Certificate of Common Criteria as per ISO & IEC 15408 issued by signatories of the Common Criteria Recognition Agreement (CCRA). Acceptance of such tests shall be in line with directions of MoP and MeitY. | This certification is not followed by IT products / hardware suppliers and has not confirmed on the same. Please check and confirm. | Bidders to comply Technical Specification. |
|  | Volume II Part-A, Section-1, General Information of the Project, 1.12, Scope of Work, 3.8.5, User Documentation for Dispatchers | Both main and backup control centers shall work in active-active mode and in case of failure of main control center, backup shall come in the role of main without any manual interruption (except commands & signals) Initially both Main & backup Control Centre shall operate active-active mode and their various combination of operation in case of failures in communication & control center. | With reference to 1.16, Main and Backup Control Center Operational Philosophy the main control center will be primary and back up control center shall be stand-by mode. The data synchronisation and changeover shall be as specified in this clause. Request Powergrid to modify clause 1.8, 1.12, 3.8.5 accordingly. | Refer Amendment-IV to the technical specification. |
|  | Volume II Part-A, Section-1, General Information of the Project, 1.13, General Requirements | The supplied system (hardware & software) shall comply with cyber security standard relevant clause of the Central Electricity Authority (Technical Standards for Communication System in Power System Operations) Regulations, 2020, Indian or International Security Standards e.g., IT and IT related elements against ISO/IEC 15408 standards, for Information Security Management System against ISO 27000 series Standards, IEC 62443 for OT Network Security, IEC 62351. | This certification is not one to one followed by hardware and software suppliers and has not confirmed on the same. Bidder should be allowed to provide relevant standard followed. | Refer Amendment-IV to the technical specification. |
|  | Volume II Part-A, Section-1, General Information of the Project, 1.14.2, Contractor’s Responsibilities and Obligations | Implement all minor civil works and identify any major civil works i.e., expansion or construction of rooms, trenches necessary for installation of proposed equipment and provide the details of such work to the Employer/Owner. | No minor or major civil works shall be in the scope contractor. Please remove this clause. | Bidder to comply technical specification. |
|  | Volume II Part-A, Section-1, General Information of the Project, 1.14.4, Owner’s Responsibilities and Obligations | j) Owner will take over the SLDC cum REMC system upon completion of operational acceptance. | We understand that ISP will be on the name of Owner. Any interruption in the ISP services if affecting the Availability of the system will not come under Contractor's scope. During AMC period after the system becomes operational, ticket raising to ISP vendors on link down will be under Owner's scope. Kindly confirm. | Bidder to comply TS. However, for ISP services refer Amendment-IV to the technical specification. |
|  | Volume II Part-A, Section-1, General Information of the Project, 1.15, Main and Backup Control Center Operational Philosophy | In case user required to sync data between main and backup control center historian for a selected period, it shall be possible. | Please explain with a situation where this functionality will be required for better understanding of the requirement. | Bidder to comply technical specification. |
|  | Volume -II, part A, Section 1, 1.17 | Energy Accounting Software & Billing software: The contractor shall offer proposed energy accounting & Billing software (EABS) from OEMS who have supplied and implemented one projects with similar type of energy scheduling or Energy Accounting or Billing software, designed in line of SAMAST guidelines for any RLDC/SLDC. The EABS shall be in operation for at least one year as on date of NOA | We would like to bring in your kind notice the SAMAST guidelines are only for SLDC's and not for RLDC's. Secondly there are only few states where SAMAST has been implemented and are currently under AMC phase. Most of the SAMAST projects are under implementation and execution phase. Hence considering the above facts we request you to kindly amend the clause as suggested below for us to participate in the tender. Suggested Clause: The contractor shall offer proposed energy accounting & Billing software (EABS) from OEMS who have supplied and implemented or executing one projects with similar type of energy scheduling or Energy Accounting or Billing software, designed in line of SAMAST guidelines for any SLDC. In case of project under execution which shall only be considered where the portion of the work has been successfully delivered and the value the delivered portion of work should be more than 25% of Project value. | Refer Amendment-IV to the technical specification. |
|  | Volume -II, part A, Section 1, 1.17 | d. Energy Accounting & Billing Software The contractor shall offer proposed Energy Accounting & Billing software (EABS) from OEMs who have supplied and implemented one project/system with similar type of software for Energy Scheduling or Energy Accounting or Billing Software, designed in line with SAMAST guideline for any RLDC/SLDC. The EABS shall be in operation for at least one year as on the date of NOA. | To increase competition, we request that POWERGRID amend the clause as follows. d. Energy Accounting & Billing Software The contractor shall offer proposed Energy Accounting & Billing software (EABS) from OEMs who have supplied and implemented one project/system with similar type of software for Energy Scheduling or Energy Accounting or Billing Software, designed in line with SAMAST guideline for any RLDC/SLDC. | Refer Amendment-IV to the technical specification. |
|  | Volume -II, part A, Section 1, 1.17 | The contractor shall offer proposed Energy Accounting & Billing software (EABS) from OEMs who have supplied and implemented one project/system with similar type of software for Energy Scheduling or Energy Accounting or Billing Software, designed in line with SAMAST guideline for any RLDC/SLDC. The EABS shall be in operation for at least one year as on the date of NOA. | In reference to the said clause we would like to request PGCIL to amend the existing clause as follows: The contractor shall offer proposed Energy Accounting & Billing software (EABS) from OEMs who have supplied and implemented/Under Execution one project/system with similar type of software for Energy Scheduling or Energy Accounting or Billing Software, designed in line with SAMAST guideline for any RLDC/SLDC. The EABS shall be in operation/Under Execution/under implementation as on the date of NOA. | Refer Amendment-IV to the technical specification. |
|  | Volume -II, part A, Section 1, 1.17 | a. Forecasting Service Providers The contractor shall offer renewable power generation forecasting services from Forecasting Service Providers (FSP), as mentioned in BoQ, from FSP which has previous experience in providing Renewable (Wind/Solar) Power forecasting services for at least 2000 MW of Wind or Solar generation or both combined for at least two years of continuous operation in past seven (7) years as on date of NOA for any transmission system operator/ Independent system operator/RE (Wind/Solar) developer or Generator. One of these FSPs shall provide the internal forecasting & scheduling application. | To increase competition, we request that POWERGRID amend the clause as follows. The contractor shall offer renewable power generation forecasting services from Forecasting Service Providers (FSP), as mentioned in BoQ, from FSP which has previous experience in providing Renewable (Wind/Solar) Power forecasting services for at least 2000 MW of Wind or Solar generation or both combined in operation in past seven (7) years as on date of NOA for any transmission system operator/ Independent system operator/RE (Wind/Solar) developer or Generator. One of these FSPs shall provide the internal forecasting & scheduling application. | Bidder to comply technical specification. |
|  | Volume -II, Part-A, Section 1, 1.17 | b. Commercial Off-The-Shelf (COTS) product The contractor shall offer Commercial Off-The-Shelf (COTS) as mentioned in BOQ. The COTs product means a product which is independently commercially available in the market. The contractor shall provide at least three references in Govt/Public Listed companies where the product has been supplied as an independent product and the solution shall be in successful operation for at least one year as on the date of NOA. | To increase competition, we request that POWERGRID amend the clause as follows. b. Commercial Off-The-Shelf (COTS) product The contractor shall offer Commercial Off-The-Shelf (COTS) as mentioned in BOQ. The COTs product means a product which is independently commercially available in the market. The contractor shall provide at least three references in Govt/Public Listed companies and the solution shall be in successful operation for at least one year as on the date of NOA. | Refer Amendment-IV to the technical specification. |
|  | Volume II Part-A, Section-4, Clause-4.2 | For all third-party equipment (Hardware & Software), Contractor shall have back to back support and warranty for all maintenance services & availability of Security Patches along with supply of spare with appropriate response time from OEM/OEM Authorized representatives and these Back-to-Back contracts will be shared with owner before start of defect liability period. | OEM back to back support is not essential for commitment of SLAs. Please change this requirement, since typical OEM Support life Cycle is 3 to 5 years and no OEM signs customer MAF format. Bidder should be allowed the freedom to maintain the system through third parties as well | Refer Amendment-IV to the technical specification. |
|  | Volume II Part-A, Section-4, Clause-4.2 | In case, any hardware / software / equipment / component items of the systems supplied under the contract shall reach its End-of-Life (EOL) or End-of-Support (EOS) whichever is earlier, and is causing security vulnerability, then the contractor shall replace such item with new Hardware or Software without any financial implication to owner. (g) OEM Back-to-back Support: | Please remove this as it is not possible to define future security vulnerabilities. Any replacement shall have financial implication. if we change the version of third party software , it depends on the Operating system which is again dependent on hardware. | Refer Amendment-IV to the technical specification. |
|  | Volume II Part-A, Section-4, Clause-4.2 | (iii)Contractor must submit proper cyber risk mitigation plan/risk offered by connecting the system to the internet (whenever required) along with necessary cyber security measures in place. The contractor is allowed then only when the plan is approved by the owner. | As per cyber security guidelines. All critical infra has to be Air Gap environments. Owner has to ensure the limited Internet connectivity vis their secured IT network. | Bidder to comply technical specification. |
|  | Volume II Part-A, Section-4, Clause-4.3 | (f) Addition and modification of database and displays, report generation, configuration and Database sizing activities including on-lining as detailed in the specification for all applications etc. and other day-to-day operational activities would primarily be the responsibility of Contractor | Please elaborate operational activity, our understanding is limited to maintenance only | Refer Amendment-IV to the technical specification. |
|  | Volume II Part-A, Section-4, Clause-4.3 | (l) The contractor shall maintain a list of inventories of all hardware and software items being supplied along with software bill of material (Bom). The inventory shall include version & firmware number for understanding of applicable vulnerabilities from publicly disclosed vulnerabilities databases and shall take required action. | Please include Inventory management tool in software BOM | Bidder to comply technical specification |
|  | Volume II Part-A, Section-4, Clause-4.3.5 | The contractor shall upgrade the various applications delivered under the project through patch management and upgrade to make it compliant with IEC standards as envisaged under the specification during the entire contract period including extension of contract, if any. Updated patches shall be applied to the system within the timelines given below. Non-compliance will be considered under Severity-2. | Our understanding from this para is for the patches only. Version change of the application is not possible as it likely depends on the OS version. | Refer Amendment-IV to the technical specification. |
|  | Volume II Part-A, Section-4, Clause-4.3.5 | Anti-virus , Firewall, HIPS ,HIDS & Network IPS signatures - Daily | It depends on the release of the patch from the OEM. Normally AV release the definition updates on daily basis but IDS/IPS etc. doesn't deliver the daily patches. | Bidder to comply technical specification. |
|  | Volume II Part-A, Section-4 Maintenance & Support | System Availability >99.90 % | The required system availability is currently very high and difficult to achieve. Typically for the software / transactional systems such as SAMAST and RE F&S system availability should be maximum 98.5 % Hence same need to be relaxed. | Bidders to comply Technical Specification. |
|  | Volume II Part-A, Section-4, Clause-4.5 | 4.5 Integration of new equipment and or control center All future services, protocol emulations and configuration support for integration of RTUs, SAS, Control Centre integration on ICCP clients for OPC Services, Web services and CIM import and export utility for off-line applications shall be the responsibility of contractor during maintenance period. Integration of the new forecast service provider, weather service provider and new link between any of the forecasting tool, RE Scheduling tool etc. shall also be the responsibility of contractor. Integration of new meters and other owner’s application with energy accounting & billing software shall be in the scope of contractor during maintenance period. | Integration with any third party application required substantial amount of integration efforts. Hence, we request to clearly defined the future coming applications that’s need to be integrated with RE F& S Application or SAMAST / Energy Accounting & Billing Application for bidder's to consider rational efforts and submit the prices accordingly instead of taking any false assumptions which may increase the overall project price. Hence request to define the no of integration with future coming application so that same can be baseline for each bidder's. | Bidder to comply technical specification. |
|  | Volume II Part-A, Section-4, Clause-4.5, Responsibility Matrix | 2.1 Report problem and assist with problem identification. 3.3 Restore or reinstall software from back-ups. 4.4 Restore operation of repaired/replaced equipment 5.0 HARDWARE SPARE PARTS 8.1 - 8.6 Patch/Signature/Update/firmware Updates etc. | 21. Problem reporting to be done by Owner. We have standard support for maintenance for S2, S3 and S4 and 24x7 for S1 issues. 3.3 We need assistance as it also depend on the Online system as well. 4.4 same as 3.3 5.0 Spares will be in Owners premises, so security has to be prime responsibility of the Owner and during replacement assistance is needed. 8.1 - 8.6 Owners assistance is required, as it requires downtime. | Bidder to comply technical specification. |
|  | Volume II Part-A, Section-4, Clause-4.11, Detailed Scope of work during the entire Contract Period | Detailed Scope of work during Warranty and AMC Period Technical upgrade of the installation to the new version (wherever applicable), as and when required, shall be done by the Contractor. Any version upgrade (in version) of the software / tool / appliance by Contractor to be done after taking prior approval of Owner and after submitting impact assessment of such upgrade at no additional cost to Owner. | Bidder shall extend software support for 8-years which includes installation of compatible patch files/service packs of offered SCADA software on the same versions of Operating systems and applications. Versions upgrade shall not be applicable as the upgrade itself becomes another complete project to be executed like the present tender, hence needs to be taken up separately after the end of AMC. | Refer Amendment-IV to the technical specification. |
|  | Volume II Part-A, Appendix-D, Typical Network Architecture for Ladakh SLDC cum REMC | General Query on CMC Server | There are two different components: an External CMC in the External DMZ LAN and an Internal CMC in the Management LAN, kindly explain each with its own purpose. However, only one quantity of CMC has been mentioned in the BOQ. We also understand that the Antivirus, SIEM, and WSUS will be hosted on the CMC Server. Kindly confirm our understanding. | Refer Amended BoQ of Amendment-IV to the technical specification |
|  | Volume II Part-A, Appendix-D, Typical Network Architecture for Ladakh SLDC cum REMC | Query on Data Replica Server. | There's no Data Replica Server mentioned in Architecture. As per the BOQ, we are considering 2 nos of Data Replica Server. | Bidders to quote as per BOQ and comply Technical Specification. |
|  | Volume II Part-A, Appendix-D, Typical Network Architecture for Ladakh SLDC cum REMC | Query on BOQ & Network Architecture | As per the Typical Network Architecture given for Ladakh SLDC cum REMC, there is a workstation console present in the Energy Accounting LAN; however, no quantity is mentioned in the BOQ. Kindly clarify. | Refer Amended BoQ & Architecture of Amendment-IV to the technical specification |
|  | Volume II Part-B, Section-1, 1.1. SCADA Functions | f) Data exchange with scheduling application WBES | Kindly provide the existing WBES (Web Based Energy Scheduling System) details & how the integration has to be done via SFTP (Secure File Transfer Protocol). | The details of scheduling shall be provided during detail engineering. Bidders to comply Technical Specification. |
|  | Volume II Part-B, Section-1, 1.1.1.8, RTU Communication Monitoring, Recording and Statistics | CFE server should be able to operate in listening mode (able to receive signal without request). | Please elaborate the exact Requirement. | Refer Amendment-IV to the technical specification |
|  | Volume II Part-B, Section-2, 2.2, Power System Analysis | The principal PSA activities of Control Centre are summarized as follows: e. Listing all Circuit Breaker and Isolator which can be filtered voltage level/station/area-wise in case the telemetered value is more than the threshold limit. On click, the user shall be able to navigate to corresponding single line diagram of sub-station containing the Circuit Breaker/Isolator. | Listing all Circuit Breaker and Isolator which can be filtered station/area wise Not Clear " in case the telemetered value is more than the threshold limit." | The threshold limit here refers to the limit of the difference between telemetered value and state estimated value. Bidders to comply Technical Specification. |
|  | Volume II Part-B, Section-2, 2.2.5.4, HVDC Model | j) RVO mode operation | What is RVO Mode Operation? | In the reduced voltage operating mode the HVDC terminal voltages are reduced below rated values and power flow continuous. Bidders to comply Technical Specification. |
|  | Volume II Part-B, Section-2, 2.2.8.2, State Estimation Characteristics | f) …...................................... It shall be possible for the programmer to disable and enable the setting of the quality code in the real-time data base on a global basis.............................. | if quality code disables in real-time in SCADA then what quality code be considered in SE? | Bidders to comply Technical Specification. |
|  | Volume II Part-B, Section-2, 2.2.9, Bus Load Forecast | - Change the filter parameters used by the smoothing process | What would be filter parameters in smoothing process? | This information shall be provided during detailed Engg. Bidders to comply Technical Specification. |
|  | Volume II Part-B, Section-2, 2.2.11.1 Contingency Cases: Following Features | c) The user shall be able to enable or inhibit the modelling of closed-loop control of transformer (voltage and phase-shifter) tap changers, reactor/capacitor switching and generating unit reactive power limiting. | Explain closed-loop Scenario in transformer tap changers used to define a contingency? | Closed Loop scenario is a scenario in which the TAP changer position is automatically controlled based on the bus voltage. Bidders to comply Technical Specification. |
|  | Volume II Part-B, Section-2, 2.2.11.1 Contingency Cases: Following Features | d) In the event of generating unit outages or outages that cause a loss of load the change in generation/load shall be assigned to all remaining generating units/loads in proportion to its maximum capacity in the affected electrical island. | Please confirm following understanding: Generation will be assigned to remaining unit but load cannot assign to other | Confirmed. For loss of Load, the generations shall be proportionately reduced as per the maximum capacity of generators in the affected island. Bidders to comply Technical Specification. |
|  | Volume II Part-B, Section-2, 2.2.12.3 OPF Output Data | · An interchange summary shall be provided showing desired and calculated net interchange, Total losses, generation, load, tie-line flows, bus mismatch, maximum bus mismatch, and spinning reserve. | Please confirm following understanding: Calculation of Spinning reserve is not a part of the network applications. It will be calculated under AGC functions. | Bidder can calculate the spinning reserve in any of the applications but the Interchange summary shall display the required data. Bidders to comply Technical Specification. |
|  | Volume II Part-B, Section-3, 3.5 Dynamic Dashboards (SCADA), 1.8.4, Reports | Capability to build on-the-fly dashboard by combining subsets/Cut-Outs of different displays onto a dashboard area. For example, the user may want to monitor a particular problem in the network and will need information from a number of different displays to do it. The portions of displays that are dropped onto a dashboard display continue to be updated in real-time. Dashboards shall offer essential data customized to each area of interest for the user with various statistical parameters of the grid data. A Business Tool shall be provided with user friendly configurable with drag and drop query builder, report builder and trend builder facility. Reports can be generated on user demand, on a preset timed interval, or be driven by specific events. | “The requirement is not clear. Is it a separate tool required and also there may not one tool for all the requirements. It is possible for POWERGRID to integrate such tools with the SCADA system/Database and create / configure dashboards and visualisation based on the requirement. As this is not an integral part of SCADA-EMS, we request POWERGRID to delete this requirement.” | Please refer section 3, clause 3.5, Dynamic dashboard are proposed to be part of SCADA system. For 1.8.4 Refer Amendment-IV to the technical specification Bidder to comply technical specification |
|  | Volume II Part-B, Section-3, Clause-3.8, Documentation | For this a web based “Document Management System” (DMS) software shall be supplied and installed at the owner’s facility by the contractor along with minimum 50 number of client access licenses. DMS shall have multiuser capability with user role and privileged management. DMS shall have complete capability of tracking the documents version, ownership and editing. This DMS shall be used as central document repository for the entire lifecycle of the Project for easy managing and referencing of the project documentation. | We understand that the DMS should be implemented first at Owner's premises after awarding of the contract as Documentation and Design is the first stage of a Project. Please elaborate. | The document management system can be implemented in the beginning or after delivery of the system. Bidder to comply technical specification |
|  | Volume II Part-B, Section-3, Clause-3.8, Documentation |  | Is the document approval through DMS is in time bound manner? E.g.: The submission by Contractor and responses from Employer are bound to be with in some time apart from Appendix E Row Number 3, pdf page number 143. Please elaborate | Bidder to comply technical specification |
|  | Volume II Part-B, Section-3, Clause-3.9, Trending (SCADA Application) | Points to be trended: All SCADA points shall be made available for trending, by default. However, any system parameters such as communication or application statistics whose trend is required by user, need to be integrated as SCADA data and shall also be available for trending. | Kindly clarify whether communication links also has to be trend. | Bidder to comply technical specification. |
|  | Volume II Part-B, Section-4, 4.2.2, Operating System | The operating system of all the equipment of SCADA/EMS & REMC system including network equipment shall be latest version released preferably up to six (06) months prior to FAT. | Since version selection depends on last release and tested with application software, hence please modify this requirement so that bidder can offer tested version and not latest version. | Bidder to comply technical specification. |
|  | Volume II Part-B, Section-4, 4.2.2, Operating System | In case of end-of-life, obsolescence and end-of-support of the operating system, Anti-Virus or any other software delivered in the project, the contractor should provide latest version and license of operating system, Anti-Virus or any other software delivered in the project at its own cost. If changes of software and operating system require replacement of hardware, then, hardware shall also be replaced by the contractor without any cost implication to owner. Replacement shall be of either the same or higher configuration keeping required performance specified under the contract and from same OEMs. | This clause is not acceptable. Please allow bidder to maintain the system with 3rd party support. Further any replacement if necessary, shall have financial implications as technology and threat landscape is continuously evolving and it is not possible to predict obsolescence of products 7 years down the line since it depends on a lot of factor. | Bidder to comply technical specification. |
|  | Volume II Part-B, Section-4, 4.4 Network Software | The network software for the SCADA/EMS & REMC system shall include software for network communication and network services. Network software shall include the user node software that provides the connection of that node to the network. The network node software shall be provided for each type of network node connection supplied with the initial system and shall be licensed for the quantities and types of nodes defined for the SCADA/EMS & REMC System configuration. It should be able to generate reports for a defined period regarding availability of communication links. In case any communication link is DOWN/OUT/Failure, then a pop-up should come up for it along with the SMS and e-mail facility shall be implemented for the same. | Kindly confirm whether the network software will only be recording the communication link status or the Hardware/Software status. | Refer Amendment-IV to the technical specification. |
|  | Volume II Part-B, Section-4, 4.6.10, Development System (DDS or PDS) as a test bench | • Integration of New RTU Testing of Integration of new control Centre on ICCP protocol | Since there are no quantities of WAN Routers cum Firewall specified in the BOQ for testing ICCP/FEP links, please clarify the data flow from the ICCP/RTU LAN to the PDS LAN | Refer Part-B, Appendix-G and Price schedule in Vol-III. Bidders to comply Technical Specification. |
|  | Volume II Part-B, Section-4, 4.6.10, Development System (DDS or PDS) as a test bench | This system shall also be used as a Test bench for Cyber security and shall accordingly be equipped with firewall, antivirus and enable mode wherein threat scenarios can be tested with configured security elements before implementing on the main/production system. | 1) Development System cannot be used for the testing of the Signatures/updates of the firewall. Firewall signature does not require any testing. 2)It is not possible to simulate the Threat scenarios in the SCADA/REMC environment. Development system can be used only for the testing of signatures/definition/patch updates so as we can check any update is not impacting the running application/os. | Refer Amendment No-IV to technical specification. Bidders to comply Technical Specification. |
|  | Volume II Part-B, Section-4, 4.8.3, On-Line Monitoring Diagnostics | Designated backup server(s) and associated auxiliary memories shall be automatically tested for proper operation to ensure they are ready if needed for a failover contingency. Any failure to perform diagnostic functions correctly shall cause an alarm to be issued. | Online backup is automated process but restoration cannot be automated, it requires manual intervention with respective system in down condition e.g. if we have to restore the backup of IC2 in that case no other machine with the name of IC2 should be live. A new bare server will be placed in place of IC2 and then backup will be restored. Please elaborate, if there is any other understanding. | Bidders to comply Technical Specification. |
|  | Volume II Part-B, Section-5, 5.2 | The Bidder shall ensure that the product/technologies/services quoted under this project are latest and it shall have more than 7 years of life initially (i.e.., “End of Support Life” for minimum 7 years, from date of the bid submission) which shall be extended during entire contract period (including extension of contract, if any) by extending the OEM warranty or replacing the product.). | Please remove this provision since most reputed OEMs don't confirm "more than 7 years of life". Please limit this upto 7 years, i.e. Maintenance period of contract without any extensions. | Bidders to comply Technical Specification. |
|  | Volume II Part-B, Section-5, 5.5.2 RTU communication over IEC 60870-5-104 | The CFE shall be provided with suitable interfaces for communication with the RTUs/SAS over IEC 60870-5-104 protocol. One set of Router cum firewall for RTUs shall be provided between RTUs/SAS and CFE for RTUs/SAS communicating with control center on IEC60870-5-104 protocol as per the Part-B Appendix-F. | We understand all RTU's shall be connected to redundant CFE's via IEC 104 Protocol. Kindly confirm. | Bidders to comply Technical Specification. |
|  | Volume II Part-B, Section-5, 5.8, Storage Devices, 5.8.1 Storage Area Network (SAN) based storage | Separate FC switches shall be provided along with SAN for connecting the Servers/Devices. The no of ports in a FC switch shall be as per the network architecture & the no of servers/devices to be connected. | We understand that separate SAN switches should be provided according to the Technical Specification (TS). However, there are no SAN switches mentioned in the Bill of Quantities (BOQ). Please clarify this discrepancy. | Refer Part-B, Appendix-G and Price Schedule, SAN switch is mentioned along with SAN. Bidders to comply Technical Specification. |
|  | Volume II Part-B, Section-5, 5.8, Storage Devices | Query on Storage Devices | We understand that the SAN (Storage Area Network) will be used to store Historian data, image backups of servers and workstations, image backups of networking equipment (Routers, Switches, Firewall), Repository data, displays, reports, trends, analysis, raw meter data, application logs, audit logs of the EABA System, and SIEM data. We also understand that the NAS (Network-Attached Storage) will store image backups of servers and workstations as well as backups of networking equipment (Routers, Switches, Firewall). Additionally, tape storage will be used for backup purposes, including storing backups of servers and workstations, networking equipment, and archival data from SAN and NAS storage. Kindly confirm whether our understanding is correct. We are also seeking clarification on the frequency of backups taken on devices other than image backups of servers and workstations. Will tape storage also store image backups of servers and workstations? | Kindly refer Part-B, Section - 4, Clause- 4.8.1 of technical specification Bidders to comply Technical Specification. |
|  | Volume II Part-B, Section-5, 5.18.2, KVM | The contractor shall supply an IP-based KVM system as per the technical specification. All the Servers shall be connected to KVM system and shall be accessible through IP in KVM system. Proposed KVM over IP (KVMoIP) system shall be connected to switches envisaged for server Management console system. Through this KVM over IP (KVMoIP) connection, users shall access and control servers simultaneously from centrally. | As per the architecture given on page 141/484, there is no separate LAN designated for SMC, and it is considered part of the Management LAN. However, based on the information provided in the Technical Specifications (TS) for the KVM, we understand that it should be part of a separate SMC LAN. Kindly clarify whether the KVM nodes should be connected to the Management LAN or if a separate SMC LAN should be established. | Refer Amended BoQ and architecture of Amendment-IV to the technical specification. |
|  | Volume II Part-B, Section-6, Configuration Characteristics, 6.1 Redundancy | l) Storage device a. SAN – SAN shall be configured as redundant. b. NAS – NAS shall be configured as non-redundant device. | We understand that the Bill of Quantities (BOQ) specifies the provision of 2 SANs per Control Centre, indicating they will operate in Active-Passive mode. Kindly confirm our understanding. | Refer Clause 5.8.1, Section-5, Part-B of Amendment-IV to the technical specification. |
|  | Volume II Part-B, Section-8, 8.2.2, Load Forecast | Load Forecast | Load Forecast is generally done by DISCOMs as part of the demand forecast which is shared to LDCs by them. As this is already being done by the DISCOMs it may not be required to be done again at SLDC. This will also enable a single source information w.r.t demand/load forecast. Hence, this shall be removed from the specification. | Bidder to comply technical specification. |
|  | Volume II Part-B Section-8, 8.2.3, Integration with Scheduling Application (WBES) | "The WBES application output data (quarter hourly schedules and five-minute schedules of Generating Stations/plants and drawl schedules of constituents) for day a head shall be integrated with SCADA/EMS & REMC and network applications (State estimator etc.). It shall have the facility to integrate future schedule and trend for schedule, Forecast and Actual simultaneously in single trend window. Units schedule shall be derived from Generating stations schedules by distributing the total station generation among units based on the unit availability by the Contractor application. Application shall be capable of adding unit values to reach at station values to compare scheduled versus actual generation of station values. " | Bidder requests PGCIL to provide more details about WBES, i.e. regarding integration with other applications. | Bidder to comply technical specification. |
|  | Volume II Part-B, Section-8, 8.3 Web System | From operational requirement, if transfer of data from DMZ Zone to SCADA/F&S zone is required, separate database shall be created in DMZ from where data shall be read by SCADA/F&S zone. | Kindly clarify the following points : - How will the separate database in the DMZ Zone be set up and maintained for data transfer to the SCADA/F&S Zone? - Who will have access rights to read data from the DMZ database in the SCADA/F&S Zone, and how will access control be managed? - What security measures will be implemented to ensure the secure transfer of data from the DMZ Zone to the SCADA/F&S Zone? | Refer Part-B, Section-8.2.3 & 8.3.3 of Vol-II, technical specification |
|  | Volume II Part-B, Section-8, 8.3.1 Web Server | The web server in External DMZ shall be provided with host-based Intrusion detection system (HIDS). The HIDS will be installed on all the machines connected to the Web server LAN. | We understand HIDS shall be installed on a total 6 machines 2 (main-backup) X 3(servers) | Refer Note (c) in Bill of Quantity Appendix-G. Bidders to comply Technical Specification. |
|  | Volume II Part-B, Section-9, Cyber Security Requirements | 9.2.4 Intrusion Detection & Prevention System b) Network based Intrusion Prevention System (NIPS) 9.2.6 Application Whitelisting tool | According to the Technical Specifications (TS), there are other measures for cybersecurity aspects mentioned in Section 9, such as NIPS (Network Intrusion Prevention System) and an Application Whitelisting Tool. Kindly clarify how these measures will be implemented. | Bidders to comply Technical Specification. |
|  | Volume II Part-B, Section-9, 9.2.5 Cyber Security Requirements | 9.2.5 Security Information and Event management (SIEM) Create custom remediation packages to address recurring configuration issues, remove unauthorized files and applications, and patch software. | This is not a SIEM feature and available with specific OEM. We request you to remove this clause. | Refer Amendment-IV to the technical specification. |
|  | Volume II Part-B, Section-9, 9.2.8 Software update and Patch Management tool | Patches shall be downloaded from authentic sources in patch management server that is available in DMZ zone. After successful downloading, it shall be transferred to patch management server in PDS LAN, where all the patches will be tested. After successful testing of the patches, it shall be distributed to the entire system. | According to the Network Architecture provided on page 141/484, the Identity & Patch Management Server is listed under the Management LAN, not in the DMZ LAN. Additionally, there is no mention of a Patch Management Server in the PDS LAN. Please clarify this discrepancy. | Refer Amended BoQ and architecture of Amendment-IV to the technical specification. |
|  | Volume II Part-B, Section-12 Energy Accounting & Billing Application | General Query on MDMS | Kindly confirm if MDMS system is present in the SLDC Ladakh. | Kindly refer Part-B, Section - 12, Clause no. 12.3.1.1 of technical specification. Bidders to comply Technical Specification. |
|  | Volume II Part-B, Section-12.1, Energy Accounting and Billing Application Requirements | "Energy Accounting & Billing Software: The EABS shall be designed as per the SAMAST- “Scheduling, Accounting, Metering and Settlement of Transactions in Electricity” framework encompassing the various aspects of energy accounting, metering, deviation settlement at the inter-State/intra-State level and evolving a uniform procedure for SAMAST in Electricity." | Energy Accounting & Billing is implemented separately as standalone software and not part of SCADA EMS, Hence we request POWERGRID to remove this from the scope. | Bidder to comply technical specification. |
|  | Volume II Part-B, Section-12.1.1, Energy Accounting and Billing Application Requirements | “The UT of Ladakh is in the process of establishing the EABA as per the SAMAST guidelines. At present, the EABA is being managed by the JKPTCL and it is being manually done. However, the EABA mechanism shall gradually be independently managed by Ladakh. The details of various entities existing and future i.e. DISCOM, IPPs, State generators, Open access Customers, Renewable energy Generators shall be shared during detail engineering.” | We understand Energy Accounting and Billing application is already being procured separately, hence same may be removed from the tender BOM and price schedule. | Bidder to comply technical specification. |
|  | Volume II Part-B, Section-12 Clause no -12.2, Para no D | The application/module shall be web based and installed in Energy Accounting & Billing Server. The EABS server shall be in redundant configuration. The users and administrators of the application/module for external entities shall be accessed through Graphical User interface via a Web server. The web-based application shall have access control management and role-based displays/rights for various entities. It shall be possible to define a minimum of 10 user types with accesses to the different modules and their combinations. | Requesting you to please suggest/confirm total number of concurrent users for EABS System. We understand that the energy accounting and billing server shall keep all data online minimum for last two months including current day, to enable downloading of selected data by external users. All the data of energy accounting and billing application shall be stored in SAN. | Bidder to comply technical specification. |
|  | Volume II Part-B, Section-12, Clause no -12.2, Para no D | The web-based GUI shall be sized to support 100 concurrent clients/users for providing access to application/module. There shall be no limitation on the number of named users. Each user shall be assigned to a user type. | Please provide the clarity on the total no of users who are going to use RE Forecasting & Scheduling Application including Energy Accounting & Billing Application. Total count should includes external as well as internal users. Hence same is required for estimating the HWSW sizing. | Refer Amendment-IV to the technical specification. |
|  | Volume II Part-B, Section-12 ,Clause no -12.3.1 | All the meter records of all Interface energy meters (main, check & standby) shall be collated at SLDC for energy accounting at State level. The application/module shall be able to read the energy meter data, block by block, analyze for any discrepancies and compute the energy drawn by each of the entities. The application/module shall also be capable of integrating with the Automatic Meter Reading (AMR) software, which collects meter data from meters in the state or provide option for meter data reading upload from remote location by registered users (from Meter Site, Substation/Area Office). The application shall also support reading energy meter data from ASCII files in offline mode. | Need clarity in case of non-availability of meter readings than system will generate the discrepancy report and will not compute the energy accounting functions with capturing the correct meter readings and missing meter readings. | Bidder to comply technical specification |
|  | Volume II, Part-B, Appendix-F: System Sizing | Table – 4: System sizing for RTUs and data received from RTUs | According to the Technical Specifications provided in the 'Details of RTU Location' on page 153/484, it states that there are 24 RTUs. However, the System Sizing indicates that there should be 30 RTUs. Please clarify the correct number of RTUs. | The present scope includes Supply, Installation, Testing, and Commissioning of 24 no. of RTUs. The 30 no. of RTU mentioned for system sizing. Bidders to comply Technical Specification. |
|  | Volume II, Part-B, Appendix-G, Bill of Quantity | Query on BOQ | There are no switches mentioned for the Energy Accounting LAN. However, based on the architecture, our understanding is that it should be in a separate LAN. Kindly confirm this. | Bidders to comply Technical Specification. |
|  | Volume II, Part-B, Appendix-G, Bill of Quantity | Query on BOQ | We did not find a PCMT Tool for the configuration of RTUs in the BOQ. Our understanding is that a PCMT Laptop will be provided for RTU database configuration and maintenance, Also the PCMT hardware specifications have been provided. Please confirm this. | Kindly refer Part-D, Section - 1, Clause no. 1.28 of technical specification. Bidders to comply Technical Specification. |
|  | Volume II, Part-B, Appendix-G, Bill of Quantity | Query on BOQ | We understand AV shall be installed in 36 machines which includes (servers+ workstations + laptop + vps + h/w for repository server +remote console). Kindly confirm if our understanding is correct. | Refer Note (c) in Bill of Quantity Appendix-G. Bidders to comply Technical Specification. |
|  | Volume II, Part-B, Appendix-G, Bill of Quantity | 13 Storage System c. Hardware for Repository Server | According to the TS for the SAN, our understanding is that Repository Data will be stored in the SAN. However, BOQ lists 2 Nos. Quantity for the Repository Server. Please clarify whether Repository data will be stored in the SAN or in a dedicated Server for Repository. | Kindly refer Part-B, Section - 5, Clause- 5.6 of technical specification Bidders to comply Technical Specification. |
|  | Volume II, Part-B, Appendix-G, Bill of Quantity | Under EMS Application | Current BOQ have only provision for Forecasting and Scheduling Software and not have provision or separate BOQ line item for Energy Accounting and Billing Application (EABP). Kindly Clarify against which line items of BOQ we have to quote the Price of EABA / SAMAST module. | Refer Bill of Quantity, Appendix-G and Vol-III price schedule. Bidders to comply Technical Specification. |
|  | Volume II, Part-B, Appendix-G, Bill of Quantity | Under Section D <AMC> Charges of 3 FSPs are quoted based on total Pooling substation 6 No's. | Kindly confirm that the forecaster has to consider total quantum of 10.14 GW (Both Solar and Wind) across 6 polling stations while quoting the prices. | Refer Appendix- O, List of RE Pooling Station of Technical Specification. Bidders to comply Technical Specification. |
|  | Volume II, Part-B, Appendix-G, Bill of Quantity | Identity Management Software and patch management software | Identity and patch management are the two different software and to be deployed in different zones as per the cyber security requirements. Please confirm | Refer Amendment-IV to the technical specification |
|  | Volume II, Part-B, Appendix-G, Bill of Quantity |  | There is no line item for whitelisting tool | Refer Section –9, Clause 9.2.6 of technical specification. Bidders to comply Technical Specification. |
|  | Volume II, Part-B, Appendix-G, Bill of Quantity | 13. Storage System | There is no line item for SAN Switches | Kindly refer Part-B, Section - 5, Clause- 5.6 of technical specification Bidders to comply Technical Specification. |
|  | Volume II, Part-B, Appendix-G, Bill of Quantity | 16. Cyber Security Appliances | There is no line item for APT (Sandboxing) | Refer Amendment-IV to the technical specification. |
|  | Volume II, Part-B, Appendix-G, Bill of Quantity & Vol-III, Price Schedule | Bill of Material/Price Schedule | During Prebid discussions Powergrid has confirmed Network connectivity shall be provided by employer, however there is a line item for ISP services in BoM/Price schedule. As per TRAI norms ISP services are scalable. Please exclude the same from Bidder scope. | Refer Amendment-IV to the technical specification. |
|  | Volume II, Part-B, Appendix-G, Bill of Quantity & Vol-III, Price Schedule | Bill of Material/Price Schedule | The operator training simulator should be added as a separate line item | Refer Amendment-IV to the technical specification. |
|  | Volume II, Part-B, Appendix-G, Bill of Quantity & Vol-III, Price Schedule | Bill of Material/Price Schedule | We request Mandays to be taken on additional service basis | Refer Amendment-IV to the technical specification. |
|  | Volume II | General Query | Are we going to transfer any scheduling file from REMC to corporate LAN or to existing SLDC ? | There are no existing scheduling application but there will be data exchange between REMC application with SLDC SCADA, RLDC REMC, Market application in Power exchanges, SAMAST application as per APIs and protocols & interfaces mentioned in the TS. Bidders to comply Technical Specification. |
|  | Volume II, Part-B, Appendix-G, Bill of Quantity & Vol-III, Price Schedule | SPARE S.NO.27 48V DC POWER SUPPLY OF 35 AMP RATING S.NO.28 VRLA BATTERY BANK 450AH FOR DCPS | Both 48V/35A DCPS and VRLA 450AH Battery bank has been asked in Spares whereas in Price Schedule, it has been asked in Main Supply. Kindly Clarify/ Correct. | Refer Amendment-IV to the technical specification. |
|  | Volume II, Part-B, Appendix-G, Bill of Quantity & Vol-III, Price Schedule | SUPPLY S.NO.5 RTU base Equipment -CAT ll,lll & LV S/S | In Tender BOQ, RTU base Equipment -CAT ll, lll & LV S/S has been asked in Supply whereas it has not been asked in price schedule. Kindly Clarify/Correct. | Refer Amendment-IV to the technical specification. |
|  | Volume II, Part-B, Appendix-G, Bill of Quantity & Vol-III, Price Schedule | SUPPLY S.NO.1 RTU for Auxiliary system-RTU base equipment comprising racks, sub-racks, power supply modules, CPU, including internal wiring except cards modules specified below. S.NO.17 Laptop for PCMT | In Price Schedule, Both RTU for Auxiliary system-RTU base equipment comprising racks, sub-racks, power supply modules, CPU, including internal wiring except cards module and Laptop for PCMT has been asked in price schedule where as it has not been asked in Tender BOQ. Kindly Clarify/Correct. | Refer Amendment-IV to the technical specification. |
|  | Volume II, Part-B, Appendix-G, Bill of Quantity & Vol-III, Price Schedule | 44 U Server Rack with IP based KVM Switch(Tender BOQ) 44 U Server Rack with IP based KVM Switch & Rack Mounted Monitor(Price Schedule) | In price schedule, 44 U Server Rack with IP based KVM Switch & Rack Mounted Monitor has been asked where as in Tender BOQ, 44 U Server Rack with IP based KVM Switch is asked Kindly Clarify/ Correct. | Refer Amendment-IV to the technical specification. |
|  | Volume II, Part-B, Appendix-G, Bill of Quantity & Vol-III, Price Schedule | Database development system (DDS) cum test bench for SCADA & ICCP integration (Tender BOQ) Database development system (DDS) cum test bench for RTU & ICCP integration (Price Schedule) | In price schedule, Database development system (DDS) cum test bench for RTU & ICCP integration has been asked but in Tender BOQ, it is Database development system (DDS) cum test bench for SCADA & ICCP integration is asked. Kindly clarify / Correct. | Refer Amendment-IV to the technical specification. |
|  | Volume II, Part-B, Appendix-G, Bill of Quantity & Vol-III, Price Schedule | Workstation Console integrated with dual 23.8' TFT Monitors for operators a. Workstation b. dual 23.8' TFT Monitors | In Tender BOQ, Dual monitor description has been provided whereas in price schedule description is not provided Kindly Clarify / Correct | Refer Amendment-IV to the technical specification. |
|  | Volume II, Part-B, Appendix-G, Bill of Quantity & Vol-III, Price Schedule | S.No.14(A) WAN Router cum Firewall for ICCP Communication S.No.14(B) WAN Router for RTU Communication with Firewall | In Price schedule, Both Router for ICCP Communication & Router for RTU Communication ports description has been provided whereas in Tender BOQ, it is not provided. Kindly Clarify/ Correct. | Refer Amendment-IV to the technical specification. |
|  | Volume II, Part-B, Appendix-G, Bill of Quantity & Vol-III, Price Schedule | WAN router for remote console | In Price Schedule, Router for remote console description has been provided whereas in Tender BOQ description is not provided Kindly Clarify/ Correct. | Refer Amendment-IV to the technical specification. |
|  | Volume II, Part-B, Appendix-G, Bill of Quantity & Vol-III, Price Schedule | 24 Port L-3 LAN Switch for SCADA LAN. 24 Port L-3 LAN switch for Data LAN. 24 Port L-3 LAN Switch for External DMZ LAN. 24 Port L-3 LAN switch for ICCP LAN. | In Tender BOQ, all four switches no. of ports has been provided but in Price schedule, no. of ports are not given Kindly Clarify/ Correct. | Refer Amendment-IV to the technical specification. |
|  | Volume II, Part-B, Appendix-G, Bill of Quantity & Vol-III, Price Schedule | NAS Box(Tender BOQ) WAMS hardware-Network attached storage (NAS) system of min 6TB of RAID 10 or better configuration(Price Schedule) | In price schedule, NAS capacity has been provided where as in Tender BOQ, NAS Box has been provided without NAS system capacity. Kindly Clarify/Correct | Refer Amendment-IV to the technical specification. |
|  | Volume II, Part-B, Appendix-G, Bill of Quantity & Vol-III, Price Schedule | Centralized Management console (CMC) | In Price schedule, CMC Qty. for both MCC & BCC has been provided 2 for each where as in Tender BOQ, 1 for each has been provided Kindly Clarify / Correct. | Refer Amendment-IV to the technical specification. |
|  | Volume II, Part-B, Appendix-G, Bill of Quantity & Vol-III, Price Schedule | Spares @ One of each type of External Firewall and One of each type of Internal Firewall shall be considered against this line item | In Tender BOQ, both internal and external firewall has been asked in Spare where as in Price schedule, only internal firewall has been asked in spare. Kindly Clarify / Correct | Refer Amendment-IV to the technical specification. |
|  | Volume II, Part-B, Appendix-G, Bill of Quantity & Vol-III, Price Schedule | One complete VPS Module without screen / frame structure | In Tender BOQ, VPS module has been asked for both MCC and BCC where as in Price schedule, it has been asked for BCC Kindly Clarify / Correct. | Refer Amendment-IV to the technical specification. |
|  | Volume II, Part-B, Appendix-G, Bill of Quantity & Vol-III, Price Schedule | AMC SMS Services annually for 20,000 users shall be considered | In Tender BOQ, SMS service has been asked for 1 lakh messages annually where as In Price schedule, sms service for 20,000 users has been asked annually. Kindly Clarify /Correct. | Refer Amendment-IV to the technical specification. |
|  | Volume II, Part-B, Appendix-G, Bill of Quantity & Vol-III, Price Schedule | Integration of new bay (including supply and commissioning of each type of card, MFT, CMR, Cables etc) at RTU site | In price schedule AMC for integration of new bay at RTU has been asked for 50 Qty where as in Tender BOQ, it has not been asked. | Refer Amendment-IV to the technical specification. |
|  | Volume II, Part-B, Appendix-G, Bill of Quantity & Vol-III, Price Schedule | Annual maintenance of RTU during one year of warranty Annual maintenance of RTU for 6 year after expiry of warranty period | In price schedule, AMC duration has been provided where as it is not provided in Tender BOQ. | Refer Amendment-IV to the technical specification. |