| Sl. No. | Tender Document Reference | Clause | Bidder’s Query | POWERGRID Reply |
| --- | --- | --- | --- | --- |
| 1 | Volume II-Technical Specifications 400kV Transformer _Rev 13 Clause no 3.14- Dynamic Short Circuit Test requirement | 3.14.1 - For 400 kV Class Auto transformer Bidder / Manufacturer should have successfully carried out Dynamic Short Circuit test on 315MVA or above rating 400/220/33kV or 400/230/33kV, 3-Phase Auto transformer as on the originally scheduled date of bid opening and shall enclose the relevant Test Report/certificate along with bid. In case bidder/manufacturer has not successfully tested 315MVA or above rating 400/220/33kV or 400/230/33kV, 3-Phase Auto transformer for Dynamic Short Circuit test, their bid shall be considered technically non responsive. Further, design review of offered 400kV Class Auto transformer shall be carried out based on the design of short circuit tested 315MVA or above rating 400/220/33kVor 400/230/33kV, 3-Phase Auto transformer. | DSC test Certificate shall be provided at the time of Despatch. Please confirm. | Bidder/ Manufacturer should has successfully carried out Dynamic Short Circuit test on 315MVA or above rating 400/220/33kV, 3-Phase Auto transformer as on the originally scheduled date of bid opening and shall enclose the relevant Test Report/certificate along with bid which is in compliance with Clause 3.14.1 of Technical Specification Section: Transformer (Up to 400kV Class Rev 13). Design review of offered 400kV Class Auto Transformer shall be carried out based on the design of short circuit tested 315MVA or above rating 400/220/33kV, 3-Phase Auto transformer. In case dynamic short circuit test is planned on new 500MVA 400/220/33kV 3-Ph Autotransformer, same has to be carried out by bidder/ manufacturer without any additional cost & time implication to POWERGRID. |

| 2 | Volume II-Technical Specifications 400kV Transformer _Rev 13 Clause no 5.3- Design Review | 5.3 - The manufacturer shall provide all necessary information and calculations to demonstrate that the transformer meets the requirements for short circuit strength and H2 CH4 C2H2 C2H4 C2H6 CO CO2 TDCG 100 120 1 50 65 350 2500 720 Technical Specification: Section -Transformer (Upto 400kV Class) Page 9 of 109 C/ENGG/MODEL-SPEC/TRF Rev. 13 durability. The latest recommendations of IEC and Cigre SC 12 shall be applied for short circuit withstand evaluation. | DSC test Certificate or any relevant documentation in this regard shall be provided at the time of Despatch. Please confirm. | Design review of offered 400kV Class Auto Transformer shall be carried out based on the design of short circuit tested 315MVA or above rating 400/220/33kV, 3-Phase Auto transformer. In case dynamic short circuit test is planned on new 500MVA 400/220/33kV 3-Ph Autotransformer, same has to be carried out by bidder/ manufacturer without any additional cost & time implication to POWERGRID. |
| --- | --- | --- | --- | --- |