## Technical PRE-BID
Clarification No.-1 (technical part) dated 20.02.2020 to the Bidding Documents for GIS Substation Extension Package-SS-56 for Construction of 2 Nos. of 400 kV GIS line bays under ISTS at 765/400kV Varanasi Substation; Spec. No.: CC-CS/981-NR3/GIS-4048/3/G3
S/No. | Sub-station | Clause Ref | Specification Description | Clarification Required | POWERGRID Reply
1 | Section Project | 4.1.1 a)iii & Page 4 of 13 | Gas monitoring devices, barriers, pressure switches, UHF PD Sensors etc. as | We are not considering supply of any PD monitoring device in our scope as it is not mentioned in BOQ as well. | PD Monitoring Kit is not envisaged under present Scope. However PD sensors are part of respective GIS moduls and GIB.
2 | Section Project | 4.1.7 b) & Page 5 & 6 of 13 | Busbar Augmentation | Line item is missing in Supply price schedule. | The existing 400 kV Bus bar protection relay is ALSTOM make P747 Centralized Bus Bar Protection relay with available CT modules in the relay for bays under present scope. Other minor items if required for Bus Bar Protection augmentation is to be consideredunder respective service item. Bidder is to quote accordingly
3 | Section Project | 4.1.7 e) & Page 6 of 13 | Fire protection and alarm system for switchyard panel room & GIS area. | We are considering that only 1 no. SPR is required & for which we need to supply 1 set of Fire protection alarm system i.e standard for 6 mtr panel room.However price schedule is asking for 2 sets.request you to confirm sets & sepcifcations required for this package. | One SYPR is envisaged per diameter hence bidder to quote as per the BPS and Technical Specification
4 | Section Project | 4.1.7 h) & Page 6 of 13 | Complete lighting and illumination for the 400 kV switchyard (extension) area and switchyard panel under present scope. | We are considering that only 1 no. SPR is required & for which we need to supply 1 set of illumination i.e standard for 6 mtr panel room.However price schedule is asking for 2 sets.request you to confirm sets & sepcifcations required for this package. | refer our above said reply to the similar query
5 | Price Schedule -Sch 1 | S/No. 16 | Air conditioning System | We are considering that only 1 no. SPR is required & for which we need to supply 1 set of Air conditioning system i.e standard for 6 mtr panel room.However price schedule is asking for 2 sets.request you to confirm sets & sepcifcations required for this package. | refer our above said reply to the similar query
6 | Price Schedule -Sch 1 | S/No. 1 | Extension of existing GIS | Please provide existing layout dimensional/section drawings of Hyosung GIS & the existing Hyosung busbar/conductor cross sectional drawings with dimensions enabling us to design interface.Also provide gas pressure details. | refer our above said reply to the similar query
7 |  | General | Tender drawings | please confirm Switchyard panel room location in outdoor switchyard & provide Cable trench route layout from existing CRB to Switchyard panel room and Sectional layout of outdoor layout. | SYPR shall be place at suitbal location in 400 kV Switchyard under present scope. The Location of SYPR and Cable route shall be decided during detailed engg
8 | Price Schedule -Sch 1 | S/No.65 | General | 02 PMUs has been asked but if we refer Section project, 400 KV main bays are 04 nos.Kindly confirm the requirement & PMU requirement is not mentioned in section project. | PMUs scope is considered only for present 400 kV line bays.Bidder to quote as per BPS.
9 |  | TV tower | Tender drawings | PGCIL tender drawing for Tower TV is for 50 m/s wind speed.Kindly confirm that the same drawing will be applicable for 47ms/s wind speed or not.If not then please furnish revised drawing to calculate tower weight. | Please find attcahed tender drawing for the Tower TV applicable for 47ms/s wind speed.
10 | Price Schedule -Sch 1 | S/No. 22 | GIB length | Request you to confirm that length given in the price schedule includes bus extension and feeder bays connection to bushings. | Bidder's understanding is correct
11 | Price Schedule -Sch 1 | S/No. 14,15,17 | Quantity & Unit | for these line items qauntity should be 1 & unit should be LS. | Bidder to quote as per BPS
12 |  | 02-Second Envelope Price Schedules_SS56 | PDM | As per the BOQ , Line item for PDM is not mentioned. As per our understanding, we need to supply only PDM sensors for 400kVGIS and there is no requirement to provide Portable PDM Kit or On-line PDM equipment. Kindly clarify. | refer our above said reply to the similar query
13 |  | 02-Second Envelope Price Schedules_SS56 | Length of GIB | As per the BOQ, the quantity of 400kV bus duct mentioned is 850m, Kindly confirm that mentioned length of bus duct includes GIB from FES to airbushing and GIB from existing GIS to present GIS. | refer our above said reply to the similar query
14 |  | 02-Second Envelope Price Schedules_SS56 |  | Neither Portable nor Online Partial Discharge Monitoring system is mentioned in BPS. We believe that only UHF PD sensors are envisaged. Please confirm. | Please refer our reply for similar query above
15 | BOQ | PDM | Customer's Requirement: N/A | Bidder's Remark: We would like to inform you that, as per the BPS received, there is no requirement for PDM. Kindly let us know if there is any requirement for the same. Kindly confirm the same. | Please refer our reply for similar query above
16 | Section Project | For 400kV GIS 3 Phase CB,ES & DS | Customer's Requirement: 3 Phase CB,ES & DS. | Bidder's Remark: We provide single phase CB, ES & DS. However our ES and DS mechanism is gang operated. Kindly accept the same. | Bidder to to meet the funcational requirement for GIS equipment as specifiied in Technical Specification and Bidder shall supply the euipment as per the requirement of Technical Specification.
17 | Section Project | For 400kV GIS 3 Phase HES | Customer's Requirement: 3 Phase single pole, group operated high speed earth switch is required. | Bidder's Remark: We provide single pole, individually operated high speed earth switch. Kindly accept the same. | Bidder to to meet the funcational requirement for GIS equipment as specifiied in Technical Specification and Bidder shall supply the euipment as per the requirement of Technical Specification.
18 | TS | CT Data | Customer's Requirement: One minute power frequency withstand voltage between secondary terminal and earth is mentioned 5kV rms | Bidder's Remark: We would like to inform you that, as per the IEC standards, the mentioned value shall be 3kV rms. Kindly accept as per IEC. | Bidder shall supply the euipment as per the requirement of Technical Specification.